## NOx_Small Gas Boilers 13.310_09
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
OK-0128 | MID AMERICAN STEEL ROLLING MILL | MID AMERICAN STEEL AND WIRE COMPANY | MARSHALL | OK | 73446 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2003-106-C(M-1) PSD | 3312 | 331111 | 110022524062 | 03/26/2008 &nbsp;ACT | 09/08/2008 &nbsp;ACT | 2008-12-31 | 2010-12-17 | B |  | THE FACILITY WAS CONSTRUCTED UNDER PERMIT NO. 2003-106-C ISSUED MARCH 25, 2003, AND IS CURRENTLY OPERATED UNDER PERMIT NO. 2003-106-O ISSUED JANUARY 3, 2005. THE FACILITY CURRENTLY OPERATES A SINGLE 74 MMBTUH GAS-FIRED FURNACE FOR SOFTENING STEEL BILLETS SO THAT THEY CAN BE DRAWN IN TO WIRE. | MID AMERICAN PROPOSES TO INSTALL TWO ELECTRIC ARC STEEL MELTING FURNACES. THE FURNACES WERE FABRICATED IN 2000 FOR INSTALLATION AT ANOTHER COMPANY SITE THAT WAS NOT CONSTRUCTED, THE PROPOSED GRIFFIN WHEEL PLANT AT TULSA. THE PROPOSED FURNACES WILL BE CAPABLE OF PRODUCING A TOTAL OF APPROXIMATELY 80 TONS/HR (640,000 TONS PER YEAR) OF Â¿BILLETÂ¿ Â¿ (BAR-SHAPED INGOTS) STEEL. THE STEEL MAY BE USED ON-SITE IN THE EXISTING WIRE PRODUCTION UNIT OR SOLD TO OTHER MILLS. | Ladle pre-heater and refractory drying | 13.31 | natural gas | 0 |  |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good Combustion natural gas fuel | 0.1 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0173 | CMC STEEL OKLAHOMA | COMMERCIAL METALS COMPANY | BRYAN | OK | 74701 | USA | RANDALL WALKER | 830-372-8507 | RANDALL.WALKER@CMC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2015-0643-C PSD | 3312 | 331111 | 013-00047 | 09/09/2015 &nbsp;ACT | 01/19/2016 &nbsp;ACT | 2016-01-19 | 2016-07-07 | A |  | In this steel mill, CMC will manufacture steel products from scrap steel. Iron ore will not be processed at the mill. Scrap metal will be transported into the facility to be used as feedstock for the Melt Shop. Once the molten steel reaches the desired conditions, it will be transferred to a large refractory-lined vessel known as a ladle. The ladle will be transported to a continuous caster, where the steel will be poured into a refractory-lined surge vessel called a tundish and subsequently into a water-cooled mold. After casting, the continuous steel strand will be rolled to the desired shape. After rolling, the steel will be cooled, bundled, and stored. To produce some structural material such as angles and channels, the rebar will be unbundled and passed through a straightener roller process. The finished products will be shipped off-site by truck as needed for use by customers. | Emissions of NOx, CO, VOC, SO2,PM10/PM2.5, and GHG exceed the applicable SER. Therefore, each is subject to PSD review. | Heaters (Gas-Fired) | 13.31 | Natural Gas | 0 |  | Numerous gas-fired heaters will be installed. The application requested that the sizes all be kept confidential. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good Combustion Natural Gas Fuel | 0.1 | LB/MMBTU |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*FL-0363 | DANIA BEACH ENERGY CENTER | FLORIDA POWER AND LIGHT COMPANY | BROWARD | FL | 33314 | USA | JOHN HAMPP | 561-691-2894 | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0110037-017-AC | 4911 | 221112 | 110002044065 | 07/27/2017 &nbsp;ACT | 12/04/2017 &nbsp;ACT | 2018-04-03 | 2018-04-11 | B | https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.F.ZIP | 1200 megawatt 2-on-1 combined cycle facility, natural gas-fired, with limited ULSD use. GE 7HA turbines | Technical evaluation available at https://arm-permit2k.dep.state.fl.us/nontv/0110037.017.AC.D.ZIP | Two natural gas heaters | 13.31 | Natural gas | 9.9 | MMBtu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices / Manufactuer design | 0.1 | LB/MMBTU | DESIGN VALUE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | No testing required; design spec only
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Two natural gas heaters | 13.31 | Natural gas | 10 | MMBtu/hr | Fueled only with gas. May operate one heater at a time. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices Must have NOx emission design value less than 0.1 lb/MMBtu | 0.1 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Design standard only. No testing required.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-AUXBOILER1-2; Two (2) natural gas-fired auxiliary boilers. | 13.31 | natural gas | 40 | MMBTU/H | Two (2) natural gas-fired auxiliary boilers. 40 MMBTU/H each. Fuel restriction = 360.8 MMSCF/YR total for both units. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices. | 0.035 | LB/MMBTU | TEST PROTOCOL; EACH UNIT. | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The NOx limit of 0.035 LB/MMBTU applies to each unit.
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2018-06-25 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | Auxiliary Boiler | 13.31 | Natural Gas | 77.8 | mmBtu/hr | Annual emission based on 4600 hours/year. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LNB, FGR, Good Combustion Practices | 0.0011 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 1.96 | TONS/YEAR |  | 0.0011 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP26 | 13.31 | NATURAL GAS | 24 | MMBTU/H | UNIT CP26 IS A UNILUX BOILER AT CAESAR'S PALACE. THE UNIT IS ALLOWED TO OPERATE UP TO 8,760 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER | 0.0108 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 9 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0108 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP01 | 13.31 | NATURAL GAS | 35.4 | MMBTU/H | UNIT CP01 IS A HURST BOILER AT CAESAR'S PALACE. UNIT CP01 IS IDENTICAL TO UNIT CP02. UNITS CP01 THROUGH CP05 (FIVE BOILERS) ARE SUBJECT TO THE ANNUAL LIMIT OF TOTAL OPERATING TIME FOR 33,520 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER | 0.035 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 29 | PPMVD | CORRECTED TO 3% OXYGEN | 0.035 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP03 | 13.31 | NATURAL GAS | 33.48 | MMBTU/H | UNIT CP03 IS A BURNHAM BOILER AT CAESAR'S PALACE. UNITS CP01 THROUGH CP05 (FIVE BOILERS) ARE SUBJECT TO THE ANNUAL LIMIT OF TOTAL OPERATING TIME FOR 33,520 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER | 0.0367 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 30 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0367 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT FL01 | 13.31 | NATURAL GAS | 14.34 | MMBTU/H | UNIT FL01 IS A JOHNSTON BOILER AT FLAMINGO LAS VEGAS. THIS UNIT MAY OPERATE 8,760 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER AND FLUE GAS RECIRCULATION | 0.0353 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 29 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0353 | LB/MMBTU |  | 0 | 0 | N
FL-0335 | SUWANNEE MILL | KLAUSER HOLDING USA, INC. | SUWANNEE COUNTY | FL | 32060 | USA | MICHEL FUNK | 843-626-9600 | MICHAEL.FUNK@KLAUSNER-GROUP.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | David Read is the permitting engineer for this project, 850-717-9075. | 1210468-001-AC(PSD-FL-417) | 2421 | 321113 | Not Available | 01/09/2012 &nbsp;ACT | 09/05/2012 &nbsp;ACT | 2012-10-29 | 2013-05-30 | U |  | The Suwannee Mill produces dimensional kiln dried lumber and timber byproducts consisting of bark, wood chips, sawdust, and dry shavings. When the facility is fully constructed, the mill has a maximum annual production capacity of 700 MMBF/yr. The mill processes tree-length green saw logs into dimensional lumber. Raw materials, finished lumber and saleable by-products are received and dispatched from the facility by truck or rail. | The Suwannee Mill produces dimensional kiln dried lumber and timber byproducts consisting of bark, wood chips, sawdust, and dry shavings. When the facility is fully constructed, the mill has a maximum annual production capacity of 700 MMBF/yr. The mill processes tree-length green saw logs into dimensional lumber. Raw materials, finished lumber and saleable by-products are received and dispatched from the facility by truck or rail. The mill will operate kilns that heat the green rough sawn lumber to reduce the moisture content to meet required finished product market specifications. The kilns are heated with hot water that is generated in four natural gas-fired boilers (46 million British thermal units per hour (MMBtu/hr)) and two biomass-fired boilers (120 MMBtu/hr). The biomass boilers are fired by untreated bark, wood chips, and sawdust that are byproducts of the mills operation. Clean, untreated woody biomass obtained from off-site sources may also be fired in the biomass boilers | Four(4) Natural Gas Boilers - 46 MMBtu/hour | 13.31 | Natural Gas | 46 | MMBTU/H | The four natural gas boilers are used to generate the hot water that is used in the lumber kiln drying process. Two boilers each share a common stack for a total of two stacks. In the initial phase of construction, two natural gas fired boilers will supply hot water to one block of kilns. As other kiln blocks are completed, the two other natural gas boilers will be constructed and brought online. Finally, the two biomass boilers will be built and brought on line. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burner and Flue Gas Recirculation | 0.036 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) NATURAL GAS AUXILIARY BOILERS | 13.31 | NATURAL GAS | 80 | MMBTU/H | BOTH BOILERS, LABELED AS B001 AND B002, ARE EQUIPPED WITH LOW NOX BURNERS WITH FLUE GAS REGULATION. THIS IS CONSIDERED A STEAM GENERATING UNIT. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNER WITH FLUE GAS RECIRCULATION | 0.032 | LB/MMBTU | 3 HOURS | BACT-PSD |  |  | 50 |  | 2.56 | LB/H | 3 HOURS | 0 |  |  | 0 | 0 | N |  | LIMIT ONE AND TWO ARE FOR EACH BOILER
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | AUXILIARY BOILER | 13.31 | PIPELINE QUALITY NATURAL GAS | 93 | MMBTU/H | ONE AUXILIARY BOILER WITH ULTRA-LOW NOX BURNER (ULNB) AND FLUE GAS RECIRCULATION (FGR) SUBJECT TO NSPS SUBPART DC RECORDKEEPING AND REPORTING REQUIREMENTS | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER, EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS, AND APPLICATION OF GOOD COMBUSTION PRACTICES | 0.01 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0393 | RAY COMPRESSOR STATION | CONSUMERS ENERGY | MACOMB | MI | 48005-4510 | USA | AMY KAPUGA | 517-788-2201 | ADKAPUGA@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact Jeff Rathbun (permit engineer) for questions at 517-241-8072 | 206-09 | 4925 | 486210 | 110001845246 | 06/03/2010 &nbsp;ACT | 10/14/2010 &nbsp;ACT | 2012-06-21 | 2017-07-20 | B |  | Compressor Station |  | Auxiliary Boiler | 13.31 | natural gas | 12.25 | MMBTU/H | Boiler provides building heat. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx burner. | 0.035 | LB/MMBTU | TEST METHOD | BACT-PSD | N/A | N | 0.5 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Based on emission factor of 0.035 lb/MMBTU
TX-0772 | PORT OF BEAUMONT PETROLEUM TRANSLOAD TERMINAL (PBPTT) | JEFFERSON RAILPORT TERMINAL I TEXAS LLC | ORANGE | TX |  | USA | PHILIP TREW | 409-239-5382 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Teresa Hurley, (512) 239-5316 Teresa.Hurley@tceq.texas.gov | 118901, GHGPSDTX108 AND PSDTX1 | 5171 | 424710 | 110055496379 | 09/21/2015 &nbsp;ACT | 11/06/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | Crude oil, condensate, bitumen storage and marine/railcar loading terminal |  | Commercial/Institutional-Size Boilers/Furnaces | 13.31 | natural gas | 40 | MMBTU/H | Hot oil heater | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low NOx burners | 0.036 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0755 | RAMSEY GAS PLANT | DELAWARE BASIN MIDSTREAM LLC | REEVES | TX |  | USA | MICAH CARTER | 720-929-6788 | MICAH.CARTER@ANADARKO.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ozden Tamer, (512)239-4577, ozden.tamer@tceq.texas.gov | 117323 AND PSDTX1392,O-3546 | 1321 | 211112 | 110054879985 | 07/10/2015 &nbsp;ACT | 05/21/2015 &nbsp;ACT | 2015-07-20 | 2016-07-06 | B |  | Ramsey IV, V and VI Gas Plants and associated Amine I and II Plants. Each Ramsey Plant will have gas gathering, treating, conditioning, compression and processing capabilities. This expansion project will increase the processing capacity of the existing plant with three 200 MMSCF/day cryogenic plants and two amine plants with a combined capacity of 2000 gallon per minute (gpm). A percentage of the acid gas from the amine still vents (EPNs: A-4 and A-5) will be captured and routed to a pipeline for Carbon capture and Sequestration (CCS) purposes and the remaining acid gas from the amine still vents will be routed to the regenerative thermal oxidizers (EPNs: RTO-4 and RTO-5) |  | Hot Oil Heaters and Regeneration Heaters | 13.31 | Residue gas equivalent to natural gas | 60 | MMBTU/H | Hot Oil Heaters: 60 MMBtu/hr; Regeneration Heaters: 36 MMBtu/hr | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | low NOx burners | 0.045 | LB/MMBTU |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WY-0066 | MEDICINE BOW IGL PLANT | MEDICINE BOW FUEL & POWER | CARBON | WY |  | USA | ROBERT MOSS |  |  | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-5873 | 1311 | 324110 | 110009762051 | 06/20/2007 &nbsp;ACT | 03/04/2009 &nbsp;ACT | 2009-03-19 | 2009-04-20 | A |  | COAL TO LIQUIDS PLANT |  | GASIFICATION PREHEATER 2 | 13.31 | NATURAL GAS | 21 | MMBTU/H | 500 HOURS OF OPERATION | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNERS | 0.05 | LB/MMBTU | HOURLY | BACT-PSD |  | N | 0 | N | 1 | LB/H | HOURLY | 0.3 | T/YR | ANNUAL | 0 | 0 | N
WY-0066 | MEDICINE BOW IGL PLANT | MEDICINE BOW FUEL & POWER | CARBON | WY |  | USA | ROBERT MOSS |  |  | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-5873 | 1311 | 324110 | 110009762051 | 06/20/2007 &nbsp;ACT | 03/04/2009 &nbsp;ACT | 2009-03-19 | 2009-04-20 | A |  | COAL TO LIQUIDS PLANT |  | GASIFICATION PREHEATER 3 | 13.31 | NATURAL GAS | 21 | MMBTU/H | 500 HOURS OF OPERATION | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNERS | 0.05 | LB/MMBTU | HOURLY | BACT-PSD |  | N | 0 | U | 1 | LB/H | HOURLY | 0.3 | T/YR | ANNUAL | 0 | 0 | N
WY-0066 | MEDICINE BOW IGL PLANT | MEDICINE BOW FUEL & POWER | CARBON | WY |  | USA | ROBERT MOSS |  |  | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-5873 | 1311 | 324110 | 110009762051 | 06/20/2007 &nbsp;ACT | 03/04/2009 &nbsp;ACT | 2009-03-19 | 2009-04-20 | A |  | COAL TO LIQUIDS PLANT |  | GASIFICATION PREHEATER 4 | 13.31 | NATURAL GAS | 21 | MMBTU/H | 500 HOURS OF OPERATION | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNERS | 0.05 | LB/MMBTU | HOURLY | BACT-PSD |  | N | 0 | U | 1 | LB/H | HOURLY | 0.3 | T/YR | ANNUAL | 0 | 0 | N
WY-0066 | MEDICINE BOW IGL PLANT | MEDICINE BOW FUEL & POWER | CARBON | WY |  | USA | ROBERT MOSS |  |  | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-5873 | 1311 | 324110 | 110009762051 | 06/20/2007 &nbsp;ACT | 03/04/2009 &nbsp;ACT | 2009-03-19 | 2009-04-20 | A |  | COAL TO LIQUIDS PLANT |  | GASIFICATION PREHEATER 5 | 13.31 | NATURAL GAS | 21 | MMBTU/H | 500 HOURS OF OPERATION | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNERS | 0.05 | LB/MMBTU | HOURLY | BACT-PSD |  | N | 0 | U | 1 | LB/H | HOURLY | 0.3 | T/YR | ANNUAL | 0 | 0 | N
WY-0066 | MEDICINE BOW IGL PLANT | MEDICINE BOW FUEL & POWER | CARBON | WY |  | USA | ROBERT MOSS |  |  | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-5873 | 1311 | 324110 | 110009762051 | 06/20/2007 &nbsp;ACT | 03/04/2009 &nbsp;ACT | 2009-03-19 | 2009-04-20 | A |  | COAL TO LIQUIDS PLANT |  | GASIFICATION PREHEATER 1 | 13.31 | NATURAL GAS | 21 | MMBTU/H | 500 HOURS OF OPERATION | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNERS | 0.05 | LB/MMBTU | HOURLY | BACT-PSD |  | N | 0 | N | 1 | LB/H | HOURLY | 0.3 | T/YR | ANNUAL | 0 | 0 | N
SC-0112 | NUCOR STEEL - BERKELEY | NUCOR STEEL | BERKELEY | SC | 29450 | USA | RAY SIMS | 8433366123 | SIMSR@NUCORSTEEL.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MR. DENNIS CAMIT | (803)898-4284 | camitdr@dhec.sc.gov | WANDA PARNELL (803) 898-4123 | 0420-0060-DO | 3312 | 331111 | 110000353527 | 12/06/2007 &nbsp;ACT | 05/05/2008 &nbsp;ACT | 2012-05-09 | 2013-10-30 | D |  | SCRAP STEEL RECYCLING MILL |  | TUNNEL FURNACE BURNERS | 13.31 | NATURAL GAS | 58 | MMBTU/H | THIS PROJECT IS ADDING AN ADDITIONAL 58 MILLION BTU/HR HEAT INPUT TO EXISTING TUNNEL FURNACE SYSTEM. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNERS | 0.1 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0.1 | LB/MMBTU |  | 0 | 0 | N |  | THE EMISSION RATE WILL BE THE RATE FROM THE NEW BURNERS.
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Inlet Air Heater (EP07) | 13.31 | Natural Gas | 16.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.012 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 0.2 | LB/H | 3-HOUR AVERAGE | 0.4 | T/YR |  | 0 | 0 | N |  | limited to 4,380 hours of operation per calendar year
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Inlet Air Heater (EP08) | 13.31 | Natural Gas | 16.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.012 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 0.2 | LB/H | 3-HOUR AVERAGE | 0.4 | T/YR |  | 0 | 0 | N |  | limited to 4,380 hours of operation per calendar year
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Inlet Air Heater (EP09) | 13.31 | Natural Gas | 16.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.012 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 0.2 | LB/H | 3-HOUR AVERAGE | 0.4 | T/YR |  | 0 | 0 | N |  | limited to 4,380 hours of operation per calendar year
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Inlet Air Heater (EP10) | 13.31 | Natural Gas | 16.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.012 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 0.2 | LB/H | 3-HOUR AVERAGE | 0.4 | T/YR |  | 0 | 0 | N |  | limited to 4,380 hours of operation per calendar year
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Inlet Air Heater (EP11) | 13.31 | Natural Gas | 16.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.012 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 0.2 | LB/H | 3-HOUR AVERAGE | 0.4 | T/YR |  | 0 | 0 | N |  | limited to 4,380 hours of operation per calendar year
TX-0656 | GAS TO GASOLINE PLANT | NATGASOLINE | JEFFERSON | TX |  | USA | KEVIN STRUVE |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Cheryl Covone 512-239-1248 | PSDTX1340 AND 107764 | 2911 | 325199 | 110064577006 | 01/16/2013 &nbsp;ACT | 05/16/2014 &nbsp;ACT | 2014-05-20 | 2016-05-12 | A |  | Chemical Plant |  | Heaters | 13.31 | natural gas | 45 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low NOx Burners | 0.036 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0656 | GAS TO GASOLINE PLANT | NATGASOLINE | JEFFERSON | TX |  | USA | KEVIN STRUVE |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Cheryl Covone 512-239-1248 | PSDTX1340 AND 107764 | 2911 | 325199 | 110064577006 | 01/16/2013 &nbsp;ACT | 05/16/2014 &nbsp;ACT | 2014-05-20 | 2016-05-12 | A |  | Chemical Plant |  | heaters (5) | 13.31 | natural gas | 24.3 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low NOx Burners | 0.036 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WY-0075 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | MD-16173 | 491 | 221122 | Not Found | 05/01/2014 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2014-06-16 | 2018-05-11 | B |  | Nominal 220 megawatt (MW) gross electrical facility. | Installation of a 25.06 MMBtu/hr Auxiliary Boiler (Cleaver Brooks CBEX Elite 600). Subject to PSD based on project aggregation. | Auxiliary Boiler | 13.31 | natual gas | 25.06 | MMBtu/h |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.0175 | LB/MMBTU | 3 HOUR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0.4 | LB/H | 3 HOUR AVERAGE | 0 |  |  | 0 | 0 | N
LA-0246 | ST. CHARLES REFINERY | VALERO REFINING - NEW ORLEANS, LLC | ST. CHARLES | LA | 70079 | USA | ROBERT MARTIN | 985-764-8611 | ROB.MARTIN@VALERO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - 225-219-3395 | PSD-LA-619(M6) | 2911 | 324110 | Not Applicable | 08/02/2010 &nbsp;ACT | 12/31/2010 &nbsp;ACT | 2011-03-29 | 2011-07-06 | C |  | A typical Petroleum Refinery |  | EQT0323 - Boiler 401F | 13.31 | refinery fuel | 99 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx Burners | 0.04 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 3.96 | LB/H | HOURLY MAXIMUM | 0 |  |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Inlet Air Heater (EP06) | 13.31 | Natural Gas | 16.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.012 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 0.2 | LB/H | 3-HOUR AVERAGE | 0.4 | T/YR |  | 0 | 0 | N |  | limited to 4,380 hours of operation per calendar year
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Reactor Charge Heater - 53B001 | 13.31 | Natural Gas | 10.1 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.04 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.77 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.04 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002A | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.04 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 5.71 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.04 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002B | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.04 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 5.71 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.04 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002C | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.04 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 5.71 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.04 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002D | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.04 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 5.71 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.04 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002E | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.04 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 5.71 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.04 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Regeneraton Heater - 51B001 | 13.31 | Natural Gas | 61 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.04 | lb/MMBtu | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 10.69 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.04 LB/MMBTU (12-Month Rolling Average)
SC-0112 | NUCOR STEEL - BERKELEY | NUCOR STEEL | BERKELEY | SC | 29450 | USA | RAY SIMS | 8433366123 | SIMSR@NUCORSTEEL.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MR. DENNIS CAMIT | (803)898-4284 | camitdr@dhec.sc.gov | WANDA PARNELL (803) 898-4123 | 0420-0060-DO | 3312 | 331111 | 110000353527 | 12/06/2007 &nbsp;ACT | 05/05/2008 &nbsp;ACT | 2012-05-09 | 2013-10-30 | D |  | SCRAP STEEL RECYCLING MILL |  | VACUUM DEGASSER BOILER | 13.31 | NATURAL GAS | 50.21 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low NOx Burners | 0.035 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 1.76 | LB/H |  | 0.035 | LB/MMBTU |  | 0 | 0 | N
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | Auxiliary boiler | 13.31 | natural gas | 39.8 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.035 | LB/MMBTU | 3-HR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0772 | PORT OF BEAUMONT PETROLEUM TRANSLOAD TERMINAL (PBPTT) | JEFFERSON RAILPORT TERMINAL I TEXAS LLC | ORANGE | TX |  | USA | PHILIP TREW | 409-239-5382 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Teresa Hurley, (512) 239-5316 Teresa.Hurley@tceq.texas.gov | 118901, GHGPSDTX108 AND PSDTX1 | 5171 | 424710 | 110055496379 | 09/21/2015 &nbsp;ACT | 11/06/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | Crude oil, condensate, bitumen storage and marine/railcar loading terminal |  | Commercial/Institutional-Size Boilers/Furnaces | 13.31 | natural gas | 95.7 | MMBTU/H | Three boilers will be used intermittently to provide steam for heating tanks or railcars as necessary to reduce viscosity of heavy liquids. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low NOx burners and flue gas recirculation | 0.011 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | Auxillary Boiler | 13.31 | Natural Gas | 99 | MMBtu/H | 99 MMBTU/H auxillary boiler with low-NOx burners and flue gas re-circulation, burning only natural gas. Boiler restricted to 2000 hours of operation per rolling 12-months. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | low NOx burners and flue gas recirculation | 0.02 | LB/MMBTU |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 1.98 | T/YR | PER ROLLING 12-MONTHS | 0.02 | LB/MMBTU |  | 0 | 0 | N |  | BACT: 0.020 LB/MMBTU. Restricted to 2000 hours of operation per rolling 12-months.
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGAUXBOILERS: Two auxiliary boilers &lt; 100 MMBTU/H heat input each | 13.31 | natural gas | 100 | MMBTU/H heat input each | There are two auxiliary boilers each rated at less than 100 MMBTU/H heat input. Fuel usage limited to not more than 416.3 MMscf of natural gas in each boiler per 12-month rolling timeperiod as determined at the end of each month. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners and flue gas recirculation. | 0.05 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | N/A | N | 70 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is 0.05 LB/MMBTU heat input, for each boiler. Test protocol will specify the averaging time. Fuel usage limited to not more tahn 416.3 MMSCF of natural gas in each boiler per 12-month rolling time period as determined at the end of each month.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler A (EUAUXBOILERA) | 13.31 | natural gas | 55 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 55 MMBTU/hr fuel heat input (EUAUXBOILERA within flexible group FGAUXBOILERS). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners and good combustion practices | 0.05 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 70 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Low NOx burners (LNB) with flue gas recirculation is greater than $8,000/ton for NOx. The efficiency range for LNB alone is 40-70 percent.
MI-0421 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions related to the permit. Thank you. | 59-16 | 2493 | 321219 | Not Found | 06/30/2016 &nbsp;ACT | 08/26/2016 &nbsp;ACT | 2017-01-27 | 2017-07-20 | A |  | Particleboard manufacturing |  | EUFLTOS1 in FGTOH (Thermal Oil System for Thermally Fused Lamination Lines) | 13.31 | Natural gas | 34 | MMBTU/H | One natural gas fired thermal oil system for thermally fused lamination lines rated at 10.2 MMBTU/H fuel heat input (EUFLTOS1 in FGTOH). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners and good design and combustion practices. | 0.05 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 50 | N | 2.2 | T/YR | BASED UPON A 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | SCR is not economically feasible for the press/sifter thermal oil heater with a cost of $27,000/ton. Given this high cost for the larger heater, SCR would also not be cost effective for the smaller heater.
MI-0421 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions related to the permit. Thank you. | 59-16 | 2493 | 321219 | Not Found | 06/30/2016 &nbsp;ACT | 08/26/2016 &nbsp;ACT | 2017-01-27 | 2017-07-20 | A |  | Particleboard manufacturing |  | EUTOH (In FGTOH)--Thermal Oil Heater | 13.31 | Natural gas | 34 | MMBTU/H | One natural gas fired thermal oil heater for press and sifter rated at 34 MMBTU/H fuel heat input (EUTOH in FGTOH). All falls under RBLC Process Type Code 30.590. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners and good design and combustion practices. | 0.05 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 50 | N | 7.3 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | The company conducted a cost analysis for SCR for the press/sifter thermal oil heater. The results show that SCR is not economically feasible with a cost of $27,000/ton.
WY-0067 | ECHO SPRINGS GAS PLANT | WILLIAMS FIELD SERVICES COMPANY | CARBON | WY | 82336 | USA | CORTNIE MORRELL | 3078722880 | CORTNIE.MORRELL@WILLIAMS.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov | MS. JAMIE SHARP WY DEQ AIR QUALITY DIVISION 122 WEST 25TH STREET CHEYENNE, WY 82002 307-777-7817 | MD-7837 | 1321 | 211112 | 110010144628 | 05/29/2008 &nbsp;ACT | 04/01/2009 &nbsp;ACT | 2009-04-02 | 2009-04-16 | A |  |  |  | HOT OIL HEATER S38 | 13.31 | NATURAL GAS | 84 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNERS WITH FLUE GAS RECIRCULATION | 0.03 | LB/MMBTU |  | BACT-PSD | NSPS , NESHAP | N | 0 | N | 11 | T/YR |  | 0 |  |  | 0 | 0 | N |  | 60-90% ESTIMATED EFFICIENCY
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, PICKLE LINE | 13.31 | NATURAL GAS | 67 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.035 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILERS SN-26 AND 27, GALVANIZING LINE | 13.31 | NATURAL GAS | 24.5 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.035 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS SCR COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.1 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler B (EUAUXBOILERB) | 13.31 | natural gas | 95 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 95 MMBtu/hr fuel heat input (EUAUXBOILERB within flexible group FGAUXBOILERS). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | low NOx burners, flue gas recirculation and good combustion practices. | 0.05 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 80 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Selective catalytic reduction is greater than $11,000/ton for NOx. The efficiency range for Low NOx burners and flue gas recirculation is 60-85 percent.
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUTOH in FGTOH | 13.31 | Natural gas | 38 | MMBTU/H | One natural gas-fired thermal oil heater for press and sifter rated at 38 MMBTU/hr fuel heat input (EUTOH in FGTOH). Also falls under the RBLC Process Type Code 30.590. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners. | 0.05 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 50 | N | 8.16 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | The company conducted a cost analysis for SCR for the press/sifter thermal oil heater. The results show that SCR is not economically feasible, with a cost of $27,000/ton. The small increase in heat input capacity (4 MMBTU/HR) does not make add on control cost effective.
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUFLTOS1 in FGTOH | 13.31 | Natural gas | 10.2 | MMBTU/H | One natural gas-fired thermal oil system for thermally fused lamination lines rated at 10.2 MMBTU/H fuel heat input (EUFLTOS1 in FGTOH). Note: The throughput capacity, 10.2 MMBTU/H, is not a change but instead a correction from the previous entry. The previous entry is under MI-0421 for the original permit. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners. | 0.05 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 50 | N | 2.2 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | SCR is not economically feasible for the press/sifter thermal oil heater, with a cost of $27,000 per ton. Given this high cost for the larger heater, SCR would also not be cost effective for the smaller heater.
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUAUXBOILER (North Plant): Auxiliary Boilder | 13.31 | Natural gas | 61.5 | MMBTU/H | A natural gas-fired auxiliary boiler, rated at 61.5 MMBTU/H (HHV) to facilitate startup of the CTGHRSG train and to provide the required steam to support the startup of the facility, including but not limited to steam for sparging, STG seals, etc. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners/flue gas recirculation and good combustion practices. | 0.04 | LB/MMBTU | 30-DAY ROLLING AVG TIME PERIOD | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Selective catalytic reduction (SCR) was calculated to be over $18,000/ton for NOx.
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUAUXBOILER (South Plant): Auxiliary Boiler | 13.31 | Natural gas | 61.5 | MMBTU/h | A natural gas-fired auxiliary boiler, rated at 61.5 MMBTU/H (HHV) to facilitate startup of the CTGHRSG train and to provide the required steam to support the startup of the facility, including but not limited to steam for sparging, STG seals, etc. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners/flue gas recirculation and good combustion practices. | 0.04 | LB/MMBTU | 30 DAY ROLLING AVG TIME PERIOD | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Selective catalytic reduction (SCR) was calculated to be over $18,000/ton for NOx.
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUAUXBOILER: Auxiliary Boiler | 13.31 | Natural gas | 99.9 | MMBTU/H | A natural gas-fired auxiliary boiler, rated at 99.9 MMBTU/H to facilitate startup of the CTG/HRSG trains and to provide steam to the steam turbine generator seals. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low NOx burners/Flue gas recirculation. | 0.036 | LB/MMBTU | HOURLY | BACT-PSD | SIP | N | 0 | N | 3.6 | LB/H | HOURLY | 0 |  |  | 0 | 0 | N |  | The cost of selective catalytic reduction (SCR) is over $100,000 for the project.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUAUXBOILER (Auxiliary boiler) | 13.31 | natural gas | 83.5 | MMBTU/H | One natural gas fired auxiliary boiler rated at 83.5 MMBTU/hr fuel heat input (EUAUXBOILER). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners/Internal flue gas recirculation and good combustion practices. | 0.05 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 70 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Selective catalytic reduction (SCR) is greater than $12,000/ton for NOx.
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | BOILER | 13.31 | NATURAL GAS | 93 | MMBTU/H | AUXILIARY BOILER | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX WITH FGR | 0.011 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LAER
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT BA03 | 13.31 | NATURAL GAS | 31.38 | MMBTU/H | UNIT BA03 IS A KIWANEE BOLER AT BALLY'S LAS VEGAS. THE ANNUAL OPERATING TIME IS LIMITED TO 2,920 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOX BURNER | 0.0306 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 25 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0306 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT BA01 | 13.31 | NATURAL GAS | 16.8 | MMBTU/H | UNIT BA01 IS A KEWANEE BOILER AT BALLY'S LAS VEGAS. UNIT BA01 IS IDENTICAL TO UNIT BA02. THE TWO BOILERS ARE SUBJECT TO THE ANNUAL LIMIT OF COMBINED TOTAL OPERATING TIME FOR 10,900 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOX BURNER AND BLUE GAS RECIRCULATION | 0.03 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 25 | PPMVD | CORRECTED TO 3% OXYGEN | 0.03 | LB/MMBTU |  | 0 | 0 | N
TX-0680 | SONORA GAS PLANT | WTG SONORA GAS PLANT LLC | UPTON | TX |  | USA | ELENA HOFFMAN | (713) 983-0112 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 106139 PSDTX1316 | 1321 | 211112 | 110056413064 | 09/28/2012 &nbsp;ACT | 06/14/2013 &nbsp;ACT | 2015-03-13 | 2016-05-09 | B |  | The new Sonora Gas Plant will be a natural gas dehydration and natural gas liquids recovery and recompression plant. Pre-treated, sweet inlet natural gas will be received by pipeline into the facility, dehydrated, and then sent to the cryogenic natural gas liquids (NGL) recovery plant. Ethane and heavier hydrocarbons will be fractionated from the gas stream by refrigeration and transported for sales via pipeline. The residue gas stream will also be transported for sales via pipeline. |  | Heater | 13.31 | natural gas | 10 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | low-NOx burners | 0.01 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0714 | S R BERTRON ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | HARRIS | TX |  | USA | CRAIG ECKBERG | (713) 537-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | 102731 PSDTX1294 | 4911 | 221112 | 110034988413 | 05/10/2012 &nbsp;ACT | 12/19/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | NRG Texas is proposing to construct an additional electric power generation station at the Bertron Power Project which will generate electric power for sale on the wholesale electric market. The Bertron Power Project will include two power blocks that can be operated in combined cycle mode. |  | boiler | 13.31 | natural gas | 80 | MMBTU/H | operation limitation of 4,000 hours per year | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | low-NOx burners | 0.036 | LB/MMBTU | 3-HR ROLLING | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0148 | BUFFALO CREEK PROCESSING PLANT | MARKWEST BUFFALO CREEK GAS CO LLC | BECKHAM | OK | 73662 | USA | KRISTIN IKARD |  | KRISTIN.IKARD@ACCESSMIDSTREAM.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2012-1026-C PSD | 1321 | 211112 | Not Found | 02/21/2012 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2014-06-13 | 2018-05-11 | A |  | Mid-America Midstream Gas Services (MAMGS)proposes to construct a natural gas plant with ten natural gas-fired reciprocating internal combustion engines, two natural gas-fired turbines, a 230-MMSCFD amine unit with a 11.04 MMBTUH reboiler, an acid gas flare, eight condensate tanks, and six produced water tanks. Associated support operations include condensate truck loading, blowdowns and fugitive emissions. | FRS Entered as &lsquo;&lsquo;009-00118&lsquo;&lsquo;. Too short for a FRS. MAMGS proposes to construct a natural gas plant with ten natural gas-fired reciprocating internal combustion engines, two natural gas-fired turbines, a 230-MMSCFD amine unit with a 11.04 MMBTUH reboiler, an acid gas flare, eight condensate tanks, and six produced water tanks. Associated support operations include condensate truck loading, blowdowns and fugitive emissions. | Commercial/Institutional Boilers (&lt;100 MMBTUH) | 13.31 | Natural Gas | 11.04 | MMBTUH |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low-NOx burners | 0.045 | LB/MMBTU |  | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0153 | ROSE VALLEY PLANT | SEMGAS LP | WOODS | OK | 73717 | USA | KRISTIN IKARD | 405-727-1443 | KRISTIN.IKARD@ACCESSMIDSTREAM.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2012-1393-C PSD | 1321 | 211112 | 151-00432 | 05/15/2012 &nbsp;ACT | 03/01/2013 &nbsp;ACT | 2014-06-17 | 2016-07-29 | A |  | Mid-America Midstream Gas Services, L.L.C. (MAMGS) has applied for a permit to construct a new gas plant. A summary of the new emission sources authorized under this construction permit is presented below: â€¢ Ten 1,775-hp Caterpillar G3606 engines equipped with oxidation catalysts. â€¢ Two 9,443-hp Siemens SGT-200-2S turbines. â€¢ Two 2,889-hp Caterpillar G3520C IM emergency generators with oxidation catalysts. â€¢ Two 5.605-MMBTUH regeneration heaters. â€¢ Two 17.4-MMBTUH hot oil heaters. â€¢ Four 1,000-bbl condensate storage tanks controlled by flares. â€¢ Four 400-bbl produced water tanks. â€¢ Two 20,000-bbl/day amine units. â€¢ Two 2.66-MMBTUH emergency flares. â€¢ One 0.99-MMBTUH enclosed flare. Facility-wide gas processing capacity will be 460 MMSCFD. | This permit authorizes the construction of the Rose Valley Plant and addresses the regulatory requirements associated with the equipment which will be installed at that facility. | REGENERATION HEATERS | 13.31 | NATURAL GAS | 5.61 | MMBTUH | THERE ARE TO BE TWO IDENTICAL HEATERS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOx BURNERS | 0.045 | LB/MMBTU | 3-HR | BACT-PSD | N/A | U | 0 | U | 0.27 | LB/HR | 3-HR | 0 |  |  | 0 | 0 | N
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Auxiliary Boiler, 99.8 MMBtu/hr | 13.31 | Natural gas | 99.8 | MMBtu/hr | Fires only natural gas. Limited to 2000 hr/yr. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low-NOx burners | 0.05 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Method 7E testing, or manufacturer certification is sufficient
OK-0129 | CHOUTEAU POWER PLANT | ASSOCIATED ELECTRIC COOPERATIVE INC | MAYES | OK | 74362 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2007-115-C(M-1)PSD | 4911 | 221112 | 4009700017 | 06/19/2008 &nbsp;ACT | 01/23/2009 &nbsp;ACT | 2009-11-20 | 2010-02-18 | B |  |  |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 33.5 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOX BURNERS | 0.07 | LB/MMBTU |  | BACT-PSD | N/A , N/A | U | 0 | U | 2.36 | LB/H |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 42 | MMBTU/H | PIPELINE QUALITY NATURAL GAS FUEL ONLY, OPERATION OF ULTRA LOW-NOX BURNER TECHNOLOGY SUBJECT TO NSPS SUBPART DC RECORDKEEPING AND REPORTING REQUIREMENTS | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW-NOX BURNERS, AND GOOD COMBUSTION PRACTICES | 0.01 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0153 | ROSE VALLEY PLANT | SEMGAS LP | WOODS | OK | 73717 | USA | KRISTIN IKARD | 405-727-1443 | KRISTIN.IKARD@ACCESSMIDSTREAM.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2012-1393-C PSD | 1321 | 211112 | 151-00432 | 05/15/2012 &nbsp;ACT | 03/01/2013 &nbsp;ACT | 2014-06-17 | 2016-07-29 | A |  | Mid-America Midstream Gas Services, L.L.C. (MAMGS) has applied for a permit to construct a new gas plant. A summary of the new emission sources authorized under this construction permit is presented below: â€¢ Ten 1,775-hp Caterpillar G3606 engines equipped with oxidation catalysts. â€¢ Two 9,443-hp Siemens SGT-200-2S turbines. â€¢ Two 2,889-hp Caterpillar G3520C IM emergency generators with oxidation catalysts. â€¢ Two 5.605-MMBTUH regeneration heaters. â€¢ Two 17.4-MMBTUH hot oil heaters. â€¢ Four 1,000-bbl condensate storage tanks controlled by flares. â€¢ Four 400-bbl produced water tanks. â€¢ Two 20,000-bbl/day amine units. â€¢ Two 2.66-MMBTUH emergency flares. â€¢ One 0.99-MMBTUH enclosed flare. Facility-wide gas processing capacity will be 460 MMSCFD. | This permit authorizes the construction of the Rose Valley Plant and addresses the regulatory requirements associated with the equipment which will be installed at that facility. | HOT OIL HEATER | 13.31 | NATURAL GAS | 17.4 | MMBTUH | PROCESS PERTAINS TO TWO(2) IDENTICAL HEATERS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOx BURNERS. | 0.045 | LB/MMBTU | 3-HR | BACT-PSD | N/A | U | 0 | U | 0.83 | LB/HR | 3-HR | 0 |  |  | 0 | 0 | N
LA-0229 | SHINTECH PLAQUEMINE PLANT 2 | SHINTECH LOUISIANA LLC | IBERVILLE | LA | 70764 | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-731 | 2821 | 325211 | UNKNOWN | 11/19/2010 &nbsp;ACT | 07/10/2008 &nbsp;ACT | 2009-04-02 | 2009-04-20 | B |  | A PROPOSED 1.81 BILLION LBS/YR PVC PRODUCTION COMPLEX WHICH WILL CONSIST OF A CHLORALKALI PLANT, AN EDC/VCM PLANT, AND A PVC PLANT | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | EQT122-EQT125 - FOUR VCM CRACKING FURNACES | 13.31 | NATURAL GAS | 90 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SELECTIVE CATALYTIC REDUCTION (SCR) | 0.009 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0204 | PLAQUEMINE PVC PLANT | SHINTECH LOUISIANA LLC | IBERVILLE | LA |  | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: ANTHONY RANDALL, 225-219-3181 | PSD-LA-709(M-1) | 2821 | 325211 | 110020900104 | 03/03/2008 &nbsp;ACT | 02/27/2009 &nbsp;ACT | 2006-06-25 | 2009-08-06 | A |  | NEW 1.3 BILLION POUND PER YEAR PVC PLANT CONSISTING OF A CHLOR-ALKALI UNIT, AND EDC/VCM UNIT, AND A PVC UNIT. | VINYL CHLORIDE - 28.82 TPY. VINYL CHLORIDE (VC) WAS REGULATED AS A PSD POLLUTANT (SIGNIFICANCE LEVEL OF 1 TPY) IN LOUISIANA WHEN THIS PERMIT WAS ISSUED. LOUISIANA'S NSR REFORM RULES, ADOPTED DECEMBER 20, 2005, DELISTED VC. HAPS FROM THE PVC UNIT WERE SUBJECTED TO A 112(J) MACT DETERMINATION AFTER VACATURE OF 40 CFR 63 SUBPART J ON APRIL 19, 2005. BACT FOR VC IS EQUIVALENT TO MACT FOR VC. NNSR: BECAUSE VOC AND NOX EMISSIONS ARE LESS THAN 100 TPY, LAER WAS NOT REQUIRED. OFFSETS WERE REQUIRED PURSUANT TO A STATE-ONLY PROVISION IN LAC 33:III.504. PSD-LA-709(M-1) IS FOR 1) REMOVING A COOLING TOWER (M-8), CORRECTING CAPACITY OF COOLING TOWER M-7, AND 3) INCLUDING 19 EMERGENCY ENGINES AND THREE LOADING HOPPERS. | CRACKING FURNACES A-D | 13.31 |  | 90 | MMBTU/H EA. |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SELECTIVE CATALYTIC REDUCTION (SCR) | 0.009 | LB/MMBTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | dew point heater | 13.31 | natural gas | 13.32 | mmBtu/hr |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.013 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | auxiliary boiler | 13.31 | natural gas | 60.1 | mmBtu/hr | fuel limit of 288.7 million cubic feet of natural gas per 12-month rolling period | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.013 | LB/MMBTU | AVERAGE OF 3 ONE-HOUR TEST RUNS | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0693 | ANTELOPE ELK ENERGY CENTER | GOLDEN SPREAD ELECTRIC COOPERATIVE INC | HALE | TX |  | USA | JEFF PIPPIN | (806) 418-3010 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Laura Gibson 512-239-2175 laura.gibson@tceq.texas.gov | 109148 PSDTX1358 | 4911 | 221112 | 110043432737 | 04/01/2013 &nbsp;ACT | 04/22/2014 &nbsp;ACT | 2015-03-19 | 2016-07-29 | B |  | Golden Spread Electric Cooperative (GSEC) currently owns and operates Antelope Station (now renamed Antelope Elk Energy Center), a 168 MW generating facility made up of 18 quick start WÃ¤rtsilÃ¤ engines. GSEC is proposing to build a new combustion turbine-generator (CTG) facility at Antelope Station, while the 18 WÃ¤rtsilÃ¤ engines will remain and continue to be authorized by TCEQ Standard Permit. The new turbine-generator will provide primarily peaking and intermediate power needs in a highly cyclical operation. The CTG will produce approximately 100 - 200 MW of electricity, depending on loading and ambient temperature. |  | heater | 13.31 | natural gas | 5.5 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.036 | LB/MMBTU | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0285 | WHITING CLEAN ENERGY, INC. | WHITING CLEAN ENERGY, INC. | LAKE | IN | 46394 | USA |  |  |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Trip Sinha, Section Chief, 317-234-4907, TSinha@idem.in.gov Tamara Havics, permit writer, 317-232-8219, THavics@idem.in.gov | 089-37495-00449 | 4911 | 221112 | Not Found | 08/08/2016 &nbsp;ACT | 08/02/2017 &nbsp;ACT | 2018-05-02 | 2018-06-15 | C | HTTP://PERMITS.AIR.IDEM.IN.GOV/37495f.pdf | Industrial steam and 545 MWe co-generation (combined heat and power) plant |  | Space Heaters | 13.31 |  | 0 |  | (a) Six (6) Sterling TF-400 natural gas-fired space heaters, identified as HTR 1 through 6, constructed in 2000, with a maximum capacity of 0.4 MMBtu per hour, each, with low NOx burners, and exhausting to atmosphere. (b) Three (3) Carrier 48TCED natural gas-fired space heaters, identified as HTR 7 through 9, constructed in 2000, with a maximum capacity of 0.224 MMBtu per hour, each, and exhausting to atmosphere. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.05 | LB/MMBTU | UNITS 1-6, COMBUSTING NATURAL GAS | BACT-PSD |  | U | 0 | U | 0.092 | LB/MMBTU | UNITS 7-9, COMBUSTING NATURAL GAS | 0 |  |  | 0 | 0 | N |  | Additional PSD BACT NOx limit requirements: NOx emissions from Heaters 1 through 9 shall be controlled through the use of Good Combustion Practices. Heaters 1 through 9 shall combust only natural gas. The combined heat input to Heaters 1 through 6 shall not exceed 5,256 MMBtu per year. The combined heat input to Heaters 7 through 9 shall not exceed 1,766 MMBtu per year.
MI-0393 | RAY COMPRESSOR STATION | CONSUMERS ENERGY | MACOMB | MI | 48005-4510 | USA | AMY KAPUGA | 517-788-2201 | ADKAPUGA@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact Jeff Rathbun (permit engineer) for questions at 517-241-8072 | 206-09 | 4925 | 486210 | 110001845246 | 06/03/2010 &nbsp;ACT | 10/14/2010 &nbsp;ACT | 2012-06-21 | 2017-07-20 | B |  | Compressor Station |  | Reboiler (dehydrator with reboiler) | 13.31 | natural gas | 4.8 | MMBTU/H | 4.8 MMBTU/H reboiler | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.098 | LB/MMBTU | TEST METHOD | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | HEATER | 13.31 | NATURAL GAS | 1.7 | MMBTU/H | FUEL GAS HEATER | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.1 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LAER
TX-0680 | SONORA GAS PLANT | WTG SONORA GAS PLANT LLC | UPTON | TX |  | USA | ELENA HOFFMAN | (713) 983-0112 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 106139 PSDTX1316 | 1321 | 211112 | 110056413064 | 09/28/2012 &nbsp;ACT | 06/14/2013 &nbsp;ACT | 2015-03-13 | 2016-05-09 | B |  | The new Sonora Gas Plant will be a natural gas dehydration and natural gas liquids recovery and recompression plant. Pre-treated, sweet inlet natural gas will be received by pipeline into the facility, dehydrated, and then sent to the cryogenic natural gas liquids (NGL) recovery plant. Ethane and heavier hydrocarbons will be fractionated from the gas stream by refrigeration and transported for sales via pipeline. The residue gas stream will also be transported for sales via pipeline. |  | 2 Heaters | 13.31 | natural gas | 5 | MMBTU/H | two small heaters (~3 and 5 MMBtu/hr) | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.1 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0691 | PH ROBINSON ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | GALVESTON | TX |  | USA | CRAIG ECKBERG | (832) 357-5291 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 erik.hendrickson@tceq.texas.gov | 108182 PSDTX1346 | 4911 | 221112 | 110002345515 | 02/06/2013 &nbsp;ACT | 05/20/2014 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | NRG proposes to construct six natural gas-fired simple cycle combustion turbine generators (CTG) for peaking, designed to operate during periods of high electric demand. The six CTGs selected by NRG are General Electric Frame 7E turbines have an ISO rating of 65 MW and a nominal maximum generating capacity of 80 MW. Each of the turbines will not exceed 20 percent annual capacity (equivalent to 1,752 full load hours) in any single year or 10 percent annual capacity factor (equivalent to 876 full load hours) averaged over any three year period. |  | fuel gas heater | 13.31 | natural gas | 18 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.1 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0694 | INDECK WHARTON ENERGY CENTER | INDECK WHARTON, L.L.C. | WHARTON | TX |  | USA | JAMES SCHNEIDER | (847) 520-3212 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 111724 PSDTX1374 | 4911 | 221112 | unknown | 06/18/2013 &nbsp;ACT | 02/02/2015 &nbsp;ACT | 2015-03-19 | 2016-05-09 | A |  | Indeck Wharton, L.L.C. proposes to install three new natural gas fired combustion turbine generators (CTGs). The CTGs will either be the General Electric 7FA (~214 MW each) or the Siemens SGT6-5000F (~227 MW each), operating as peaking units in simple cycle mode. |  | heater | 13.31 | natural gas | 3 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.1 | LB/MMBTU | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0772 | PORT OF BEAUMONT PETROLEUM TRANSLOAD TERMINAL (PBPTT) | JEFFERSON RAILPORT TERMINAL I TEXAS LLC | ORANGE | TX |  | USA | PHILIP TREW | 409-239-5382 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Teresa Hurley, (512) 239-5316 Teresa.Hurley@tceq.texas.gov | 118901, GHGPSDTX108 AND PSDTX1 | 5171 | 424710 | 110055496379 | 09/21/2015 &nbsp;ACT | 11/06/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | Crude oil, condensate, bitumen storage and marine/railcar loading terminal |  | Commercial/Institutional-Size Boilers/Furnaces | 13.31 | natural gas | 13.2 | MMBTU/H | Boiler will be operated continuously to maintain system temperatures in the intermittent boilers and heavy liquid storage tanks. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.1 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N

## Low NOx Burners
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2018-06-25 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | Auxiliary Boiler | 13.31 | Natural Gas | 77.8 | mmBtu/hr | Annual emission based on 4600 hours/year. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LNB, FGR, Good Combustion Practices | 0.0011 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 1.96 | TONS/YEAR |  | 0.0011 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP26 | 13.31 | NATURAL GAS | 24 | MMBTU/H | UNIT CP26 IS A UNILUX BOILER AT CAESAR'S PALACE. THE UNIT IS ALLOWED TO OPERATE UP TO 8,760 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER | 0.0108 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 9 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0108 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP01 | 13.31 | NATURAL GAS | 35.4 | MMBTU/H | UNIT CP01 IS A HURST BOILER AT CAESAR'S PALACE. UNIT CP01 IS IDENTICAL TO UNIT CP02. UNITS CP01 THROUGH CP05 (FIVE BOILERS) ARE SUBJECT TO THE ANNUAL LIMIT OF TOTAL OPERATING TIME FOR 33,520 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER | 0.035 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 29 | PPMVD | CORRECTED TO 3% OXYGEN | 0.035 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP03 | 13.31 | NATURAL GAS | 33.48 | MMBTU/H | UNIT CP03 IS A BURNHAM BOILER AT CAESAR'S PALACE. UNITS CP01 THROUGH CP05 (FIVE BOILERS) ARE SUBJECT TO THE ANNUAL LIMIT OF TOTAL OPERATING TIME FOR 33,520 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER | 0.0367 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 30 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0367 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT FL01 | 13.31 | NATURAL GAS | 14.34 | MMBTU/H | UNIT FL01 IS A JOHNSTON BOILER AT FLAMINGO LAS VEGAS. THIS UNIT MAY OPERATE 8,760 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER AND FLUE GAS RECIRCULATION | 0.0353 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 29 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0353 | LB/MMBTU |  | 0 | 0 | N
FL-0335 | SUWANNEE MILL | KLAUSER HOLDING USA, INC. | SUWANNEE COUNTY | FL | 32060 | USA | MICHEL FUNK | 843-626-9600 | MICHAEL.FUNK@KLAUSNER-GROUP.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | David Read is the permitting engineer for this project, 850-717-9075. | 1210468-001-AC(PSD-FL-417) | 2421 | 321113 | Not Available | 01/09/2012 &nbsp;ACT | 09/05/2012 &nbsp;ACT | 2012-10-29 | 2013-05-30 | U |  | The Suwannee Mill produces dimensional kiln dried lumber and timber byproducts consisting of bark, wood chips, sawdust, and dry shavings. When the facility is fully constructed, the mill has a maximum annual production capacity of 700 MMBF/yr. The mill processes tree-length green saw logs into dimensional lumber. Raw materials, finished lumber and saleable by-products are received and dispatched from the facility by truck or rail. | The Suwannee Mill produces dimensional kiln dried lumber and timber byproducts consisting of bark, wood chips, sawdust, and dry shavings. When the facility is fully constructed, the mill has a maximum annual production capacity of 700 MMBF/yr. The mill processes tree-length green saw logs into dimensional lumber. Raw materials, finished lumber and saleable by-products are received and dispatched from the facility by truck or rail. The mill will operate kilns that heat the green rough sawn lumber to reduce the moisture content to meet required finished product market specifications. The kilns are heated with hot water that is generated in four natural gas-fired boilers (46 million British thermal units per hour (MMBtu/hr)) and two biomass-fired boilers (120 MMBtu/hr). The biomass boilers are fired by untreated bark, wood chips, and sawdust that are byproducts of the mills operation. Clean, untreated woody biomass obtained from off-site sources may also be fired in the biomass boilers | Four(4) Natural Gas Boilers - 46 MMBtu/hour | 13.31 | Natural Gas | 46 | MMBTU/H | The four natural gas boilers are used to generate the hot water that is used in the lumber kiln drying process. Two boilers each share a common stack for a total of two stacks. In the initial phase of construction, two natural gas fired boilers will supply hot water to one block of kilns. As other kiln blocks are completed, the two other natural gas boilers will be constructed and brought online. Finally, the two biomass boilers will be built and brought on line. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burner and Flue Gas Recirculation | 0.036 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) NATURAL GAS AUXILIARY BOILERS | 13.31 | NATURAL GAS | 80 | MMBTU/H | BOTH BOILERS, LABELED AS B001 AND B002, ARE EQUIPPED WITH LOW NOX BURNERS WITH FLUE GAS REGULATION. THIS IS CONSIDERED A STEAM GENERATING UNIT. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNER WITH FLUE GAS RECIRCULATION | 0.032 | LB/MMBTU | 3 HOURS | BACT-PSD |  |  | 50 |  | 2.56 | LB/H | 3 HOURS | 0 |  |  | 0 | 0 | N |  | LIMIT ONE AND TWO ARE FOR EACH BOILER
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | AUXILIARY BOILER | 13.31 | PIPELINE QUALITY NATURAL GAS | 93 | MMBTU/H | ONE AUXILIARY BOILER WITH ULTRA-LOW NOX BURNER (ULNB) AND FLUE GAS RECIRCULATION (FGR) SUBJECT TO NSPS SUBPART DC RECORDKEEPING AND REPORTING REQUIREMENTS | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER, EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS, AND APPLICATION OF GOOD COMBUSTION PRACTICES | 0.01 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0393 | RAY COMPRESSOR STATION | CONSUMERS ENERGY | MACOMB | MI | 48005-4510 | USA | AMY KAPUGA | 517-788-2201 | ADKAPUGA@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact Jeff Rathbun (permit engineer) for questions at 517-241-8072 | 206-09 | 4925 | 486210 | 110001845246 | 06/03/2010 &nbsp;ACT | 10/14/2010 &nbsp;ACT | 2012-06-21 | 2017-07-20 | B |  | Compressor Station |  | Auxiliary Boiler | 13.31 | natural gas | 12.25 | MMBTU/H | Boiler provides building heat. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx burner. | 0.035 | LB/MMBTU | TEST METHOD | BACT-PSD | N/A | N | 0.5 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Based on emission factor of 0.035 lb/MMBTU
TX-0772 | PORT OF BEAUMONT PETROLEUM TRANSLOAD TERMINAL (PBPTT) | JEFFERSON RAILPORT TERMINAL I TEXAS LLC | ORANGE | TX |  | USA | PHILIP TREW | 409-239-5382 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Teresa Hurley, (512) 239-5316 Teresa.Hurley@tceq.texas.gov | 118901, GHGPSDTX108 AND PSDTX1 | 5171 | 424710 | 110055496379 | 09/21/2015 &nbsp;ACT | 11/06/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | Crude oil, condensate, bitumen storage and marine/railcar loading terminal |  | Commercial/Institutional-Size Boilers/Furnaces | 13.31 | natural gas | 40 | MMBTU/H | Hot oil heater | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low NOx burners | 0.036 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0755 | RAMSEY GAS PLANT | DELAWARE BASIN MIDSTREAM LLC | REEVES | TX |  | USA | MICAH CARTER | 720-929-6788 | MICAH.CARTER@ANADARKO.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ozden Tamer, (512)239-4577, ozden.tamer@tceq.texas.gov | 117323 AND PSDTX1392,O-3546 | 1321 | 211112 | 110054879985 | 07/10/2015 &nbsp;ACT | 05/21/2015 &nbsp;ACT | 2015-07-20 | 2016-07-06 | B |  | Ramsey IV, V and VI Gas Plants and associated Amine I and II Plants. Each Ramsey Plant will have gas gathering, treating, conditioning, compression and processing capabilities. This expansion project will increase the processing capacity of the existing plant with three 200 MMSCF/day cryogenic plants and two amine plants with a combined capacity of 2000 gallon per minute (gpm). A percentage of the acid gas from the amine still vents (EPNs: A-4 and A-5) will be captured and routed to a pipeline for Carbon capture and Sequestration (CCS) purposes and the remaining acid gas from the amine still vents will be routed to the regenerative thermal oxidizers (EPNs: RTO-4 and RTO-5) |  | Hot Oil Heaters and Regeneration Heaters | 13.31 | Residue gas equivalent to natural gas | 60 | MMBTU/H | Hot Oil Heaters: 60 MMBtu/hr; Regeneration Heaters: 36 MMBtu/hr | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | low NOx burners | 0.045 | LB/MMBTU |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WY-0066 | MEDICINE BOW IGL PLANT | MEDICINE BOW FUEL & POWER | CARBON | WY |  | USA | ROBERT MOSS |  |  | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-5873 | 1311 | 324110 | 110009762051 | 06/20/2007 &nbsp;ACT | 03/04/2009 &nbsp;ACT | 2009-03-19 | 2009-04-20 | A |  | COAL TO LIQUIDS PLANT |  | GASIFICATION PREHEATER 2 | 13.31 | NATURAL GAS | 21 | MMBTU/H | 500 HOURS OF OPERATION | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNERS | 0.05 | LB/MMBTU | HOURLY | BACT-PSD |  | N | 0 | N | 1 | LB/H | HOURLY | 0.3 | T/YR | ANNUAL | 0 | 0 | N
WY-0066 | MEDICINE BOW IGL PLANT | MEDICINE BOW FUEL & POWER | CARBON | WY |  | USA | ROBERT MOSS |  |  | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-5873 | 1311 | 324110 | 110009762051 | 06/20/2007 &nbsp;ACT | 03/04/2009 &nbsp;ACT | 2009-03-19 | 2009-04-20 | A |  | COAL TO LIQUIDS PLANT |  | GASIFICATION PREHEATER 3 | 13.31 | NATURAL GAS | 21 | MMBTU/H | 500 HOURS OF OPERATION | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNERS | 0.05 | LB/MMBTU | HOURLY | BACT-PSD |  | N | 0 | U | 1 | LB/H | HOURLY | 0.3 | T/YR | ANNUAL | 0 | 0 | N
WY-0066 | MEDICINE BOW IGL PLANT | MEDICINE BOW FUEL & POWER | CARBON | WY |  | USA | ROBERT MOSS |  |  | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-5873 | 1311 | 324110 | 110009762051 | 06/20/2007 &nbsp;ACT | 03/04/2009 &nbsp;ACT | 2009-03-19 | 2009-04-20 | A |  | COAL TO LIQUIDS PLANT |  | GASIFICATION PREHEATER 4 | 13.31 | NATURAL GAS | 21 | MMBTU/H | 500 HOURS OF OPERATION | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNERS | 0.05 | LB/MMBTU | HOURLY | BACT-PSD |  | N | 0 | U | 1 | LB/H | HOURLY | 0.3 | T/YR | ANNUAL | 0 | 0 | N
WY-0066 | MEDICINE BOW IGL PLANT | MEDICINE BOW FUEL & POWER | CARBON | WY |  | USA | ROBERT MOSS |  |  | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-5873 | 1311 | 324110 | 110009762051 | 06/20/2007 &nbsp;ACT | 03/04/2009 &nbsp;ACT | 2009-03-19 | 2009-04-20 | A |  | COAL TO LIQUIDS PLANT |  | GASIFICATION PREHEATER 5 | 13.31 | NATURAL GAS | 21 | MMBTU/H | 500 HOURS OF OPERATION | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNERS | 0.05 | LB/MMBTU | HOURLY | BACT-PSD |  | N | 0 | U | 1 | LB/H | HOURLY | 0.3 | T/YR | ANNUAL | 0 | 0 | N
WY-0066 | MEDICINE BOW IGL PLANT | MEDICINE BOW FUEL & POWER | CARBON | WY |  | USA | ROBERT MOSS |  |  | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-5873 | 1311 | 324110 | 110009762051 | 06/20/2007 &nbsp;ACT | 03/04/2009 &nbsp;ACT | 2009-03-19 | 2009-04-20 | A |  | COAL TO LIQUIDS PLANT |  | GASIFICATION PREHEATER 1 | 13.31 | NATURAL GAS | 21 | MMBTU/H | 500 HOURS OF OPERATION | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNERS | 0.05 | LB/MMBTU | HOURLY | BACT-PSD |  | N | 0 | N | 1 | LB/H | HOURLY | 0.3 | T/YR | ANNUAL | 0 | 0 | N
SC-0112 | NUCOR STEEL - BERKELEY | NUCOR STEEL | BERKELEY | SC | 29450 | USA | RAY SIMS | 8433366123 | SIMSR@NUCORSTEEL.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MR. DENNIS CAMIT | (803)898-4284 | camitdr@dhec.sc.gov | WANDA PARNELL (803) 898-4123 | 0420-0060-DO | 3312 | 331111 | 110000353527 | 12/06/2007 &nbsp;ACT | 05/05/2008 &nbsp;ACT | 2012-05-09 | 2013-10-30 | D |  | SCRAP STEEL RECYCLING MILL |  | TUNNEL FURNACE BURNERS | 13.31 | NATURAL GAS | 58 | MMBTU/H | THIS PROJECT IS ADDING AN ADDITIONAL 58 MILLION BTU/HR HEAT INPUT TO EXISTING TUNNEL FURNACE SYSTEM. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNERS | 0.1 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0.1 | LB/MMBTU |  | 0 | 0 | N |  | THE EMISSION RATE WILL BE THE RATE FROM THE NEW BURNERS.
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Inlet Air Heater (EP07) | 13.31 | Natural Gas | 16.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.012 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 0.2 | LB/H | 3-HOUR AVERAGE | 0.4 | T/YR |  | 0 | 0 | N |  | limited to 4,380 hours of operation per calendar year
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Inlet Air Heater (EP08) | 13.31 | Natural Gas | 16.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.012 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 0.2 | LB/H | 3-HOUR AVERAGE | 0.4 | T/YR |  | 0 | 0 | N |  | limited to 4,380 hours of operation per calendar year
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Inlet Air Heater (EP09) | 13.31 | Natural Gas | 16.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.012 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 0.2 | LB/H | 3-HOUR AVERAGE | 0.4 | T/YR |  | 0 | 0 | N |  | limited to 4,380 hours of operation per calendar year
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Inlet Air Heater (EP10) | 13.31 | Natural Gas | 16.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.012 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 0.2 | LB/H | 3-HOUR AVERAGE | 0.4 | T/YR |  | 0 | 0 | N |  | limited to 4,380 hours of operation per calendar year
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Inlet Air Heater (EP11) | 13.31 | Natural Gas | 16.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.012 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 0.2 | LB/H | 3-HOUR AVERAGE | 0.4 | T/YR |  | 0 | 0 | N |  | limited to 4,380 hours of operation per calendar year
TX-0656 | GAS TO GASOLINE PLANT | NATGASOLINE | JEFFERSON | TX |  | USA | KEVIN STRUVE |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Cheryl Covone 512-239-1248 | PSDTX1340 AND 107764 | 2911 | 325199 | 110064577006 | 01/16/2013 &nbsp;ACT | 05/16/2014 &nbsp;ACT | 2014-05-20 | 2016-05-12 | A |  | Chemical Plant |  | Heaters | 13.31 | natural gas | 45 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low NOx Burners | 0.036 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0656 | GAS TO GASOLINE PLANT | NATGASOLINE | JEFFERSON | TX |  | USA | KEVIN STRUVE |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Cheryl Covone 512-239-1248 | PSDTX1340 AND 107764 | 2911 | 325199 | 110064577006 | 01/16/2013 &nbsp;ACT | 05/16/2014 &nbsp;ACT | 2014-05-20 | 2016-05-12 | A |  | Chemical Plant |  | heaters (5) | 13.31 | natural gas | 24.3 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low NOx Burners | 0.036 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WY-0075 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | MD-16173 | 491 | 221122 | Not Found | 05/01/2014 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2014-06-16 | 2018-05-11 | B |  | Nominal 220 megawatt (MW) gross electrical facility. | Installation of a 25.06 MMBtu/hr Auxiliary Boiler (Cleaver Brooks CBEX Elite 600). Subject to PSD based on project aggregation. | Auxiliary Boiler | 13.31 | natual gas | 25.06 | MMBtu/h |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.0175 | LB/MMBTU | 3 HOUR AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0.4 | LB/H | 3 HOUR AVERAGE | 0 |  |  | 0 | 0 | N
LA-0246 | ST. CHARLES REFINERY | VALERO REFINING - NEW ORLEANS, LLC | ST. CHARLES | LA | 70079 | USA | ROBERT MARTIN | 985-764-8611 | ROB.MARTIN@VALERO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - 225-219-3395 | PSD-LA-619(M6) | 2911 | 324110 | Not Applicable | 08/02/2010 &nbsp;ACT | 12/31/2010 &nbsp;ACT | 2011-03-29 | 2011-07-06 | C |  | A typical Petroleum Refinery |  | EQT0323 - Boiler 401F | 13.31 | refinery fuel | 99 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx Burners | 0.04 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 3.96 | LB/H | HOURLY MAXIMUM | 0 |  |  | 0 | 0 | N
WY-0070 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC. | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | CT-12636 | 491 | 221112 | Not Found | 03/01/2012 &nbsp;ACT | 08/28/2012 &nbsp;ACT | 2012-08-23 | 2018-05-11 | A |  | A nominal 220 megawatt (MW) gross electrical facility. The station is to consist of five (5) 40 MW GE LM6000 combustion turbine generators with two (2) of the turbines operating in combined cycle mode for an additional 20 MW in generation. |  | Inlet Air Heater (EP06) | 13.31 | Natural Gas | 16.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.012 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | N | 0 | U | 0.2 | LB/H | 3-HOUR AVERAGE | 0.4 | T/YR |  | 0 | 0 | N |  | limited to 4,380 hours of operation per calendar year
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Reactor Charge Heater - 53B001 | 13.31 | Natural Gas | 10.1 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.04 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.77 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.04 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002A | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.04 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 5.71 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.04 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002B | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.04 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 5.71 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.04 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002C | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.04 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 5.71 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.04 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002D | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.04 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 5.71 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.04 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002E | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.04 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 5.71 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.04 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Regeneraton Heater - 51B001 | 13.31 | Natural Gas | 61 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.04 | lb/MMBtu | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 10.69 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.04 LB/MMBTU (12-Month Rolling Average)
SC-0112 | NUCOR STEEL - BERKELEY | NUCOR STEEL | BERKELEY | SC | 29450 | USA | RAY SIMS | 8433366123 | SIMSR@NUCORSTEEL.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MR. DENNIS CAMIT | (803)898-4284 | camitdr@dhec.sc.gov | WANDA PARNELL (803) 898-4123 | 0420-0060-DO | 3312 | 331111 | 110000353527 | 12/06/2007 &nbsp;ACT | 05/05/2008 &nbsp;ACT | 2012-05-09 | 2013-10-30 | D |  | SCRAP STEEL RECYCLING MILL |  | VACUUM DEGASSER BOILER | 13.31 | NATURAL GAS | 50.21 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low NOx Burners | 0.035 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 1.76 | LB/H |  | 0.035 | LB/MMBTU |  | 0 | 0 | N
OR-0050 | TROUTDALE ENERGY CENTER, LLC | TROUTDALE ENERGY CENTER, LLC | MULTNOMAH | OR | 97060 | USA | WILLARD LADD | 914-468-2400 |  | 10 | OR001 | OREGON DEPT OF ENVIRONMENTAL QUALITY | JILL INAHARA | (503) 229-5001 | inahara.jill@deq.state.or.us | George Davis 503-229-5534 | 26-0235 | 4911 | 221112 | 110057118417 | 04/05/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2015-01-06 | 2016-05-05 | A |  | Troutdale Energy Center (TEC) proposes to construct and operate a 653 megawatt (MW) electric generating plant in Troutdale, Oregon. TEC proposes to generate electricity with three natural gas-fired turbines, one of which will be a combined-cycle unit with duct burner and heat recovery steam generator. |  | Auxiliary boiler | 13.31 | natural gas | 39.8 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners | 0.035 | LB/MMBTU | 3-HR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0772 | PORT OF BEAUMONT PETROLEUM TRANSLOAD TERMINAL (PBPTT) | JEFFERSON RAILPORT TERMINAL I TEXAS LLC | ORANGE | TX |  | USA | PHILIP TREW | 409-239-5382 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Teresa Hurley, (512) 239-5316 Teresa.Hurley@tceq.texas.gov | 118901, GHGPSDTX108 AND PSDTX1 | 5171 | 424710 | 110055496379 | 09/21/2015 &nbsp;ACT | 11/06/2015 &nbsp;ACT | 2015-11-05 | 2016-07-06 | A |  | Crude oil, condensate, bitumen storage and marine/railcar loading terminal |  | Commercial/Institutional-Size Boilers/Furnaces | 13.31 | natural gas | 95.7 | MMBTU/H | Three boilers will be used intermittently to provide steam for heating tanks or railcars as necessary to reduce viscosity of heavy liquids. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low NOx burners and flue gas recirculation | 0.011 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | Auxillary Boiler | 13.31 | Natural Gas | 99 | MMBtu/H | 99 MMBTU/H auxillary boiler with low-NOx burners and flue gas re-circulation, burning only natural gas. Boiler restricted to 2000 hours of operation per rolling 12-months. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | low NOx burners and flue gas recirculation | 0.02 | LB/MMBTU |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 1.98 | T/YR | PER ROLLING 12-MONTHS | 0.02 | LB/MMBTU |  | 0 | 0 | N |  | BACT: 0.020 LB/MMBTU. Restricted to 2000 hours of operation per rolling 12-months.
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGAUXBOILERS: Two auxiliary boilers &lt; 100 MMBTU/H heat input each | 13.31 | natural gas | 100 | MMBTU/H heat input each | There are two auxiliary boilers each rated at less than 100 MMBTU/H heat input. Fuel usage limited to not more than 416.3 MMscf of natural gas in each boiler per 12-month rolling timeperiod as determined at the end of each month. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners and flue gas recirculation. | 0.05 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | N/A | N | 70 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is 0.05 LB/MMBTU heat input, for each boiler. Test protocol will specify the averaging time. Fuel usage limited to not more tahn 416.3 MMSCF of natural gas in each boiler per 12-month rolling time period as determined at the end of each month.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler A (EUAUXBOILERA) | 13.31 | natural gas | 55 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 55 MMBTU/hr fuel heat input (EUAUXBOILERA within flexible group FGAUXBOILERS). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners and good combustion practices | 0.05 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 70 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Low NOx burners (LNB) with flue gas recirculation is greater than $8,000/ton for NOx. The efficiency range for LNB alone is 40-70 percent.
MI-0421 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions related to the permit. Thank you. | 59-16 | 2493 | 321219 | Not Found | 06/30/2016 &nbsp;ACT | 08/26/2016 &nbsp;ACT | 2017-01-27 | 2017-07-20 | A |  | Particleboard manufacturing |  | EUFLTOS1 in FGTOH (Thermal Oil System for Thermally Fused Lamination Lines) | 13.31 | Natural gas | 34 | MMBTU/H | One natural gas fired thermal oil system for thermally fused lamination lines rated at 10.2 MMBTU/H fuel heat input (EUFLTOS1 in FGTOH). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners and good design and combustion practices. | 0.05 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 50 | N | 2.2 | T/YR | BASED UPON A 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | SCR is not economically feasible for the press/sifter thermal oil heater with a cost of $27,000/ton. Given this high cost for the larger heater, SCR would also not be cost effective for the smaller heater.
MI-0421 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions related to the permit. Thank you. | 59-16 | 2493 | 321219 | Not Found | 06/30/2016 &nbsp;ACT | 08/26/2016 &nbsp;ACT | 2017-01-27 | 2017-07-20 | A |  | Particleboard manufacturing |  | EUTOH (In FGTOH)--Thermal Oil Heater | 13.31 | Natural gas | 34 | MMBTU/H | One natural gas fired thermal oil heater for press and sifter rated at 34 MMBTU/H fuel heat input (EUTOH in FGTOH). All falls under RBLC Process Type Code 30.590. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners and good design and combustion practices. | 0.05 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 50 | N | 7.3 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | The company conducted a cost analysis for SCR for the press/sifter thermal oil heater. The results show that SCR is not economically feasible with a cost of $27,000/ton.
WY-0067 | ECHO SPRINGS GAS PLANT | WILLIAMS FIELD SERVICES COMPANY | CARBON | WY | 82336 | USA | CORTNIE MORRELL | 3078722880 | CORTNIE.MORRELL@WILLIAMS.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov | MS. JAMIE SHARP WY DEQ AIR QUALITY DIVISION 122 WEST 25TH STREET CHEYENNE, WY 82002 307-777-7817 | MD-7837 | 1321 | 211112 | 110010144628 | 05/29/2008 &nbsp;ACT | 04/01/2009 &nbsp;ACT | 2009-04-02 | 2009-04-16 | A |  |  |  | HOT OIL HEATER S38 | 13.31 | NATURAL GAS | 84 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNERS WITH FLUE GAS RECIRCULATION | 0.03 | LB/MMBTU |  | BACT-PSD | NSPS , NESHAP | N | 0 | N | 11 | T/YR |  | 0 |  |  | 0 | 0 | N |  | 60-90% ESTIMATED EFFICIENCY
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, PICKLE LINE | 13.31 | NATURAL GAS | 67 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.035 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILERS SN-26 AND 27, GALVANIZING LINE | 13.31 | NATURAL GAS | 24.5 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.035 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS SCR COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.1 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler B (EUAUXBOILERB) | 13.31 | natural gas | 95 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 95 MMBtu/hr fuel heat input (EUAUXBOILERB within flexible group FGAUXBOILERS). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | low NOx burners, flue gas recirculation and good combustion practices. | 0.05 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 80 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Selective catalytic reduction is greater than $11,000/ton for NOx. The efficiency range for Low NOx burners and flue gas recirculation is 60-85 percent.
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUTOH in FGTOH | 13.31 | Natural gas | 38 | MMBTU/H | One natural gas-fired thermal oil heater for press and sifter rated at 38 MMBTU/hr fuel heat input (EUTOH in FGTOH). Also falls under the RBLC Process Type Code 30.590. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners. | 0.05 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 50 | N | 8.16 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | The company conducted a cost analysis for SCR for the press/sifter thermal oil heater. The results show that SCR is not economically feasible, with a cost of $27,000/ton. The small increase in heat input capacity (4 MMBTU/HR) does not make add on control cost effective.
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUFLTOS1 in FGTOH | 13.31 | Natural gas | 10.2 | MMBTU/H | One natural gas-fired thermal oil system for thermally fused lamination lines rated at 10.2 MMBTU/H fuel heat input (EUFLTOS1 in FGTOH). Note: The throughput capacity, 10.2 MMBTU/H, is not a change but instead a correction from the previous entry. The previous entry is under MI-0421 for the original permit. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners. | 0.05 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 50 | N | 2.2 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | SCR is not economically feasible for the press/sifter thermal oil heater, with a cost of $27,000 per ton. Given this high cost for the larger heater, SCR would also not be cost effective for the smaller heater.
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUAUXBOILER (North Plant): Auxiliary Boilder | 13.31 | Natural gas | 61.5 | MMBTU/H | A natural gas-fired auxiliary boiler, rated at 61.5 MMBTU/H (HHV) to facilitate startup of the CTGHRSG train and to provide the required steam to support the startup of the facility, including but not limited to steam for sparging, STG seals, etc. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners/flue gas recirculation and good combustion practices. | 0.04 | LB/MMBTU | 30-DAY ROLLING AVG TIME PERIOD | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Selective catalytic reduction (SCR) was calculated to be over $18,000/ton for NOx.
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUAUXBOILER (South Plant): Auxiliary Boiler | 13.31 | Natural gas | 61.5 | MMBTU/h | A natural gas-fired auxiliary boiler, rated at 61.5 MMBTU/H (HHV) to facilitate startup of the CTGHRSG train and to provide the required steam to support the startup of the facility, including but not limited to steam for sparging, STG seals, etc. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners/flue gas recirculation and good combustion practices. | 0.04 | LB/MMBTU | 30 DAY ROLLING AVG TIME PERIOD | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Selective catalytic reduction (SCR) was calculated to be over $18,000/ton for NOx.
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUAUXBOILER: Auxiliary Boiler | 13.31 | Natural gas | 99.9 | MMBTU/H | A natural gas-fired auxiliary boiler, rated at 99.9 MMBTU/H to facilitate startup of the CTG/HRSG trains and to provide steam to the steam turbine generator seals. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low NOx burners/Flue gas recirculation. | 0.036 | LB/MMBTU | HOURLY | BACT-PSD | SIP | N | 0 | N | 3.6 | LB/H | HOURLY | 0 |  |  | 0 | 0 | N |  | The cost of selective catalytic reduction (SCR) is over $100,000 for the project.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUAUXBOILER (Auxiliary boiler) | 13.31 | natural gas | 83.5 | MMBTU/H | One natural gas fired auxiliary boiler rated at 83.5 MMBTU/hr fuel heat input (EUAUXBOILER). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners/Internal flue gas recirculation and good combustion practices. | 0.05 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 70 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Selective catalytic reduction (SCR) is greater than $12,000/ton for NOx.
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | BOILER | 13.31 | NATURAL GAS | 93 | MMBTU/H | AUXILIARY BOILER | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX WITH FGR | 0.011 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LAER
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT BA03 | 13.31 | NATURAL GAS | 31.38 | MMBTU/H | UNIT BA03 IS A KIWANEE BOLER AT BALLY'S LAS VEGAS. THE ANNUAL OPERATING TIME IS LIMITED TO 2,920 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOX BURNER | 0.0306 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 25 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0306 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT BA01 | 13.31 | NATURAL GAS | 16.8 | MMBTU/H | UNIT BA01 IS A KEWANEE BOILER AT BALLY'S LAS VEGAS. UNIT BA01 IS IDENTICAL TO UNIT BA02. THE TWO BOILERS ARE SUBJECT TO THE ANNUAL LIMIT OF COMBINED TOTAL OPERATING TIME FOR 10,900 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOX BURNER AND BLUE GAS RECIRCULATION | 0.03 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 25 | PPMVD | CORRECTED TO 3% OXYGEN | 0.03 | LB/MMBTU |  | 0 | 0 | N
TX-0680 | SONORA GAS PLANT | WTG SONORA GAS PLANT LLC | UPTON | TX |  | USA | ELENA HOFFMAN | (713) 983-0112 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 106139 PSDTX1316 | 1321 | 211112 | 110056413064 | 09/28/2012 &nbsp;ACT | 06/14/2013 &nbsp;ACT | 2015-03-13 | 2016-05-09 | B |  | The new Sonora Gas Plant will be a natural gas dehydration and natural gas liquids recovery and recompression plant. Pre-treated, sweet inlet natural gas will be received by pipeline into the facility, dehydrated, and then sent to the cryogenic natural gas liquids (NGL) recovery plant. Ethane and heavier hydrocarbons will be fractionated from the gas stream by refrigeration and transported for sales via pipeline. The residue gas stream will also be transported for sales via pipeline. |  | Heater | 13.31 | natural gas | 10 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | low-NOx burners | 0.01 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0714 | S R BERTRON ELECTRIC GENERATING STATION | NRG TEXAS POWER LLC | HARRIS | TX |  | USA | CRAIG ECKBERG | (713) 537-2146 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | 102731 PSDTX1294 | 4911 | 221112 | 110034988413 | 05/10/2012 &nbsp;ACT | 12/19/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | NRG Texas is proposing to construct an additional electric power generation station at the Bertron Power Project which will generate electric power for sale on the wholesale electric market. The Bertron Power Project will include two power blocks that can be operated in combined cycle mode. |  | boiler | 13.31 | natural gas | 80 | MMBTU/H | operation limitation of 4,000 hours per year | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | low-NOx burners | 0.036 | LB/MMBTU | 3-HR ROLLING | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0148 | BUFFALO CREEK PROCESSING PLANT | MARKWEST BUFFALO CREEK GAS CO LLC | BECKHAM | OK | 73662 | USA | KRISTIN IKARD |  | KRISTIN.IKARD@ACCESSMIDSTREAM.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2012-1026-C PSD | 1321 | 211112 | Not Found | 02/21/2012 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2014-06-13 | 2018-05-11 | A |  | Mid-America Midstream Gas Services (MAMGS)proposes to construct a natural gas plant with ten natural gas-fired reciprocating internal combustion engines, two natural gas-fired turbines, a 230-MMSCFD amine unit with a 11.04 MMBTUH reboiler, an acid gas flare, eight condensate tanks, and six produced water tanks. Associated support operations include condensate truck loading, blowdowns and fugitive emissions. | FRS Entered as &lsquo;&lsquo;009-00118&lsquo;&lsquo;. Too short for a FRS. MAMGS proposes to construct a natural gas plant with ten natural gas-fired reciprocating internal combustion engines, two natural gas-fired turbines, a 230-MMSCFD amine unit with a 11.04 MMBTUH reboiler, an acid gas flare, eight condensate tanks, and six produced water tanks. Associated support operations include condensate truck loading, blowdowns and fugitive emissions. | Commercial/Institutional Boilers (&lt;100 MMBTUH) | 13.31 | Natural Gas | 11.04 | MMBTUH |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low-NOx burners | 0.045 | LB/MMBTU |  | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0153 | ROSE VALLEY PLANT | SEMGAS LP | WOODS | OK | 73717 | USA | KRISTIN IKARD | 405-727-1443 | KRISTIN.IKARD@ACCESSMIDSTREAM.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2012-1393-C PSD | 1321 | 211112 | 151-00432 | 05/15/2012 &nbsp;ACT | 03/01/2013 &nbsp;ACT | 2014-06-17 | 2016-07-29 | A |  | Mid-America Midstream Gas Services, L.L.C. (MAMGS) has applied for a permit to construct a new gas plant. A summary of the new emission sources authorized under this construction permit is presented below: â€¢ Ten 1,775-hp Caterpillar G3606 engines equipped with oxidation catalysts. â€¢ Two 9,443-hp Siemens SGT-200-2S turbines. â€¢ Two 2,889-hp Caterpillar G3520C IM emergency generators with oxidation catalysts. â€¢ Two 5.605-MMBTUH regeneration heaters. â€¢ Two 17.4-MMBTUH hot oil heaters. â€¢ Four 1,000-bbl condensate storage tanks controlled by flares. â€¢ Four 400-bbl produced water tanks. â€¢ Two 20,000-bbl/day amine units. â€¢ Two 2.66-MMBTUH emergency flares. â€¢ One 0.99-MMBTUH enclosed flare. Facility-wide gas processing capacity will be 460 MMSCFD. | This permit authorizes the construction of the Rose Valley Plant and addresses the regulatory requirements associated with the equipment which will be installed at that facility. | REGENERATION HEATERS | 13.31 | NATURAL GAS | 5.61 | MMBTUH | THERE ARE TO BE TWO IDENTICAL HEATERS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOx BURNERS | 0.045 | LB/MMBTU | 3-HR | BACT-PSD | N/A | U | 0 | U | 0.27 | LB/HR | 3-HR | 0 |  |  | 0 | 0 | N
FL-0356 | OKEECHOBEE CLEAN ENERGY CENTER | FLORIDA POWER & LIGHT | OKEECHOBEE | FL | 34972 | USA | JOHN HAMPP |  | JOHN.HAMPP@FPL.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us | John Dawson, john.dawson@dep.state.fl.us, 850-717-9085 | 0930117-001-AC | 4911 | 221112 | Unknown | 09/25/2015 &nbsp;ACT | 03/09/2016 &nbsp;ACT | 2016-03-14 | 2016-07-06 | A | http://depedms.dep.state.fl.us:80/Oculus/servlet/shell?command=getEntity&[guid=75.93290.1]&[profile=Permitting_Authorization] | Fossil-fueled power plant, consisting of a 3-on-1 combined cycle unit and auxiliary equipment. The combined cycle unit consists of three GE 7HA.02 turbines, each with nominal generating capacity of 350 MW. The total generating capacity for the combined cycle unit is 1,600 MW. | Technical evaluation of project available at http://depedms.dep.state.fl.us/Oculus/servlet/shell?command=getEntity&[guid=75.89000.1]&[profile=Permitting_Authorization] | Auxiliary Boiler, 99.8 MMBtu/hr | 13.31 | Natural gas | 99.8 | MMBtu/hr | Fires only natural gas. Limited to 2000 hr/yr. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low-NOx burners | 0.05 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Method 7E testing, or manufacturer certification is sufficient
OK-0129 | CHOUTEAU POWER PLANT | ASSOCIATED ELECTRIC COOPERATIVE INC | MAYES | OK | 74362 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2007-115-C(M-1)PSD | 4911 | 221112 | 4009700017 | 06/19/2008 &nbsp;ACT | 01/23/2009 &nbsp;ACT | 2009-11-20 | 2010-02-18 | B |  |  |  | AUXILIARY BOILER | 13.31 | NATURAL GAS | 33.5 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOX BURNERS | 0.07 | LB/MMBTU |  | BACT-PSD | N/A , N/A | U | 0 | U | 2.36 | LB/H |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 42 | MMBTU/H | PIPELINE QUALITY NATURAL GAS FUEL ONLY, OPERATION OF ULTRA LOW-NOX BURNER TECHNOLOGY SUBJECT TO NSPS SUBPART DC RECORDKEEPING AND REPORTING REQUIREMENTS | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW-NOX BURNERS, AND GOOD COMBUSTION PRACTICES | 0.01 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0153 | ROSE VALLEY PLANT | SEMGAS LP | WOODS | OK | 73717 | USA | KRISTIN IKARD | 405-727-1443 | KRISTIN.IKARD@ACCESSMIDSTREAM.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2012-1393-C PSD | 1321 | 211112 | 151-00432 | 05/15/2012 &nbsp;ACT | 03/01/2013 &nbsp;ACT | 2014-06-17 | 2016-07-29 | A |  | Mid-America Midstream Gas Services, L.L.C. (MAMGS) has applied for a permit to construct a new gas plant. A summary of the new emission sources authorized under this construction permit is presented below: â€¢ Ten 1,775-hp Caterpillar G3606 engines equipped with oxidation catalysts. â€¢ Two 9,443-hp Siemens SGT-200-2S turbines. â€¢ Two 2,889-hp Caterpillar G3520C IM emergency generators with oxidation catalysts. â€¢ Two 5.605-MMBTUH regeneration heaters. â€¢ Two 17.4-MMBTUH hot oil heaters. â€¢ Four 1,000-bbl condensate storage tanks controlled by flares. â€¢ Four 400-bbl produced water tanks. â€¢ Two 20,000-bbl/day amine units. â€¢ Two 2.66-MMBTUH emergency flares. â€¢ One 0.99-MMBTUH enclosed flare. Facility-wide gas processing capacity will be 460 MMSCFD. | This permit authorizes the construction of the Rose Valley Plant and addresses the regulatory requirements associated with the equipment which will be installed at that facility. | HOT OIL HEATER | 13.31 | NATURAL GAS | 17.4 | MMBTUH | PROCESS PERTAINS TO TWO(2) IDENTICAL HEATERS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOx BURNERS. | 0.045 | LB/MMBTU | 3-HR | BACT-PSD | N/A | U | 0 | U | 0.83 | LB/HR | 3-HR | 0 |  |  | 0 | 0 | N
[40 empty] | min | 0.0011
[40 empty] | max | 0.1