## All Pollutants_Small Gas Boiler
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | Auxillary Boiler | 13.31 | Natural Gas | 99 | MMBtu/H | 99 MMBTU/H auxillary boiler with low-NOx burners and flue gas re-circulation, burning only natural gas. Boiler restricted to 2000 hours of operation per rolling 12-months. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Clean burning fuel, only burning natural gas | 0.008 | LB/MMBTU |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.79 | T/YR | PER ROLLING 12-MONTHS | 0.008 | LB/MMBTU |  | 0 | 0 | N |  | Limit is for PM10 and PM2.5 together. BACT: 0.008 LB/MMBTU. Restricted to 2000 hours of operation per rolling 12-months.
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002A | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002B | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002C | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002D | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002E | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Regeneraton Heater - 51B001 | 13.31 | Natural Gas | 61 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.99 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Reactor Charge Heater - 53B001 | 13.31 | Natural Gas | 10.1 | MMBTU/HR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0.33 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002A | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002B | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002C | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002D | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002E | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Regeneraton Heater - 51B001 | 13.31 | Natural Gas | 61 | MMBTU/HR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.99 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Reactor Charge Heater - 53B001 | 13.31 | Natural Gas | 10.1 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.008 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0.33 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Hour Rolling Average)
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 5.2 | X10^-4 LB/MMBTU |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, PICKLE LINE | 13.31 | NATURAL GAS | 67 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 5.2 | X10^-4 LB/MMBTU |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 5.2 | X10^-4 LB/MMBTU |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILERS SN-26 AND 27, GALVANIZING LINE | 13.31 | NATURAL GAS | 24.5 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 5.2 | X10^-4 LB/MMBTU |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, PICKLE LINE | 13.31 | NATURAL GAS | 67 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 5.2 | X10^-4 LB/MMBTU |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 5.2 | X10^-4 LB/MMBTU |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILERS SN-26 AND 27, GALVANIZING LINE | 13.31 | NATURAL GAS | 24.5 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 5.2 | X10^-4 LB/MMBTU |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, PICKLE LINE | 13.31 | NATURAL GAS | 67 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | AUXILIARY BOILER | 13.31 | PIPELINE QUALITY NATURAL GAS | 93 | MMBTU/H | ONE AUXILIARY BOILER WITH ULTRA-LOW NOX BURNER (ULNB) AND FLUE GAS RECIRCULATION (FGR) SUBJECT TO NSPS SUBPART DC RECORDKEEPING AND REPORTING REQUIREMENTS | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP EFFICIENT BOILER DESIGN, EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS, AND APPLICATION OF GOOD COMBUSTION PRACTICES | 0.0075 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | AUXILIARY BOILER | 13.31 | PIPELINE QUALITY NATURAL GAS | 93 | MMBTU/H | ONE AUXILIARY BOILER WITH ULTRA-LOW NOX BURNER (ULNB) AND FLUE GAS RECIRCULATION (FGR) SUBJECT TO NSPS SUBPART DC RECORDKEEPING AND REPORTING REQUIREMENTS | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP EFFICIENT BOILER DESIGN, EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS, AND APPLICATION OF GOOD COMBUSTION PRACTICES | 0.0075 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGAUXBOILERS: Two auxiliary boilers &lt; 100 MMBTU/H heat input each | 13.31 | natural gas | 100 | MMBTU/H heat input each | There are two auxiliary boilers each rated at less than 100 MMBTU/H heat input. Fuel usage limited to not more than 416.3 MMscf of natural gas in each boiler per 12-month rolling timeperiod as determined at the end of each month. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Efficient combustion; natural gas fuel. | 0.0018 | LB/MMBTU | HEAT INPUT; TEST PROTOCOL WILL SPECIFY | BACT-PSD | N/A | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is 0.0018 LB/MMBTU heat input for each boiler. Test protocol will specify the averaging time. The fuel usage is limited to not more than 416.3 MMSCF of natural gas in each boiler per 12-month rolling time period as determined at the end of each month.
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGAUXBOILERS: Two auxiliary boilers &lt; 100 MMBTU/H heat input each | 13.31 | natural gas | 100 | MMBTU/H heat input each | There are two auxiliary boilers each rated at less than 100 MMBTU/H heat input. Fuel usage limited to not more than 416.3 MMscf of natural gas in each boiler per 12-month rolling timeperiod as determined at the end of each month. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Efficient combustion; natural gas fuel. | 0.007 | LB/MMBTU | HEAT INPUT; TEST PROTOCOL SPECIFY AVG | BACT-PSD | N/A | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is 0.007 LB/MMBTU heat input for each boiler. Test protocol will specify averaging time. Fuel usage is limited to not more than 416.3 MMscf of natural gas in each boiler per 12 month rolling time period as determined at the end of each month
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGAUXBOILERS: Two auxiliary boilers &lt; 100 MMBTU/H heat input each | 13.31 | natural gas | 100 | MMBTU/H heat input each | There are two auxiliary boilers each rated at less than 100 MMBTU/H heat input. Fuel usage limited to not more than 416.3 MMscf of natural gas in each boiler per 12-month rolling timeperiod as determined at the end of each month. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Efficient combustion; natural gas fuel. | 0.007 | LB/MMBTU | HEAT INPUT; TEST PROTOCOL WILL SPECIFY | BACT-PSD | N/A | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is 0.007 LB/MMBTU heat input for each boiler. Test protocol will specify the averaging time. Fuel usage is limited to not more than 416.3 MMscf of natural gas in each boiler per 12 month rolling time period as determined at the end of each month.
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | AUXILLARY BOILER | 13.31 | NATURAL GAS | 45 | MMBTU/H | NATURAL GAS FUEL ONLY, OPERATION OF ULTRA LOW-NOX BURNER TECHNOLOGY, GOOD COMBUSTION PRACTICES, MAX HEAT INPUT OF 90,000 MMBUT/HR PER 12-MONTH ROLLING PERIOD | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES | 0.0075 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | AUXILLARY BOILER | 13.31 | NATURAL GAS | 45 | MMBTU/H | NATURAL GAS FUEL ONLY, OPERATION OF ULTRA LOW-NOX BURNER TECHNOLOGY, GOOD COMBUSTION PRACTICES, MAX HEAT INPUT OF 90,000 MMBUT/HR PER 12-MONTH ROLLING PERIOD | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES | 0.0075 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | AUXILLARY BOILER | 13.31 | NATURAL GAS | 45 | MMBTU/H | NATURAL GAS FUEL ONLY, OPERATION OF ULTRA LOW-NOX BURNER TECHNOLOGY, GOOD COMBUSTION PRACTICES, MAX HEAT INPUT OF 90,000 MMBUT/HR PER 12-MONTH ROLLING PERIOD | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES | 0.0075 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
SC-0112 | NUCOR STEEL - BERKELEY | NUCOR STEEL | BERKELEY | SC | 29450 | USA | RAY SIMS | 8433366123 | SIMSR@NUCORSTEEL.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MR. DENNIS CAMIT | (803)898-4284 | camitdr@dhec.sc.gov | WANDA PARNELL (803) 898-4123 | 0420-0060-DO | 3312 | 331111 | 110000353527 | 12/06/2007 &nbsp;ACT | 05/05/2008 &nbsp;ACT | 2012-05-09 | 2013-10-30 | D |  | SCRAP STEEL RECYCLING MILL |  | TUNNEL FURNACE BURNERS | 13.31 | NATURAL GAS | 58 | MMBTU/H | THIS PROJECT IS ADDING AN ADDITIONAL 58 MILLION BTU/HR HEAT INPUT TO EXISTING TUNNEL FURNACE SYSTEM. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP NATURAL GAS COMBUSTION WITH GOOD COMBUSTION PRACTICES PER MANUFACTURER'S GUIDANCE | 0.0076 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0.0076 | LB/MMBTU |  | 0 | 0 | N
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Auxillary Boiler | 13.31 | Natural gas | 13.31 | MMBtu/hr | Fired only on natural gas supplied by a public utility. Limited to 4000 hrs per year on a 12 month rolling basis. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.002 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 0.69 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
OK-0128 | MID AMERICAN STEEL ROLLING MILL | MID AMERICAN STEEL AND WIRE COMPANY | MARSHALL | OK | 73446 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2003-106-C(M-1) PSD | 3312 | 331111 | 110022524062 | 03/26/2008 &nbsp;ACT | 09/08/2008 &nbsp;ACT | 2008-12-31 | 2010-12-17 | B |  | THE FACILITY WAS CONSTRUCTED UNDER PERMIT NO. 2003-106-C ISSUED MARCH 25, 2003, AND IS CURRENTLY OPERATED UNDER PERMIT NO. 2003-106-O ISSUED JANUARY 3, 2005. THE FACILITY CURRENTLY OPERATES A SINGLE 74 MMBTUH GAS-FIRED FURNACE FOR SOFTENING STEEL BILLETS SO THAT THEY CAN BE DRAWN IN TO WIRE. | MID AMERICAN PROPOSES TO INSTALL TWO ELECTRIC ARC STEEL MELTING FURNACES. THE FURNACES WERE FABRICATED IN 2000 FOR INSTALLATION AT ANOTHER COMPANY SITE THAT WAS NOT CONSTRUCTED, THE PROPOSED GRIFFIN WHEEL PLANT AT TULSA. THE PROPOSED FURNACES WILL BE CAPABLE OF PRODUCING A TOTAL OF APPROXIMATELY 80 TONS/HR (640,000 TONS PER YEAR) OF Â¿BILLETÂ¿ Â¿ (BAR-SHAPED INGOTS) STEEL. THE STEEL MAY BE USED ON-SITE IN THE EXISTING WIRE PRODUCTION UNIT OR SOLD TO OTHER MILLS. | Ladle pre-heater and refractory drying | 13.31 | natural gas | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.0076 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0173 | CMC STEEL OKLAHOMA | COMMERCIAL METALS COMPANY | BRYAN | OK | 74701 | USA | RANDALL WALKER | 830-372-8507 | RANDALL.WALKER@CMC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2015-0643-C PSD | 3312 | 331111 | 013-00047 | 09/09/2015 &nbsp;ACT | 01/19/2016 &nbsp;ACT | 2016-01-19 | 2016-07-07 | A |  | In this steel mill, CMC will manufacture steel products from scrap steel. Iron ore will not be processed at the mill. Scrap metal will be transported into the facility to be used as feedstock for the Melt Shop. Once the molten steel reaches the desired conditions, it will be transferred to a large refractory-lined vessel known as a ladle. The ladle will be transported to a continuous caster, where the steel will be poured into a refractory-lined surge vessel called a tundish and subsequently into a water-cooled mold. After casting, the continuous steel strand will be rolled to the desired shape. After rolling, the steel will be cooled, bundled, and stored. To produce some structural material such as angles and channels, the rebar will be unbundled and passed through a straightener roller process. The finished products will be shipped off-site by truck as needed for use by customers. | Emissions of NOx, CO, VOC, SO2,PM10/PM2.5, and GHG exceed the applicable SER. Therefore, each is subject to PSD review. | Heaters (Gas-Fired) | 13.31 | Natural Gas | 0 |  | Numerous gas-fired heaters will be installed. The application requested that the sizes all be kept confidential. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.0076 | LB/MMBTU |  | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0173 | CMC STEEL OKLAHOMA | COMMERCIAL METALS COMPANY | BRYAN | OK | 74701 | USA | RANDALL WALKER | 830-372-8507 | RANDALL.WALKER@CMC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2015-0643-C PSD | 3312 | 331111 | 013-00047 | 09/09/2015 &nbsp;ACT | 01/19/2016 &nbsp;ACT | 2016-01-19 | 2016-07-07 | A |  | In this steel mill, CMC will manufacture steel products from scrap steel. Iron ore will not be processed at the mill. Scrap metal will be transported into the facility to be used as feedstock for the Melt Shop. Once the molten steel reaches the desired conditions, it will be transferred to a large refractory-lined vessel known as a ladle. The ladle will be transported to a continuous caster, where the steel will be poured into a refractory-lined surge vessel called a tundish and subsequently into a water-cooled mold. After casting, the continuous steel strand will be rolled to the desired shape. After rolling, the steel will be cooled, bundled, and stored. To produce some structural material such as angles and channels, the rebar will be unbundled and passed through a straightener roller process. The finished products will be shipped off-site by truck as needed for use by customers. | Emissions of NOx, CO, VOC, SO2,PM10/PM2.5, and GHG exceed the applicable SER. Therefore, each is subject to PSD review. | Heaters (Gas-Fired) | 13.31 | Natural Gas | 0 |  | Numerous gas-fired heaters will be installed. The application requested that the sizes all be kept confidential. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.0076 | LB/MMBTU |  | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0104 | CPV VALLEY ENERGY CENTER | CPV VALLEY LLC | ORANGE | NY | 10940 | USA |  |  |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-335600136/00001 | 4911 | 221112 | 110043332471 | 08/01/2013 &nbsp;ACT | 08/01/2013 &nbsp;ACT | 2017-08-25 | 2017-09-28 | A |  | CPV Valley Energy Center is a 680 MW combined cycle electric generating facility located in Middletown, NY. The combustion turbines are rated at 2,234 MMBTU/H firing natural gas and 2,145 MMBTU/H firing diesel fuel. The duct burners are rated for 500 MMBTU/H firing natural gas. In addition to the turbines their emission limits for the auxiliary boiler (73.5 MMBTU/H), emergency generator, fire pump, and gas heater. | State Facility Permit | Auxiliary boiler | 13.31 | natural gas | 0 |  |  | Particulate matter, filterable (FPM) | Other - Methods 201/201A and 202 | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.0063 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Also PM-10.
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2018-06-25 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | Auxiliary Boiler | 13.31 | Natural Gas | 77.8 | mmBtu/hr | Annual emission based on 4600 hours/year. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.008 | LB/MMBTU |  | BACT-PSD | SIP | U | 0 | U | 1.38 | TONS/YEAR |  | 0.008 | LB/MMBTU |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 42 | MMBTU/H | PIPELINE QUALITY NATURAL GAS FUEL ONLY, OPERATION OF ULTRA LOW-NOX BURNER TECHNOLOGY SUBJECT TO NSPS SUBPART DC RECORDKEEPING AND REPORTING REQUIREMENTS | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.0019 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | AUXILLARY BOILER | 13.31 | NATURAL GAS | 93 | MMBTU/H | NATURAL GAS FUEL ONLY, OPERATION OF LOW-NOX BURNER TECHNOLOGY, FLUE GAS RECIRCULATION (FGR), GOOD COMBUSTION CONTROLS, MAX HEAT INPUT OF 372,000 MMBTU/HR | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.005 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 42 | MMBTU/H | PIPELINE QUALITY NATURAL GAS FUEL ONLY, OPERATION OF ULTRA LOW-NOX BURNER TECHNOLOGY SUBJECT TO NSPS SUBPART DC RECORDKEEPING AND REPORTING REQUIREMENTS | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.0075 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | AUXILLARY BOILER | 13.31 | NATURAL GAS | 93 | MMBTU/H | NATURAL GAS FUEL ONLY, OPERATION OF LOW-NOX BURNER TECHNOLOGY, FLUE GAS RECIRCULATION (FGR), GOOD COMBUSTION CONTROLS, MAX HEAT INPUT OF 372,000 MMBTU/HR | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.005 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 42 | MMBTU/H | PIPELINE QUALITY NATURAL GAS FUEL ONLY, OPERATION OF ULTRA LOW-NOX BURNER TECHNOLOGY SUBJECT TO NSPS SUBPART DC RECORDKEEPING AND REPORTING REQUIREMENTS | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.0075 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Auxilary boiler | 13.31 | Natural Gas | 92.4 | MMBtu/hr | Operation of the auxiliary boiler shall not exceed 4000 hrs in any continuous 12-month period. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | GCP ULSD and good combustion practices | 0.007 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 1.29 | TPY | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Auxilary boiler | 13.31 | Natural Gas | 92.4 | MMBtu/hr | Operation of the auxiliary boiler shall not exceed 4000 hrs in any continuous 12-month period. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA/OAR Method 201/201A | (Particulate Matter (PM)) | PM | P | GCP ULSD and good combustion practices | 0.007 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 1.29 | TPY | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Auxilary boiler | 13.31 | Natural Gas | 92.4 | MMBtu/hr | Operation of the auxiliary boiler shall not exceed 4000 hrs in any continuous 12-month period. | Particulate matter, total (TPM) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | GCP ULSD and good combustion practices | 0.007 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 1.29 | TPY | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
OK-0156 | NORTHSTAR AGRI IND ENID | NORTHSTAR AGRI INDUSTRIES | GARFIELD | OK | 73701 | USA | JIM DUDLEY | 701-478-5848 | JDUDLEY@NORTHSTARAGRI.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2013-0109-C PSD | 2076 | 311223 | Not Found | 01/31/2013 &nbsp;ACT | 07/31/2013 &nbsp;ACT | 2014-06-19 | 2018-05-11 | A |  | The new Northstar Agri Industries â€“ Enid facility will be designed to convert 2,500 TPD of seeds into crude oil and RBD oil. The facility consists of several processing steps to prepare seed and remove up to 100 million gallons per year of crude oil and RBD oil. | FRS Entered as &lsquo;&lsquo;047-00098&lsquo;&lsquo;. Too short for a FRS. The new Northstar Agri Industries â€“ Enid facility will be designed to convert 2,500 TPD of seeds into crude oil and RBD oil. The facility consists of several processing steps to prepare seed and remove up to 100 million gallons per year of crude oil and RBD oil. | Gas-fired Boiler | 13.31 | Natural Gas | 95 | MMBTUH |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion | 0.013 | LB/MMBTU | 3-HOUR AVG | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Mfg Data (3 boilers)
OK-0156 | NORTHSTAR AGRI IND ENID | NORTHSTAR AGRI INDUSTRIES | GARFIELD | OK | 73701 | USA | JIM DUDLEY | 701-478-5848 | JDUDLEY@NORTHSTARAGRI.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2013-0109-C PSD | 2076 | 311223 | Not Found | 01/31/2013 &nbsp;ACT | 07/31/2013 &nbsp;ACT | 2014-06-19 | 2018-05-11 | A |  | The new Northstar Agri Industries â€“ Enid facility will be designed to convert 2,500 TPD of seeds into crude oil and RBD oil. The facility consists of several processing steps to prepare seed and remove up to 100 million gallons per year of crude oil and RBD oil. | FRS Entered as &lsquo;&lsquo;047-00098&lsquo;&lsquo;. Too short for a FRS. The new Northstar Agri Industries â€“ Enid facility will be designed to convert 2,500 TPD of seeds into crude oil and RBD oil. The facility consists of several processing steps to prepare seed and remove up to 100 million gallons per year of crude oil and RBD oil. | Gas-fired Boiler | 13.31 | Natural Gas | 95 | MMBTUH |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion | 0.0126 | LB/MMBTU |  | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Mfg Data (3 boilers)
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Fuel pre-heater (EUFUELHTR) | 13.31 | natural gas | 3.7 | MMBTU/H | One natural gas-fired dew point heater for warming the natural gas fuel (EUFUELHTR). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion pracitces. | 0.0075 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0103 | CRICKET VALLEY ENERGY CENTER | CRICKET VALLEY ENERGY CENTER LLC | USA | NY | 12522-0407 | USA |  | 845-877-0596 | INFO@CRICKETVALLEY.COM | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-1326-00275/00009 | 4911 | 221112 | 110043340364 | 02/03/2016 &nbsp;ACT | 02/03/2016 &nbsp;ACT | 2017-08-24 | 2017-09-28 | A | http://www.dec.ny.gov/chemical/32249.html | Cricket Valley Energy Center LLC (CVEC) constructed the Cricket Valley Energy Center (the Facility), a nominal net 1,000-megawatt (MW) combined-cycle gas turbine electric generating facility, on a site located in Dover, Dutchess County, New York. The Facility consists of three General Electric (GE) Model 7FA.05 combustion turbine generators (CTGs) operating in combined-cycle mode with supplemental firing of the heat recovery steam generators (HRSGs); natural gas will be the sole fuel fired in the CTGs and duct burners. The Facility will include a natural gas-fired auxiliary boiler, four ultra-low sulfur distillate (ULSD) fired black-start generator engines and a ULSD-fired emergency fire pump engine. In addition to the air emitting equipment, the Facility will include three steam turbine generators (STGs), an air cooled condenser (ACC) and associated auxiliary equipment and systems. Each combined cycle generating unit consisting of the CTG, HRSG and STG will be exhausted through its own stack. Air emissions from the proposed Facility primarily consist of products of combustion from the CTGs, HRSG duct burners, and ancillary combustion sources. Dutchess County is designated as in attainment with respect to the National Ambient Air Quality Standards (NAAQS) for all criteria pollutants with the exception of ozone. Based upon the potential to emit (PTE) estimates, the Facility is subject to Prevention of Significant Deterioration (PSD) requirements for emissions of carbon monoxide (CO); nitrogen oxides (NOx); particulate matter (PM) with a diameter equal to or less than 10 microns (PM10), PM with a diameter equal to or less than 2.5 microns (PM2.5); greenhouse gases (GHG); sulfuric acid mist (H2SO4); and volatile organic compounds (VOC). In accordance with the NYSDECâ€™s Nonattainment New Source Review (NNSR) permitting program, the Facility is also subject to NNSR for emissions of NOx and VOC. |  | Auxiliary boiler | 13.31 | natural gas | 60 | MMBTU/H | Limited to 4,500 H/YR | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | good combustion practiced and pipeline quality natural gas | 0.005 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | EPA/OAR Method 5, 201/201A, or 202
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUFLTOS1 in FGTOH | 13.31 | Natural gas | 10.2 | MMBTU/H | One natural gas-fired thermal oil system for thermally fused lamination lines rated at 10.2 MMBTU/H fuel heat input (EUFLTOS1 in FGTOH). Note: The throughput capacity, 10.2 MMBTU/H, is not a change but instead a correction from the previous entry. The previous entry is under MI-0421 for the original permit. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0004 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 0 | N | 0.02 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUFLTOS1 in FGTOH | 13.31 | Natural gas | 10.2 | MMBTU/H | One natural gas-fired thermal oil system for thermally fused lamination lines rated at 10.2 MMBTU/H fuel heat input (EUFLTOS1 in FGTOH). Note: The throughput capacity, 10.2 MMBTU/H, is not a change but instead a correction from the previous entry. The previous entry is under MI-0421 for the original permit. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0075 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 0 | N | 0.33 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0421 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions related to the permit. Thank you. | 59-16 | 2493 | 321219 | Not Found | 06/30/2016 &nbsp;ACT | 08/26/2016 &nbsp;ACT | 2017-01-27 | 2017-07-20 | A |  | Particleboard manufacturing |  | EUTOH (In FGTOH)--Thermal Oil Heater | 13.31 | Natural gas | 34 | MMBTU/H | One natural gas fired thermal oil heater for press and sifter rated at 34 MMBTU/H fuel heat input (EUTOH in FGTOH). All falls under RBLC Process Type Code 30.590. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0075 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 1.1 | T/YR | BASED UPON A 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUTOH in FGTOH | 13.31 | Natural gas | 38 | MMBTU/H | One natural gas-fired thermal oil heater for press and sifter rated at 38 MMBTU/hr fuel heat input (EUTOH in FGTOH). Also falls under the RBLC Process Type Code 30.590. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0075 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 0 | N | 1.2 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler A (EUAUXBOILERA) | 13.31 | natural gas | 55 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 55 MMBTU/hr fuel heat input (EUAUXBOILERA within flexible group FGAUXBOILERS). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0018 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler B (EUAUXBOILERB) | 13.31 | natural gas | 95 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 95 MMBtu/hr fuel heat input (EUAUXBOILERB within flexible group FGAUXBOILERS). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0018 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Fuel pre-heater (EUFUELHTR) | 13.31 | natural gas | 3.7 | MMBTU/H | One natural gas-fired dew point heater for warming the natural gas fuel (EUFUELHTR). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0075 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler A (EUAUXBOILERA) | 13.31 | natural gas | 55 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 55 MMBTU/hr fuel heat input (EUAUXBOILERA within flexible group FGAUXBOILERS). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.007 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler B (EUAUXBOILERB) | 13.31 | natural gas | 95 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 95 MMBtu/hr fuel heat input (EUAUXBOILERB within flexible group FGAUXBOILERS). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.007 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0421 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions related to the permit. Thank you. | 59-16 | 2493 | 321219 | Not Found | 06/30/2016 &nbsp;ACT | 08/26/2016 &nbsp;ACT | 2017-01-27 | 2017-07-20 | A |  | Particleboard manufacturing |  | EUFLTOS1 in FGTOH (Thermal Oil System for Thermally Fused Lamination Lines) | 13.31 | Natural gas | 34 | MMBTU/H | One natural gas fired thermal oil system for thermally fused lamination lines rated at 10.2 MMBTU/H fuel heat input (EUFLTOS1 in FGTOH). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0004 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0.02 | T/YR | BASED UPON A 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler A (EUAUXBOILERA) | 13.31 | natural gas | 55 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 55 MMBTU/hr fuel heat input (EUAUXBOILERA within flexible group FGAUXBOILERS). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.007 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler B (EUAUXBOILERB) | 13.31 | natural gas | 95 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 95 MMBtu/hr fuel heat input (EUAUXBOILERB within flexible group FGAUXBOILERS). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.007 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
WY-0075 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | MD-16173 | 491 | 221122 | Not Found | 05/01/2014 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2014-06-16 | 2018-05-11 | B |  | Nominal 220 megawatt (MW) gross electrical facility. | Installation of a 25.06 MMBtu/hr Auxiliary Boiler (Cleaver Brooks CBEX Elite 600). Subject to PSD based on project aggregation. | Auxiliary Boiler | 13.31 | natual gas | 25.06 | MMBtu/h |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0175 | LB/MMBTU | 3 HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0.4 | LB/H | 3 HOUR AVERAGE | 0 |  |  | 0 | 0 | N
AL-0280 | LENZING FIBERS, INC. | LENZING FIBERS, INC. | MOBILE | AL | 36505 | USA | MR. KEVIN, PLANT MANAGER ALLEN | 251-679-2814 | K.ALLEN@LENZING.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-0047-X011 | 2823 | 325221 | 110043792278 | 09/15/2011 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2015-03-17 | 2016-05-09 | D |  | Production of lyocell cellulose fiber by solvent spinning process. | NAICS Code: 325220 | Natural Gas Fired Broiler #3 | 13.31 | Natural Gas | 100 | MMBTU/Hr |  | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 0.0075 | LB/MMBTU | LB/MM SCF OF NATURAL GAS USED | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.0075 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N
LA-0229 | SHINTECH PLAQUEMINE PLANT 2 | SHINTECH LOUISIANA LLC | IBERVILLE | LA | 70764 | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-731 | 2821 | 325211 | UNKNOWN | 11/19/2010 &nbsp;ACT | 07/10/2008 &nbsp;ACT | 2009-04-02 | 2009-04-20 | B |  | A PROPOSED 1.81 BILLION LBS/YR PVC PRODUCTION COMPLEX WHICH WILL CONSIST OF A CHLORALKALI PLANT, AN EDC/VCM PLANT, AND A PVC PLANT | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | EQT122-EQT125 - FOUR VCM CRACKING FURNACES | 13.31 | NATURAL GAS | 90 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND CLEAN BURNING FUELS | 0.007 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) NATURAL GAS AUXILIARY BOILERS | 13.31 | NATURAL GAS | 80 | MMBTU/H | BOTH BOILERS, LABELED AS B001 AND B002, ARE EQUIPPED WITH LOW NOX BURNERS WITH FLUE GAS REGULATION. THIS IS CONSIDERED A STEAM GENERATING UNIT. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND FUEL SPECIFICATIONS | 0.0075 | LB/MMBTU | 3 HOURS | BACT-PSD |  |  | 0 |  | 0.6 | LB/H | 3 HOURS | 0 |  |  | 0 | 0 | N |  | LIMIT ONE AND TWO ARE FOR EACH BOILER
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) NATURAL GAS AUXILIARY BOILERS | 13.31 | NATURAL GAS | 80 | MMBTU/H | BOTH BOILERS, LABELED AS B001 AND B002, ARE EQUIPPED WITH LOW NOX BURNERS WITH FLUE GAS REGULATION. THIS IS CONSIDERED A STEAM GENERATING UNIT. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND FUEL SPECIFICATIONS | 0.0075 | LB/MMBTU | 3 HOURS | BACT-PSD |  |  | 0 |  | 0.6 | LB/H | 3 HOURS | 0 |  |  | 0 | 0 | N |  | LIMIT ONE AND TWO ARE FOR EACH BOILER
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) NATURAL GAS AUXILIARY BOILERS | 13.31 | NATURAL GAS | 80 | MMBTU/H | BOTH BOILERS, LABELED AS B001 AND B002, ARE EQUIPPED WITH LOW NOX BURNERS WITH FLUE GAS REGULATION. THIS IS CONSIDERED A STEAM GENERATING UNIT. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND FUEL SPECIFICATIONS | 0.0075 | LB/MMBTU | 3 HOURS | BACT-PSD |  |  | 0 |  | 0.6 | LB/H | 3 HOURS | 0 |  |  | 0 | 0 | N |  | LIMIT ONE AND TWO ARE FOR EACH BOILER.
MI-0420 | DTE GAS COMPANY--MILFORD COMPRESSOR STATION | DTE GAS COMPANY | OAKLAND | MI | 48042 | USA | BARRY MARIETTA | 313-235-5611 | MARIETTAB@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For permit related questions, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786. | 185-15 | 4922 | 486210 | Not Found | 04/12/2016 &nbsp;ACT | 06/03/2016 &nbsp;ACT | 2016-09-16 | 2017-04-28 | B |  | Natural gas compressor station. |  | FGAUXBOILERS | 13.31 | Natural gas | 6 | MMBTU/H | Two natural gas-fired auxiliary boilers, each rated at 6 MMBTU/H fuel heat input. The boilers are identified as EUAUXBOIL2 and EUAUXBOIL3 within the flexible group FGAUXBOILERS. The boilers are subject to 40 CFR Part 63 Subpart DDDDD, which requires tune ups. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuel (pipeline quality natural gas). | 0.0075 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 0.0075 lb/MMBTU for each boiler. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM10 emissions were assumed the same as PM2.5, so the cost analysis was equivalent. *Pulse jet fabric filter baghouse: minimum of $43,942 per ton *Dry ESP (Wire-plate type): minimum of $31,291 per ton *Wet ESP (Wire-plate type): minimum of $54,758 per ton *Venturi Scrubber: minimum of $37,237 per ton.
MI-0420 | DTE GAS COMPANY--MILFORD COMPRESSOR STATION | DTE GAS COMPANY | OAKLAND | MI | 48042 | USA | BARRY MARIETTA | 313-235-5611 | MARIETTAB@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For permit related questions, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786. | 185-15 | 4922 | 486210 | Not Found | 04/12/2016 &nbsp;ACT | 06/03/2016 &nbsp;ACT | 2016-09-16 | 2017-04-28 | B |  | Natural gas compressor station. |  | FGAUXBOILERS | 13.31 | Natural gas | 6 | MMBTU/H | Two natural gas-fired auxiliary boilers, each rated at 6 MMBTU/H fuel heat input. The boilers are identified as EUAUXBOIL2 and EUAUXBOIL3 within the flexible group FGAUXBOILERS. The boilers are subject to 40 CFR Part 63 Subpart DDDDD, which requires tune ups. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuel (pipeline quality natural gas). | 0.0075 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 0.0075 lb/MMBTU for each boiler. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM10 emissions were assumed the same as PM2.5, so the cost analysis was equivalent. *Pulse jet fabric filter baghouse: minimum of $43,942 per ton *Dry ESP (Wire-plate type): minimum of $31,291 per ton *Wet ESP (Wire-plate type): minimum of $54,758 per ton *Venturi Scrubber: minimum of $37,237 per ton.
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Auxilary Boiler | 13.31 | Natural Gas | 62.04 | MCF/hr | The proposed auxilary boiler will fire NG exclusively with maximum rated heat input capacity of 61.0 MMBtu/hr and is equipped with and ulatra-low NOx burner and a flue gas recirculation system for NOx control. It will be used for preheating components of HRSG and the 420 MW steam turbine during CT startup. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.005 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 1.3 | TPY | ANY CONSECUTIVE 12-MONTH PERIOD | 0 |  |  | 0 | 0 | N
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Auxilary Boiler | 13.31 | Natural Gas | 62.04 | MCF/hr | The proposed auxilary boiler will fire NG exclusively with maximum rated heat input capacity of 61.0 MMBtu/hr and is equipped with and ulatra-low NOx burner and a flue gas recirculation system for NOx control. It will be used for preheating components of HRSG and the 420 MW steam turbine during CT startup. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.005 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 1.3 | TPY | ANY CONSECUTIVE 12-MONTH PERIOD | 0 |  |  | 0 | 0 | N
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Auxilary Boiler | 13.31 | Natural Gas | 62.04 | MCF/hr | The proposed auxilary boiler will fire NG exclusively with maximum rated heat input capacity of 61.0 MMBtu/hr and is equipped with and ulatra-low NOx burner and a flue gas recirculation system for NOx control. It will be used for preheating components of HRSG and the 420 MW steam turbine during CT startup. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.005 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 1.3 | TPY | ANY CONSECUTIVE 12-MONTH PERIOD | 0 |  |  | 0 | 0 | N
LA-0204 | PLAQUEMINE PVC PLANT | SHINTECH LOUISIANA LLC | IBERVILLE | LA |  | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: ANTHONY RANDALL, 225-219-3181 | PSD-LA-709(M-1) | 2821 | 325211 | 110020900104 | 03/03/2008 &nbsp;ACT | 02/27/2009 &nbsp;ACT | 2006-06-25 | 2009-08-06 | A |  | NEW 1.3 BILLION POUND PER YEAR PVC PLANT CONSISTING OF A CHLOR-ALKALI UNIT, AND EDC/VCM UNIT, AND A PVC UNIT. | VINYL CHLORIDE - 28.82 TPY. VINYL CHLORIDE (VC) WAS REGULATED AS A PSD POLLUTANT (SIGNIFICANCE LEVEL OF 1 TPY) IN LOUISIANA WHEN THIS PERMIT WAS ISSUED. LOUISIANA'S NSR REFORM RULES, ADOPTED DECEMBER 20, 2005, DELISTED VC. HAPS FROM THE PVC UNIT WERE SUBJECTED TO A 112(J) MACT DETERMINATION AFTER VACATURE OF 40 CFR 63 SUBPART J ON APRIL 19, 2005. BACT FOR VC IS EQUIVALENT TO MACT FOR VC. NNSR: BECAUSE VOC AND NOX EMISSIONS ARE LESS THAN 100 TPY, LAER WAS NOT REQUIRED. OFFSETS WERE REQUIRED PURSUANT TO A STATE-ONLY PROVISION IN LAC 33:III.504. PSD-LA-709(M-1) IS FOR 1) REMOVING A COOLING TOWER (M-8), CORRECTING CAPACITY OF COOLING TOWER M-7, AND 3) INCLUDING 19 EMERGENCY ENGINES AND THREE LOADING HOPPERS. | CRACKING FURNACES A-D | 13.31 |  | 90 | MMBTU/H EA. |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND USE OF NATURAL GAS AS FUEL | 0.007 | LB/MMBTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
SC-0112 | NUCOR STEEL - BERKELEY | NUCOR STEEL | BERKELEY | SC | 29450 | USA | RAY SIMS | 8433366123 | SIMSR@NUCORSTEEL.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MR. DENNIS CAMIT | (803)898-4284 | camitdr@dhec.sc.gov | WANDA PARNELL (803) 898-4123 | 0420-0060-DO | 3312 | 331111 | 110000353527 | 12/06/2007 &nbsp;ACT | 05/05/2008 &nbsp;ACT | 2012-05-09 | 2013-10-30 | D |  | SCRAP STEEL RECYCLING MILL |  | VACUUM DEGASSER BOILER | 13.31 | NATURAL GAS | 50.21 | MMBTU/H |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES PER MANUFACTURER'S GUIDANCE | 0.0076 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0.0076 | LB/MMBTU |  | 0 | 0 | N
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUAUXBOILER: Auxiliary Boiler | 13.31 | Natural gas | 99.9 | MMBTU/H | A natural gas-fired auxiliary boiler, rated at 99.9 MMBTU/H to facilitate startup of the CTG/HRSG trains and to provide steam to the steam turbine generator seals. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, low sulfur fuel | 0.007 | LB/MMBTU | HOURLY | BACT-PSD | SIP | N | 0 | N | 0.7 | LB/H | HOURLY | 0 |  |  | 0 | 0 | N
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUAUXBOILER: Auxiliary Boiler | 13.31 | Natural gas | 99.9 | MMBTU/H | A natural gas-fired auxiliary boiler, rated at 99.9 MMBTU/H to facilitate startup of the CTG/HRSG trains and to provide steam to the steam turbine generator seals. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, low sulfur fuel | 0.007 | LB/MMBTU | HOURLY | BACT-PSD | SIP | N | 0 | N | 0.7 | LB/H | HOURLY | 0 |  |  | 0 | 0 | N
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUAUXBOILER: Auxiliary Boiler | 13.31 | Natural gas | 99.9 | MMBTU/H | A natural gas-fired auxiliary boiler, rated at 99.9 MMBTU/H to facilitate startup of the CTG/HRSG trains and to provide steam to the steam turbine generator seals. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, low sulfur fuel | 0.007 | LB/MMBTU | HOURLY | BACT-PSD | SIP | N | 0 | N | 0.7 | LB/H | HOURLY | 0 |  |  | 0 | 0 | N
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-AUXBOILER1-2; Two (2) natural gas-fired auxiliary boilers. | 13.31 | natural gas | 40 | MMBTU/H | Two (2) natural gas-fired auxiliary boilers. 40 MMBTU/H each. Fuel restriction = 360.8 MMSCF/YR total for both units. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.005 | LB/MMBTU | TEST PROTOCOL; EACH UNIT. | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The PM2.5 emission limit of 0.005 LB/MMBTU applies to each unit.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Fuel pre-heater (EUFUELHTR) | 13.31 | natural gas | 3.7 | MMBTU/H | One natural gas-fired dew point heater for warming the natural gas fuel (EUFUELHTR). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.007 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUFUELHTR (Fuel pre-heater) | 13.31 | Natural gas | 3.7 | MMBTU/H | One natural gas fired dew point heater for warming the natural gas fuel (EUFUELHTR). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.007 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGFUELHTR (Two fuel pre-heaters identified as EUFUELHTR1 &amp; EUFUELHTR2) | 13.31 | Natural gas | 27 | MMBTU/H | Two natural gas fired dew point heaters for warming the natural gas fuel (EUFUELHTR1 & EUFUELHTR2 in flexible group FGFUELHTR). The total combined heat input during operation shall not exceed 27 MMBTU/H (each) as well. The CO2e limit is for both units combined; however the other limits are per unit. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.002 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME. | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above of 0.002 LB/MMBTU is for each fuel heater. At greater than $40,000 for the least expensive option, none of the control technologies are economically feasible. Control technologies evaluated were a scrubber and various types of fabric filters and ESPs.
MI-0421 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions related to the permit. Thank you. | 59-16 | 2493 | 321219 | Not Found | 06/30/2016 &nbsp;ACT | 08/26/2016 &nbsp;ACT | 2017-01-27 | 2017-07-20 | A |  | Particleboard manufacturing |  | EUFLTOS1 in FGTOH (Thermal Oil System for Thermally Fused Lamination Lines) | 13.31 | Natural gas | 34 | MMBTU/H | One natural gas fired thermal oil system for thermally fused lamination lines rated at 10.2 MMBTU/H fuel heat input (EUFLTOS1 in FGTOH). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0075 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0.33 | T/YR | BASED UPON A 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-AUXBOILER1-2; Two (2) natural gas-fired auxiliary boilers. | 13.31 | natural gas | 40 | MMBTU/H | Two (2) natural gas-fired auxiliary boilers. 40 MMBTU/H each. Fuel restriction = 360.8 MMSCF/YR total for both units. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.005 | LB/MMBTU | TEST PROTOCOL; EACH UNIT. | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The PM emission limit of 0.005 LB/MMBTU applies to each unit.
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUAUXBOILER (North Plant): Auxiliary Boilder | 13.31 | Natural gas | 61.5 | MMBTU/H | A natural gas-fired auxiliary boiler, rated at 61.5 MMBTU/H (HHV) to facilitate startup of the CTGHRSG train and to provide the required steam to support the startup of the facility, including but not limited to steam for sparging, STG seals, etc. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.005 | LB/MMBTU | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUAUXBOILER (South Plant): Auxiliary Boiler | 13.31 | Natural gas | 61.5 | MMBTU/h | A natural gas-fired auxiliary boiler, rated at 61.5 MMBTU/H (HHV) to facilitate startup of the CTGHRSG train and to provide the required steam to support the startup of the facility, including but not limited to steam for sparging, STG seals, etc. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.005 | LB/MMBTU | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUAUXBOILER (Auxiliary boiler) | 13.31 | natural gas | 83.5 | MMBTU/H | One natural gas fired auxiliary boiler rated at 83.5 MMBTU/hr fuel heat input (EUAUXBOILER). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0018 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUFUELHTR (Fuel pre-heater) | 13.31 | Natural gas | 3.7 | MMBTU/H | One natural gas fired dew point heater for warming the natural gas fuel (EUFUELHTR). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0075 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUFLTOS1 in FGTOH | 13.31 | Natural gas | 10.2 | MMBTU/H | One natural gas-fired thermal oil system for thermally fused lamination lines rated at 10.2 MMBTU/H fuel heat input (EUFLTOS1 in FGTOH). Note: The throughput capacity, 10.2 MMBTU/H, is not a change but instead a correction from the previous entry. The previous entry is under MI-0421 for the original permit. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0005 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 0 | N | 0.02 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0421 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions related to the permit. Thank you. | 59-16 | 2493 | 321219 | Not Found | 06/30/2016 &nbsp;ACT | 08/26/2016 &nbsp;ACT | 2017-01-27 | 2017-07-20 | A |  | Particleboard manufacturing |  | EUTOH (In FGTOH)--Thermal Oil Heater | 13.31 | Natural gas | 34 | MMBTU/H | One natural gas fired thermal oil heater for press and sifter rated at 34 MMBTU/H fuel heat input (EUTOH in FGTOH). All falls under RBLC Process Type Code 30.590. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0005 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0.08 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUTOH in FGTOH | 13.31 | Natural gas | 38 | MMBTU/H | One natural gas-fired thermal oil heater for press and sifter rated at 38 MMBTU/hr fuel heat input (EUTOH in FGTOH). Also falls under the RBLC Process Type Code 30.590. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0005 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 0 | N | 0.08 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-AUXBOILER1-2; Two (2) natural gas-fired auxiliary boilers. | 13.31 | natural gas | 40 | MMBTU/H | Two (2) natural gas-fired auxiliary boilers. 40 MMBTU/H each. Fuel restriction = 360.8 MMSCF/YR total for both units. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.005 | LB/MMBTU | TEST PROTOCOL; EACH UNIT. | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The PM10 emission limit of 0.005 LB/MMBTU applies to each unit.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUAUXBOILER (Auxiliary boiler) | 13.31 | natural gas | 83.5 | MMBTU/H | One natural gas fired auxiliary boiler rated at 83.5 MMBTU/hr fuel heat input (EUAUXBOILER). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.007 | LB/MMBTU | TEST PROTOCOL WIL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUFUELHTR (Fuel pre-heater) | 13.31 | Natural gas | 3.7 | MMBTU/H | One natural gas fired dew point heater for warming the natural gas fuel (EUFUELHTR). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0075 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME. | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0421 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions related to the permit. Thank you. | 59-16 | 2493 | 321219 | Not Found | 06/30/2016 &nbsp;ACT | 08/26/2016 &nbsp;ACT | 2017-01-27 | 2017-07-20 | A |  | Particleboard manufacturing |  | EUTOH (In FGTOH)--Thermal Oil Heater | 13.31 | Natural gas | 34 | MMBTU/H | One natural gas fired thermal oil heater for press and sifter rated at 34 MMBTU/H fuel heat input (EUTOH in FGTOH). All falls under RBLC Process Type Code 30.590. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0004 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0.06 | T/YR | BASED UPON A 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUTOH in FGTOH | 13.31 | Natural gas | 38 | MMBTU/H | One natural gas-fired thermal oil heater for press and sifter rated at 38 MMBTU/hr fuel heat input (EUTOH in FGTOH). Also falls under the RBLC Process Type Code 30.590. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0004 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 0 | N | 0.07 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUAUXBOILER (Auxiliary boiler) | 13.31 | natural gas | 83.5 | MMBTU/H | One natural gas fired auxiliary boiler rated at 83.5 MMBTU/hr fuel heat input (EUAUXBOILER). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.007 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME. | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0240 | FLOPAM INC. | FLOPAM INC. | IBERVILLE PARISH | LA | 70764 | USA | PETER NICHOLS | 912-884-3366 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT REVIEWER: DAN NGUYEN (225) 219-3180 | PSD-LA-747/1280-00141-V0 | 2899 | 325110 | UNKNOWN | 11/23/2009 &nbsp;ACT | 06/14/2010 &nbsp;ACT | 2010-07-14 | 2010-07-22 | A |  | A PROPOSED MANUFACTURING COMPLEX CONSISTS OF AN ACRYLAMIDE PLANT, A POWDER PLANT, A DIALLYLDIMETHYLAMMONIUMCHLORIDE (DADMAC) PLANT, A SPECIALTY PRODUCTS PLANT, AN EMULSION PLANT, A POLYAMINE PLANT, A DIMETHYLAMINEOETHYLACRYLATE (ADAM) PLANT, A CHLOROMETHYLATION (CM) PLANT, AN ACRYLAMIDO TERTIO BUTYL SULFONATE (ATBS) PLANT, AND AUXILIARY AND MISCELLANEOUS EQUIPMENT. | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | Boilers | 13.31 | natural gas | 25.1 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good equipment design and proper combustion practices, fueled by natural gas/alcohol | 0.005 | LB/MMBtu | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0.005 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N
LA-0240 | FLOPAM INC. | FLOPAM INC. | IBERVILLE PARISH | LA | 70764 | USA | PETER NICHOLS | 912-884-3366 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT REVIEWER: DAN NGUYEN (225) 219-3180 | PSD-LA-747/1280-00141-V0 | 2899 | 325110 | UNKNOWN | 11/23/2009 &nbsp;ACT | 06/14/2010 &nbsp;ACT | 2010-07-14 | 2010-07-22 | A |  | A PROPOSED MANUFACTURING COMPLEX CONSISTS OF AN ACRYLAMIDE PLANT, A POWDER PLANT, A DIALLYLDIMETHYLAMMONIUMCHLORIDE (DADMAC) PLANT, A SPECIALTY PRODUCTS PLANT, AN EMULSION PLANT, A POLYAMINE PLANT, A DIMETHYLAMINEOETHYLACRYLATE (ADAM) PLANT, A CHLOROMETHYLATION (CM) PLANT, AN ACRYLAMIDO TERTIO BUTYL SULFONATE (ATBS) PLANT, AND AUXILIARY AND MISCELLANEOUS EQUIPMENT. | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | Boilers | 13.31 | natural gas | 25.1 | MMBTU/H |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good equipment design and proper combustion practices, fueled by natural gas/alcohol | 0.005 | LB/MMBtu | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0.005 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N
IA-0106 | CF INDUSTRIES NITROGEN, LLC - PORT NEAL NITROGEN COMPLEX | CF INDUSTRIES NITROGEN, LLC | WOODBURY | IA | 51054 | USA | MIKE MAAS | 712-233-6222 | MMAAS@CFINDUSTRIES.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | Christopher A. Roling, PE Environmental Engineer Senior Iowa DNR - Air Quality Bureau 7900 Hickman Rd, Suite 1 Windsor Heights, IA 50324 (515) 242-6002 chris.roling@dnr.iowa.gov | PN 13-037 | 2873 | 325311 | 110000414089 | 02/01/2013 &nbsp;ACT | 07/12/2013 &nbsp;ACT | 2013-07-16 | 2016-05-04 | B |  | Nitrogenous fertilizer manufacturing including ammonia, urea, and urea-ammonium nitrate (UAN) solutions. |  | Startup Heater | 13.31 | natural gas | 58.8 | MMBTU/H | Limited to 5.76 MMCF of natural gas/yr | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | good operating practices & use of natural gas | 0.0024 | LB/MMBTU | AVERAGE OF THREE (3) STACK TEST RUNS | BACT-PSD | SIP | U | 0 | U | 0.007 | TONS/YR | ROLLING TWELVE (12) MONTH TOTAL | 0 |  |  | 0 | 0 | N
IA-0106 | CF INDUSTRIES NITROGEN, LLC - PORT NEAL NITROGEN COMPLEX | CF INDUSTRIES NITROGEN, LLC | WOODBURY | IA | 51054 | USA | MIKE MAAS | 712-233-6222 | MMAAS@CFINDUSTRIES.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | Christopher A. Roling, PE Environmental Engineer Senior Iowa DNR - Air Quality Bureau 7900 Hickman Rd, Suite 1 Windsor Heights, IA 50324 (515) 242-6002 chris.roling@dnr.iowa.gov | PN 13-037 | 2873 | 325311 | 110000414089 | 02/01/2013 &nbsp;ACT | 07/12/2013 &nbsp;ACT | 2013-07-16 | 2016-05-04 | B |  | Nitrogenous fertilizer manufacturing including ammonia, urea, and urea-ammonium nitrate (UAN) solutions. |  | Startup Heater | 13.31 | natural gas | 58.8 | MMBTU/H | Limited to 5.76 MMCF of natural gas/yr | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - 201A with 202 | (Particulate Matter (PM)) | PM | P | good operating practices & use of natural gas | 0.0024 | LB/MMBTU | AVERAGE OF THREE (3) STACK TEST RUNS | BACT-PSD | SIP | U | 0 | U | 0.007 | TONS/YR | ROLLING TWELVE (12) MONTH TOTAL | 0 |  |  | 0 | 0 | N
IA-0106 | CF INDUSTRIES NITROGEN, LLC - PORT NEAL NITROGEN COMPLEX | CF INDUSTRIES NITROGEN, LLC | WOODBURY | IA | 51054 | USA | MIKE MAAS | 712-233-6222 | MMAAS@CFINDUSTRIES.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | Christopher A. Roling, PE Environmental Engineer Senior Iowa DNR - Air Quality Bureau 7900 Hickman Rd, Suite 1 Windsor Heights, IA 50324 (515) 242-6002 chris.roling@dnr.iowa.gov | PN 13-037 | 2873 | 325311 | 110000414089 | 02/01/2013 &nbsp;ACT | 07/12/2013 &nbsp;ACT | 2013-07-16 | 2016-05-04 | B |  | Nitrogenous fertilizer manufacturing including ammonia, urea, and urea-ammonium nitrate (UAN) solutions. |  | Startup Heater | 13.31 | natural gas | 58.8 | MMBTU/H | Limited to 5.76 MMCF of natural gas/yr | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good operating practices and use of natural gas | 0.0024 | LB/MMBTU | AVERAGE OF THREE (3) STACK TEST RUNS | BACT-PSD | SIP | U | 0 | U | 0.007 | TONS/YR | ROLLING TWELVE (12) MONTH TOTAL | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Waste Heat Boilers | 13.31 | Natural Gas | 50 | MMBTU/H | Five (5) Natural Gas-Fired 50 MMBtu/hr Waste Heat Boilers. Installed in 1986. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Limited Use (200 hr/yr) | 0.0074 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Auxiliary boiler | 13.31 | Natural gas | 18.6 | MMBTU/HR | One (1) 18.6 MMBtu/hr natural gas-fired auxiliary boiler with the capacity to produce 15,000 pounds of steam per hour (approximately 18.6 MMBtu/hr) | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.005 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Auxiliary boiler | 13.31 | Natural gas | 18.6 | MMBTU/HR | One (1) 18.6 MMBtu/hr natural gas-fired auxiliary boiler with the capacity to produce 15,000 pounds of steam per hour (approximately 18.6 MMBtu/hr) | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.005 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KS-0029 | THE EMPIRE DISTRICT ELECTRIC COMPANY | THE EMPIRE DISTRICT ELECTRIC COMPANY | CHEROKEE | KS | 66770 | USA | JEFF BURKETT | 417-625-4236 | JBURKETT@EMPIREDISCTRICT.COM | 7 | KS001 | KANSAS DEPT. OF HEALTH & ENVIRONMENT, BR. OF AIR & RADIATION, KS | GYANENDRA PRASAI, PE | 785-296-6427 | Gyanendra.X.Prasai@ks.gov | Gerald McIntyre, E-mail address: Gerald.McIntyre@ks.gov; Susana Pjesky, E-mail address: Susana.Pjesky@ks.gov | C-12987 | 4911 | 221112 | Not Found | 07/02/2015 &nbsp;ACT | 07/14/2015 &nbsp;ACT | 2017-04-06 | 2018-06-21 | U |  | The Empire District Electric Company â€“ Riverton Plant (EDEC) (Source ID: 0210002) is a fossil fuel electricity generation facility located in Cherokee County, Kansas. | This PSD permit with tracking number C-12987 is a modification of PSD permits C-12670 (Administrative Amendment, issued on 2/19/2015) and C-10913 (original PSD Permit for the proposed project, issued on 7/11/2013). | Auxiliary boiler | 13.31 | Natural gas | 18.6 | MMBTU/HR | One (1) 18.6 MMBtu/hr natural gas-fired auxiliary boiler with the capacity to produce 15,000 pounds of steam per hour (approximately 18.6 MMBtu/hr) | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.005 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | HEATER | 13.31 | NATURAL GAS | 1.7 | MMBTU/H | FUEL GAS HEATER | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.007 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | BOILER | 13.31 | NATURAL GAS | 93 | MMBTU/H | AUXILIARY BOILER | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.005 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | HEATER | 13.31 | NATURAL GAS | 1.7 | MMBTU/H | FUEL GAS HEATER | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.007 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0040 | CPV ST CHARLES | COMPETITIVE POWER VENTURES, INC./CPV MARYLAND, LLC | CHARLES | MD |  | USA | SHARON K SEGNER | 2407232300 | SSEGNER@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3230 BPAUL@MDE.STATE.US | CPCN CASE NO. 9129 | 1731 | 221122 | UNKNOWN | &nbsp; | 11/12/2008 &nbsp;ACT | 2009-01-12 | 2009-02-20 | A |  | 640 MW GENERATING FACILITY |  | BOILER | 13.31 | NATURAL GAS | 93 | MMBTU/H | AUXILIARY BOILER | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.005 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Auxillary Boiler | 13.31 | Natural gas | 13.31 | MMBtu/hr | Fired only on natural gas supplied by a public utility. Limited to 4000 hrs per year on a 12 month rolling basis. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.007 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 2.59 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064098541 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Auxilary Boiler | 13.31 | Natural Gas | 55.4 | MMBtu/hr | Shall construct qualifying small gas combustion units capable of reducing nitrogen oxides (NOx) and carbon monoxide (CO) emissions to or below: i. 30 ppmdv NOx at 3% O2 when firing gas; ii. 300 ppmdv CO at 3% O2. The combustion unit(s) shall be fired only on natural gas or liquefied petroleum gas Total fuel usage of the auxiliary boiler shall not exceed 214.9 MMscf on a 12-month rolling basis. Shall maintain and operate the source in accordance with good engineering practice. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.007 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 0.775 | TPY | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000310459 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Auxiliary Boiler | 13.31 | Natural Gas | 80 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.005 | LB/MMBTU | 1 HR AVG, DOES NOT APPLY DURING SS | BACT-PSD | SIP , OPERATING PERMIT , NSPS | U | 0 | U | 0.4 | LB/H | 1 HR AVG, DOES NOT APPLY DURING SS | 0 |  |  | 0 | 0 | N
OK-0148 | BUFFALO CREEK PROCESSING PLANT | MARKWEST BUFFALO CREEK GAS CO LLC | BECKHAM | OK | 73662 | USA | KRISTIN IKARD |  | KRISTIN.IKARD@ACCESSMIDSTREAM.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2012-1026-C PSD | 1321 | 211112 | Not Found | 02/21/2012 &nbsp;ACT | 09/12/2012 &nbsp;ACT | 2014-06-13 | 2018-05-11 | A |  | Mid-America Midstream Gas Services (MAMGS)proposes to construct a natural gas plant with ten natural gas-fired reciprocating internal combustion engines, two natural gas-fired turbines, a 230-MMSCFD amine unit with a 11.04 MMBTUH reboiler, an acid gas flare, eight condensate tanks, and six produced water tanks. Associated support operations include condensate truck loading, blowdowns and fugitive emissions. | FRS Entered as &lsquo;&lsquo;009-00118&lsquo;&lsquo;. Too short for a FRS. MAMGS proposes to construct a natural gas plant with ten natural gas-fired reciprocating internal combustion engines, two natural gas-fired turbines, a 230-MMSCFD amine unit with a 11.04 MMBTUH reboiler, an acid gas flare, eight condensate tanks, and six produced water tanks. Associated support operations include condensate truck loading, blowdowns and fugitive emissions. | Commercial/Institutional Boilers (&lt;100 MMBTUH) | 13.31 | Natural Gas | 11.04 | MMBTUH |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0075 | LB/MMBTU |  | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | AP-42 and Good Combustion
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Auxillary Boiler | 13.31 | Natural gas | 13.31 | MMBtu/hr | Fired only on natural gas supplied by a public utility. Limited to 4000 hrs per year on a 12 month rolling basis. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.007 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 2.59 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Waste Heat Boilers | 13.31 | Natural Gas | 50 | MMBTU/H | Five (5) Natural Gas-Fired 50 MMBtu/hr Waste Heat Boilers. Installed in 1986. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0074 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064098541 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Auxilary Boiler | 13.31 | Natural Gas | 55.4 | MMBtu/hr | Shall construct qualifying small gas combustion units capable of reducing nitrogen oxides (NOx) and carbon monoxide (CO) emissions to or below: i. 30 ppmdv NOx at 3% O2 when firing gas; ii. 300 ppmdv CO at 3% O2. The combustion unit(s) shall be fired only on natural gas or liquefied petroleum gas Total fuel usage of the auxiliary boiler shall not exceed 214.9 MMscf on a 12-month rolling basis. Shall maintain and operate the source in accordance with good engineering practice. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.007 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 0.775 | TPY | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
MA-0039 | SALEM HARBOR STATION REDEVELOPMENT | FOOTPRINT POWER SALEM HARBOR DEVELOPMENT LP | ESSEX | MA | 1970 | USA | SCOTT SILVERSTEIN |  |  | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Cosmo Buttaro MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3281 Cosmo.Buttaro@State.MA.US | NE-12-022 | 4911 | 221112 | 110000310459 | 09/09/2013 &nbsp;ACT | 01/30/2014 &nbsp;ACT | 2014-09-26 | 2016-05-05 | A | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | Footprint Power Salem Harbor Development LP (the Permittee) proposes to construct and operate a nominal 630 Megawatt (MW) natural gas fired, quick start (capable of producing 300 MW within 10 minutes of startup) combined cycle electric generating facility (the Facility) at Salem Harbor Station. With duct firing, the proposed Facility will be capable of generating an additional 62 MW, for a total of 692 MW. Emission units include two 315 MW (nominal) GE Model 107F Series 5 combustion turbine generators, each with dedicated heat recovery steam generator, duct burner and 31 MW (estimated) steam turbine generator, dispatchable independently of one another by ISO-NE; one 80 mmBtu/hr auxiliary boiler, one 750 kW emergency engine-generator, and one 371 bhp emergency engine-fire-pump. | separate PSD permit under delegated program, and CPA approval (including nonattainment major NSR for NOx as ozone precursor, and state minor NSR for other pollutants) other facility-wide emission limits (not listed in next section): GHG(CO2e): 2,279,530 TPY CO2: 2,277,333 TPY H2SO4: 19.0 TPY | Auxiliary Boiler | 13.31 | Natural Gas | 80 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.005 | LB/MMBTU | 1 HR BLOCK AVG, DOES NOT APPLY DURING SS | BACT-PSD | NSPS , SIP , OPERATING PERMIT | U | 0 | U | 0.4 | LB/H | 1 HR BLOCK AVG, DOES NOT APPLY DURING SS | 0 |  |  | 0 | 0 | N
IN-0285 | WHITING CLEAN ENERGY, INC. | WHITING CLEAN ENERGY, INC. | LAKE | IN | 46394 | USA |  |  |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Trip Sinha, Section Chief, 317-234-4907, TSinha@idem.in.gov Tamara Havics, permit writer, 317-232-8219, THavics@idem.in.gov | 089-37495-00449 | 4911 | 221112 | Not Found | 08/08/2016 &nbsp;ACT | 08/02/2017 &nbsp;ACT | 2018-05-02 | 2018-06-15 | C | HTTP://PERMITS.AIR.IDEM.IN.GOV/37495f.pdf | Industrial steam and 545 MWe co-generation (combined heat and power) plant |  | Space Heaters | 13.31 |  | 0 |  | (a) Six (6) Sterling TF-400 natural gas-fired space heaters, identified as HTR 1 through 6, constructed in 2000, with a maximum capacity of 0.4 MMBtu per hour, each, with low NOx burners, and exhausting to atmosphere. (b) Three (3) Carrier 48TCED natural gas-fired space heaters, identified as HTR 7 through 9, constructed in 2000, with a maximum capacity of 0.224 MMBtu per hour, each, and exhausting to atmosphere. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0072 | LB/MMBTU | WHEN COMBUSTING NATURAL GAS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Additional PSD BACT PM limit requirements: PM emissions from Heaters 1 through 9 shall be controlled through the use of Good Combustion Practices. Heaters 1 through 9 shall combust only natural gas.
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | dew point heater | 13.31 | natural gas | 13.32 | mmBtu/hr |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | N |  | 0.008 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Waste Heat Boilers | 13.31 | Natural Gas | 50 | MMBTU/H | Five (5) Natural Gas-Fired 50 MMBtu/hr Waste Heat Boilers. Installed in 1986. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0074 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0311 | MOXIE FREEDOM GENERATION PLANT | MOXIE FREEDOM LLC | LUZERNE | PA | 18603 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 40-00129A | 4911 | 221112 | 110064098541 | 10/06/2014 &nbsp;ACT | 09/01/2015 &nbsp;ACT | 2017-07-28 | 2017-07-31 | A |  | The Project is for the construction and operation of two identical 1 x 1 power blocks, each consisting of a combustion gas turbine (CGT or CT) and a steam turbine (ST) configured in single shaft alignment, where each CT and ST train share one common electric generator. The turbines to be used for this project are Two General Electric (GE) 7HA.02 CTs, each in 1 x 1 single shaft combined- cycle power islands. Each CT and duct burner will exclusively fire pipeline-quality natural gas. The HRSGs will be equipped with selective catalytic reduction (SCR) to minimize nitrogen oxide (NOx) emissions and oxidation catalysts to minimize carbon monoxide (CO) and volatile organic compound (VOC) emissions from the CTs and DBâ€™s. The Project will also include several pieces of ancillary equipment. The list of equipment includes: One fuel gas dew-point heater - natural gas fired, common for all CTs Two CT inlet evaporative coolers - one for each CT (not emissions sources) Two air-cooled condensers (ACCs) - one for each HRSG (not emissions sources) One auxiliary boiler, natural gas-fired One diesel engine powered emergency generator One diesel engine powered fire water pump Diesel fuel, lubricating oil, and aqueous ammonia storage tanks The project once operational will produce 1050 MW Electric Generation |  | Auxilary Boiler | 13.31 | Natural Gas | 55.4 | MMBtu/hr | Shall construct qualifying small gas combustion units capable of reducing nitrogen oxides (NOx) and carbon monoxide (CO) emissions to or below: i. 30 ppmdv NOx at 3% O2 when firing gas; ii. 300 ppmdv CO at 3% O2. The combustion unit(s) shall be fired only on natural gas or liquefied petroleum gas Total fuel usage of the auxiliary boiler shall not exceed 214.9 MMscf on a 12-month rolling basis. Shall maintain and operate the source in accordance with good engineering practice. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.007 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 0.775 | TPY | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
IA-0107 | MARSHALLTOWN GENERATING STATION | INTERSTATE POWER AND LIGHT | MARSHALL | IA | 50158 | USA | ALAN ARNOLD | 319-786-4476 | ALANARNOLD@ALLIANTENERGY.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-A-499-P | 4911 | 221112 | Unknown | 10/03/2013 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2014-04-15 | 2016-05-04 | B | http://www.iowadnr.gov/InsideDNR/RegulatoryAir/ConstructionPermits/PermitSearch.aspx | Utility electric generating station | Two combined cycle turbines without duct burning. | auxiliary boiler | 13.31 | natural gas | 60.1 | mmBtu/hr | fuel limit of 288.7 million cubic feet of natural gas per 12-month rolling period | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | N |  | 0.008 | LB/MMBTU | AVERAGE OF 3 ONE-HOUR TEST RUNS | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N

## GCP and Clean Fuels
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUFLTOS1 in FGTOH | 13.31 | Natural gas | 10.2 | MMBTU/H | One natural gas-fired thermal oil system for thermally fused lamination lines rated at 10.2 MMBTU/H fuel heat input (EUFLTOS1 in FGTOH). Note: The throughput capacity, 10.2 MMBTU/H, is not a change but instead a correction from the previous entry. The previous entry is under MI-0421 for the original permit. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0004 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 0 | N | 0.02 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0421 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions related to the permit. Thank you. | 59-16 | 2493 | 321219 | Not Found | 06/30/2016 &nbsp;ACT | 08/26/2016 &nbsp;ACT | 2017-01-27 | 2017-07-20 | A |  | Particleboard manufacturing |  | EUFLTOS1 in FGTOH (Thermal Oil System for Thermally Fused Lamination Lines) | 13.31 | Natural gas | 34 | MMBTU/H | One natural gas fired thermal oil system for thermally fused lamination lines rated at 10.2 MMBTU/H fuel heat input (EUFLTOS1 in FGTOH). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0004 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0.02 | T/YR | BASED UPON A 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0421 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions related to the permit. Thank you. | 59-16 | 2493 | 321219 | Not Found | 06/30/2016 &nbsp;ACT | 08/26/2016 &nbsp;ACT | 2017-01-27 | 2017-07-20 | A |  | Particleboard manufacturing |  | EUTOH (In FGTOH)--Thermal Oil Heater | 13.31 | Natural gas | 34 | MMBTU/H | One natural gas fired thermal oil heater for press and sifter rated at 34 MMBTU/H fuel heat input (EUTOH in FGTOH). All falls under RBLC Process Type Code 30.590. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0004 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0.06 | T/YR | BASED UPON A 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUTOH in FGTOH | 13.31 | Natural gas | 38 | MMBTU/H | One natural gas-fired thermal oil heater for press and sifter rated at 38 MMBTU/hr fuel heat input (EUTOH in FGTOH). Also falls under the RBLC Process Type Code 30.590. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0004 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 0 | N | 0.07 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUFLTOS1 in FGTOH | 13.31 | Natural gas | 10.2 | MMBTU/H | One natural gas-fired thermal oil system for thermally fused lamination lines rated at 10.2 MMBTU/H fuel heat input (EUFLTOS1 in FGTOH). Note: The throughput capacity, 10.2 MMBTU/H, is not a change but instead a correction from the previous entry. The previous entry is under MI-0421 for the original permit. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0005 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 0 | N | 0.02 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0421 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions related to the permit. Thank you. | 59-16 | 2493 | 321219 | Not Found | 06/30/2016 &nbsp;ACT | 08/26/2016 &nbsp;ACT | 2017-01-27 | 2017-07-20 | A |  | Particleboard manufacturing |  | EUTOH (In FGTOH)--Thermal Oil Heater | 13.31 | Natural gas | 34 | MMBTU/H | One natural gas fired thermal oil heater for press and sifter rated at 34 MMBTU/H fuel heat input (EUTOH in FGTOH). All falls under RBLC Process Type Code 30.590. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0005 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0.08 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUTOH in FGTOH | 13.31 | Natural gas | 38 | MMBTU/H | One natural gas-fired thermal oil heater for press and sifter rated at 38 MMBTU/hr fuel heat input (EUTOH in FGTOH). Also falls under the RBLC Process Type Code 30.590. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0005 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 0 | N | 0.08 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 5.2 | X10^-4 LB/MMBTU |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, PICKLE LINE | 13.31 | NATURAL GAS | 67 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 5.2 | X10^-4 LB/MMBTU |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 5.2 | X10^-4 LB/MMBTU |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILERS SN-26 AND 27, GALVANIZING LINE | 13.31 | NATURAL GAS | 24.5 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 5.2 | X10^-4 LB/MMBTU |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, PICKLE LINE | 13.31 | NATURAL GAS | 67 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 5.2 | X10^-4 LB/MMBTU |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 5.2 | X10^-4 LB/MMBTU |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILERS SN-26 AND 27, GALVANIZING LINE | 13.31 | NATURAL GAS | 24.5 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 5.2 | X10^-4 LB/MMBTU |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, PICKLE LINE | 13.31 | NATURAL GAS | 67 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.00052 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGAUXBOILERS: Two auxiliary boilers &lt; 100 MMBTU/H heat input each | 13.31 | natural gas | 100 | MMBTU/H heat input each | There are two auxiliary boilers each rated at less than 100 MMBTU/H heat input. Fuel usage limited to not more than 416.3 MMscf of natural gas in each boiler per 12-month rolling timeperiod as determined at the end of each month. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Efficient combustion; natural gas fuel. | 0.0018 | LB/MMBTU | HEAT INPUT; TEST PROTOCOL WILL SPECIFY | BACT-PSD | N/A | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is 0.0018 LB/MMBTU heat input for each boiler. Test protocol will specify the averaging time. The fuel usage is limited to not more than 416.3 MMSCF of natural gas in each boiler per 12-month rolling time period as determined at the end of each month.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler A (EUAUXBOILERA) | 13.31 | natural gas | 55 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 55 MMBTU/hr fuel heat input (EUAUXBOILERA within flexible group FGAUXBOILERS). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0018 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler B (EUAUXBOILERB) | 13.31 | natural gas | 95 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 95 MMBtu/hr fuel heat input (EUAUXBOILERB within flexible group FGAUXBOILERS). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0018 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUAUXBOILER (Auxiliary boiler) | 13.31 | natural gas | 83.5 | MMBTU/H | One natural gas fired auxiliary boiler rated at 83.5 MMBTU/hr fuel heat input (EUAUXBOILER). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0018 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 42 | MMBTU/H | PIPELINE QUALITY NATURAL GAS FUEL ONLY, OPERATION OF ULTRA LOW-NOX BURNER TECHNOLOGY SUBJECT TO NSPS SUBPART DC RECORDKEEPING AND REPORTING REQUIREMENTS | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.0019 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0309 | LACKAWANNA ENERGY CTR/JESSUP | LACKAWANNA ENERGY CENTER, LLC | LACKAWANNA | PA | 18434 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 35-00069A | 4911 | 221112 | 110069993385 | 07/11/2014 &nbsp;ACT | 12/23/2015 &nbsp;ACT | 2017-07-18 | 2017-07-20 | A |  | This plan approval is for the construction and temporary operation of three (3) identical General Electric Model 7HA.02 natural gas fired combustion turbines and heat recovery steam generator with duct burners (CT/HRSG). Each CT/HRSG combined-cycle process block includes one (1) combustion gas turbine and one (1) heat recovery steam generator with duct burners with all three (3) CT/HRSG sharing one (1) steam turbine. The entire power block is rated at 1,500 MW. Additional equipment includes: one (1) 2,000 kW diesel-fired emergency generator one (1) 315 HP diesel-fired emergency fire water pump one (1) 184.8 MM BTU/hr natural gas fired boiler one (1) 12 MMBTU/hr natural gas fuel gas heater two (2) Diesel fuel storage tanks four (4) lubricating oil tanks one (1) aqueous ammonia storage tank |  | Auxillary Boiler | 13.31 | Natural gas | 13.31 | MMBtu/hr | Fired only on natural gas supplied by a public utility. Limited to 4000 hrs per year on a 12 month rolling basis. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.002 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 0.69 | TONS | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGFUELHTR (Two fuel pre-heaters identified as EUFUELHTR1 &amp; EUFUELHTR2) | 13.31 | Natural gas | 27 | MMBTU/H | Two natural gas fired dew point heaters for warming the natural gas fuel (EUFUELHTR1 & EUFUELHTR2 in flexible group FGFUELHTR). The total combined heat input during operation shall not exceed 27 MMBTU/H (each) as well. The CO2e limit is for both units combined; however the other limits are per unit. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.002 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME. | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above of 0.002 LB/MMBTU is for each fuel heater. At greater than $40,000 for the least expensive option, none of the control technologies are economically feasible. Control technologies evaluated were a scrubber and various types of fabric filters and ESPs.
IA-0106 | CF INDUSTRIES NITROGEN, LLC - PORT NEAL NITROGEN COMPLEX | CF INDUSTRIES NITROGEN, LLC | WOODBURY | IA | 51054 | USA | MIKE MAAS | 712-233-6222 | MMAAS@CFINDUSTRIES.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | Christopher A. Roling, PE Environmental Engineer Senior Iowa DNR - Air Quality Bureau 7900 Hickman Rd, Suite 1 Windsor Heights, IA 50324 (515) 242-6002 chris.roling@dnr.iowa.gov | PN 13-037 | 2873 | 325311 | 110000414089 | 02/01/2013 &nbsp;ACT | 07/12/2013 &nbsp;ACT | 2013-07-16 | 2016-05-04 | B |  | Nitrogenous fertilizer manufacturing including ammonia, urea, and urea-ammonium nitrate (UAN) solutions. |  | Startup Heater | 13.31 | natural gas | 58.8 | MMBTU/H | Limited to 5.76 MMCF of natural gas/yr | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | good operating practices & use of natural gas | 0.0024 | LB/MMBTU | AVERAGE OF THREE (3) STACK TEST RUNS | BACT-PSD | SIP | U | 0 | U | 0.007 | TONS/YR | ROLLING TWELVE (12) MONTH TOTAL | 0 |  |  | 0 | 0 | N
IA-0106 | CF INDUSTRIES NITROGEN, LLC - PORT NEAL NITROGEN COMPLEX | CF INDUSTRIES NITROGEN, LLC | WOODBURY | IA | 51054 | USA | MIKE MAAS | 712-233-6222 | MMAAS@CFINDUSTRIES.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | Christopher A. Roling, PE Environmental Engineer Senior Iowa DNR - Air Quality Bureau 7900 Hickman Rd, Suite 1 Windsor Heights, IA 50324 (515) 242-6002 chris.roling@dnr.iowa.gov | PN 13-037 | 2873 | 325311 | 110000414089 | 02/01/2013 &nbsp;ACT | 07/12/2013 &nbsp;ACT | 2013-07-16 | 2016-05-04 | B |  | Nitrogenous fertilizer manufacturing including ammonia, urea, and urea-ammonium nitrate (UAN) solutions. |  | Startup Heater | 13.31 | natural gas | 58.8 | MMBTU/H | Limited to 5.76 MMCF of natural gas/yr | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - 201A with 202 | (Particulate Matter (PM)) | PM | P | good operating practices & use of natural gas | 0.0024 | LB/MMBTU | AVERAGE OF THREE (3) STACK TEST RUNS | BACT-PSD | SIP | U | 0 | U | 0.007 | TONS/YR | ROLLING TWELVE (12) MONTH TOTAL | 0 |  |  | 0 | 0 | N
IA-0106 | CF INDUSTRIES NITROGEN, LLC - PORT NEAL NITROGEN COMPLEX | CF INDUSTRIES NITROGEN, LLC | WOODBURY | IA | 51054 | USA | MIKE MAAS | 712-233-6222 | MMAAS@CFINDUSTRIES.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | Christopher A. Roling, PE Environmental Engineer Senior Iowa DNR - Air Quality Bureau 7900 Hickman Rd, Suite 1 Windsor Heights, IA 50324 (515) 242-6002 chris.roling@dnr.iowa.gov | PN 13-037 | 2873 | 325311 | 110000414089 | 02/01/2013 &nbsp;ACT | 07/12/2013 &nbsp;ACT | 2013-07-16 | 2016-05-04 | B |  | Nitrogenous fertilizer manufacturing including ammonia, urea, and urea-ammonium nitrate (UAN) solutions. |  | Startup Heater | 13.31 | natural gas | 58.8 | MMBTU/H | Limited to 5.76 MMCF of natural gas/yr | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good operating practices and use of natural gas | 0.0024 | LB/MMBTU | AVERAGE OF THREE (3) STACK TEST RUNS | BACT-PSD | SIP | U | 0 | U | 0.007 | TONS/YR | ROLLING TWELVE (12) MONTH TOTAL | 0 |  |  | 0 | 0 | N
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | AUXILLARY BOILER | 13.31 | NATURAL GAS | 93 | MMBTU/H | NATURAL GAS FUEL ONLY, OPERATION OF LOW-NOX BURNER TECHNOLOGY, FLUE GAS RECIRCULATION (FGR), GOOD COMBUSTION CONTROLS, MAX HEAT INPUT OF 372,000 MMBTU/HR | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.005 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0041 | CPV ST. CHARLES | CPV MARYLAND, LLC | CHARLES | MD | 20646 | USA | DONALD ATWOOD | 7818482002 | DATWOOD@CPV.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLAIM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9280 | 4911 | 221119 | Not Found | 04/23/2014 &nbsp;ACT | 04/23/2014 &nbsp;ACT | 2015-07-31 | 2018-04-26 | C |  | 725 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT &lt; 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT &lt; 100.0 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 96.6 TONS/YR FACILITY-WIDE SAM EMISISON LIMIT < 7.0 TONS/YR FACILITY-WIDE PM2.5 (TOTAL) EMISSION LIMIT < 100.0 TONS/YR | AUXILLARY BOILER | 13.31 | NATURAL GAS | 93 | MMBTU/H | NATURAL GAS FUEL ONLY, OPERATION OF LOW-NOX BURNER TECHNOLOGY, FLUE GAS RECIRCULATION (FGR), GOOD COMBUSTION CONTROLS, MAX HEAT INPUT OF 372,000 MMBTU/HR | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.005 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0103 | CRICKET VALLEY ENERGY CENTER | CRICKET VALLEY ENERGY CENTER LLC | USA | NY | 12522-0407 | USA |  | 845-877-0596 | INFO@CRICKETVALLEY.COM | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-1326-00275/00009 | 4911 | 221112 | 110043340364 | 02/03/2016 &nbsp;ACT | 02/03/2016 &nbsp;ACT | 2017-08-24 | 2017-09-28 | A | http://www.dec.ny.gov/chemical/32249.html | Cricket Valley Energy Center LLC (CVEC) constructed the Cricket Valley Energy Center (the Facility), a nominal net 1,000-megawatt (MW) combined-cycle gas turbine electric generating facility, on a site located in Dover, Dutchess County, New York. The Facility consists of three General Electric (GE) Model 7FA.05 combustion turbine generators (CTGs) operating in combined-cycle mode with supplemental firing of the heat recovery steam generators (HRSGs); natural gas will be the sole fuel fired in the CTGs and duct burners. The Facility will include a natural gas-fired auxiliary boiler, four ultra-low sulfur distillate (ULSD) fired black-start generator engines and a ULSD-fired emergency fire pump engine. In addition to the air emitting equipment, the Facility will include three steam turbine generators (STGs), an air cooled condenser (ACC) and associated auxiliary equipment and systems. Each combined cycle generating unit consisting of the CTG, HRSG and STG will be exhausted through its own stack. Air emissions from the proposed Facility primarily consist of products of combustion from the CTGs, HRSG duct burners, and ancillary combustion sources. Dutchess County is designated as in attainment with respect to the National Ambient Air Quality Standards (NAAQS) for all criteria pollutants with the exception of ozone. Based upon the potential to emit (PTE) estimates, the Facility is subject to Prevention of Significant Deterioration (PSD) requirements for emissions of carbon monoxide (CO); nitrogen oxides (NOx); particulate matter (PM) with a diameter equal to or less than 10 microns (PM10), PM with a diameter equal to or less than 2.5 microns (PM2.5); greenhouse gases (GHG); sulfuric acid mist (H2SO4); and volatile organic compounds (VOC). In accordance with the NYSDECâ€™s Nonattainment New Source Review (NNSR) permitting program, the Facility is also subject to NNSR for emissions of NOx and VOC. |  | Auxiliary boiler | 13.31 | natural gas | 60 | MMBTU/H | Limited to 4,500 H/YR | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | good combustion practiced and pipeline quality natural gas | 0.005 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | EPA/OAR Method 5, 201/201A, or 202
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Auxilary Boiler | 13.31 | Natural Gas | 62.04 | MCF/hr | The proposed auxilary boiler will fire NG exclusively with maximum rated heat input capacity of 61.0 MMBtu/hr and is equipped with and ulatra-low NOx burner and a flue gas recirculation system for NOx control. It will be used for preheating components of HRSG and the 420 MW steam turbine during CT startup. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.005 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 1.3 | TPY | ANY CONSECUTIVE 12-MONTH PERIOD | 0 |  |  | 0 | 0 | N
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Auxilary Boiler | 13.31 | Natural Gas | 62.04 | MCF/hr | The proposed auxilary boiler will fire NG exclusively with maximum rated heat input capacity of 61.0 MMBtu/hr and is equipped with and ulatra-low NOx burner and a flue gas recirculation system for NOx control. It will be used for preheating components of HRSG and the 420 MW steam turbine during CT startup. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.005 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 1.3 | TPY | ANY CONSECUTIVE 12-MONTH PERIOD | 0 |  |  | 0 | 0 | N
*PA-0307 | YORK ENERGY CENTER BLOCK 2 ELECTRICITY GENERATION PROJECT | CALPINE MID-MERIT, LLC | YORK | PA | 17314 | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083D/F | 4911 | 221112 | 110043196528 | 06/04/2014 &nbsp;ACT | 06/15/2015 &nbsp;ACT | 2017-06-26 | 2017-07-12 | B |  | Calpine Mid-Merit, LLC. currently operates Block 1 of the York Energy Center under Title V operating permit 67-05083 with a rated capacity of 565 MW. This plan approval is for the construction and temporary operation of Block 2 Electricity Generation Project having a nominal generating capacity of 835 MW. Block 2 consists of two combined cycle NG/USLD fuel fired combustion turbines, one NG-fired auxiliary boiler, one cooling tower, NG piping componets, circuit breaker upgrades, five NG condensate tanks, and additional ULSD fuel oil storage tank. Each CT will be limited to 4500 hr/yr with duct firing; 480 hr/yr of ULSD |  | Auxilary Boiler | 13.31 | Natural Gas | 62.04 | MCF/hr | The proposed auxilary boiler will fire NG exclusively with maximum rated heat input capacity of 61.0 MMBtu/hr and is equipped with and ulatra-low NOx burner and a flue gas recirculation system for NOx control. It will be used for preheating components of HRSG and the 420 MW steam turbine during CT startup. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuels | 0.005 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 1.3 | TPY | ANY CONSECUTIVE 12-MONTH PERIOD | 0 |  |  | 0 | 0 | N
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-AUXBOILER1-2; Two (2) natural gas-fired auxiliary boilers. | 13.31 | natural gas | 40 | MMBTU/H | Two (2) natural gas-fired auxiliary boilers. 40 MMBTU/H each. Fuel restriction = 360.8 MMSCF/YR total for both units. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.005 | LB/MMBTU | TEST PROTOCOL; EACH UNIT. | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The PM2.5 emission limit of 0.005 LB/MMBTU applies to each unit.
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-AUXBOILER1-2; Two (2) natural gas-fired auxiliary boilers. | 13.31 | natural gas | 40 | MMBTU/H | Two (2) natural gas-fired auxiliary boilers. 40 MMBTU/H each. Fuel restriction = 360.8 MMSCF/YR total for both units. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.005 | LB/MMBTU | TEST PROTOCOL; EACH UNIT. | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The PM emission limit of 0.005 LB/MMBTU applies to each unit.
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUAUXBOILER (North Plant): Auxiliary Boilder | 13.31 | Natural gas | 61.5 | MMBTU/H | A natural gas-fired auxiliary boiler, rated at 61.5 MMBTU/H (HHV) to facilitate startup of the CTGHRSG train and to provide the required steam to support the startup of the facility, including but not limited to steam for sparging, STG seals, etc. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.005 | LB/MMBTU | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0433 | MEC NORTH, LLC AND MEC SOUTH LLC | MARSHALL ENERGY CENTER LLC | CALHOUN | MI | 49068 | USA | WILLARD LADD | 914-468-2402 | WLADD@DEVELOPMENTPARTNERS.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | There are two plants (MEC North, LLC and MEC South, LLC) that will operate as separate entities but they are considered a single stationary source and the installation of the two new plants was reviewed as a single project. There are two Air Permits to Install for the two plants (167-17 and 168-17). For technical questions regarding either of the two permits, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786 or at asselinc@michigan.gov. Thank you. | 167-17 AND 168-17 | 4911 | 221112 | Not Found | 05/22/2018 &nbsp;ACT | 06/29/2018 &nbsp;ACT | 2018-08-17 | 2018-08-22 | A |  | Natural gas combined cycle power plant (two plants: north and south) | There are two plants that will operate as separate entities and each received a separate Air Permit to Install, but they are considered one stationary source and were reviewed as one project. | EUAUXBOILER (South Plant): Auxiliary Boiler | 13.31 | Natural gas | 61.5 | MMBTU/h | A natural gas-fired auxiliary boiler, rated at 61.5 MMBTU/H (HHV) to facilitate startup of the CTGHRSG train and to provide the required steam to support the startup of the facility, including but not limited to steam for sparging, STG seals, etc. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.005 | LB/MMBTU | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0406 | RENAISSANCE POWER LLC | LS POWER DEVELOPMENT LLC | MONTCALM | MI | 48811 | USA | BRADLEY COOLEY | 636-534-3268 | BCOOLEY@LSPOWER.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Melissa Byrnes, at 517-284-6790 or at BYRNESM@michigan.gov for technical questions regarding this permit. Thank you. | 51-13 | 4911 | 221112 | 2611705287 | 07/13/2013 &nbsp;ACT | 11/01/2013 &nbsp;ACT | 2014-03-19 | 2016-07-07 | C |  | For technical questions regarding this permit, please contact the permit engineer, Melissa Byrnes, at 517-284-6790. Thank you. | Other facility-wide pollutants not listed below (tpy): PM10=211.19+ PM2.5=205.24+ Lead=0.0027+ CO2e=5,398,441+ Sulfuric Acid Mist=5.67+ | FG-AUXBOILER1-2; Two (2) natural gas-fired auxiliary boilers. | 13.31 | natural gas | 40 | MMBTU/H | Two (2) natural gas-fired auxiliary boilers. 40 MMBTU/H each. Fuel restriction = 360.8 MMSCF/YR total for both units. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.005 | LB/MMBTU | TEST PROTOCOL; EACH UNIT. | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The PM10 emission limit of 0.005 LB/MMBTU applies to each unit.
LA-0240 | FLOPAM INC. | FLOPAM INC. | IBERVILLE PARISH | LA | 70764 | USA | PETER NICHOLS | 912-884-3366 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT REVIEWER: DAN NGUYEN (225) 219-3180 | PSD-LA-747/1280-00141-V0 | 2899 | 325110 | UNKNOWN | 11/23/2009 &nbsp;ACT | 06/14/2010 &nbsp;ACT | 2010-07-14 | 2010-07-22 | A |  | A PROPOSED MANUFACTURING COMPLEX CONSISTS OF AN ACRYLAMIDE PLANT, A POWDER PLANT, A DIALLYLDIMETHYLAMMONIUMCHLORIDE (DADMAC) PLANT, A SPECIALTY PRODUCTS PLANT, AN EMULSION PLANT, A POLYAMINE PLANT, A DIMETHYLAMINEOETHYLACRYLATE (ADAM) PLANT, A CHLOROMETHYLATION (CM) PLANT, AN ACRYLAMIDO TERTIO BUTYL SULFONATE (ATBS) PLANT, AND AUXILIARY AND MISCELLANEOUS EQUIPMENT. | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | Boilers | 13.31 | natural gas | 25.1 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good equipment design and proper combustion practices, fueled by natural gas/alcohol | 0.005 | LB/MMBtu | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0.005 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N
LA-0240 | FLOPAM INC. | FLOPAM INC. | IBERVILLE PARISH | LA | 70764 | USA | PETER NICHOLS | 912-884-3366 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT REVIEWER: DAN NGUYEN (225) 219-3180 | PSD-LA-747/1280-00141-V0 | 2899 | 325110 | UNKNOWN | 11/23/2009 &nbsp;ACT | 06/14/2010 &nbsp;ACT | 2010-07-14 | 2010-07-22 | A |  | A PROPOSED MANUFACTURING COMPLEX CONSISTS OF AN ACRYLAMIDE PLANT, A POWDER PLANT, A DIALLYLDIMETHYLAMMONIUMCHLORIDE (DADMAC) PLANT, A SPECIALTY PRODUCTS PLANT, AN EMULSION PLANT, A POLYAMINE PLANT, A DIMETHYLAMINEOETHYLACRYLATE (ADAM) PLANT, A CHLOROMETHYLATION (CM) PLANT, AN ACRYLAMIDO TERTIO BUTYL SULFONATE (ATBS) PLANT, AND AUXILIARY AND MISCELLANEOUS EQUIPMENT. | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | Boilers | 13.31 | natural gas | 25.1 | MMBTU/H |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good equipment design and proper combustion practices, fueled by natural gas/alcohol | 0.005 | LB/MMBtu | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0.005 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N
NY-0104 | CPV VALLEY ENERGY CENTER | CPV VALLEY LLC | ORANGE | NY | 10940 | USA |  |  |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 3 845-256-3000 | 3-335600136/00001 | 4911 | 221112 | 110043332471 | 08/01/2013 &nbsp;ACT | 08/01/2013 &nbsp;ACT | 2017-08-25 | 2017-09-28 | A |  | CPV Valley Energy Center is a 680 MW combined cycle electric generating facility located in Middletown, NY. The combustion turbines are rated at 2,234 MMBTU/H firing natural gas and 2,145 MMBTU/H firing diesel fuel. The duct burners are rated for 500 MMBTU/H firing natural gas. In addition to the turbines their emission limits for the auxiliary boiler (73.5 MMBTU/H), emergency generator, fire pump, and gas heater. | State Facility Permit | Auxiliary boiler | 13.31 | natural gas | 0 |  |  | Particulate matter, filterable (FPM) | Other - Methods 201/201A and 202 | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.0063 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Also PM-10.
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGAUXBOILERS: Two auxiliary boilers &lt; 100 MMBTU/H heat input each | 13.31 | natural gas | 100 | MMBTU/H heat input each | There are two auxiliary boilers each rated at less than 100 MMBTU/H heat input. Fuel usage limited to not more than 416.3 MMscf of natural gas in each boiler per 12-month rolling timeperiod as determined at the end of each month. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Efficient combustion; natural gas fuel. | 0.007 | LB/MMBTU | HEAT INPUT; TEST PROTOCOL SPECIFY AVG | BACT-PSD | N/A | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is 0.007 LB/MMBTU heat input for each boiler. Test protocol will specify averaging time. Fuel usage is limited to not more than 416.3 MMscf of natural gas in each boiler per 12 month rolling time period as determined at the end of each month
MI-0410 | THETFORD GENERATING STATION | CONSUMERS ENERGY COMPANY | GENESEE | MI | 48548-9722 | USA | JAMES WALKER | 517-788-0428 | JAMES.WALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding this permit action, please contact the permit engineer, David Riddle, at 517-284-6798 or at RIDDLED@michigan.gov. Thank you. | 191-12 | 4911 | 221112 | 2604900033 | 05/08/2013 &nbsp;ACT | 07/25/2013 &nbsp;ACT | 2014-08-01 | 2016-05-04 | B |  | Four (4) natural gas fired combined cycle combustion turbine generators (CTG) and heat recovery steam generators (HRSG) with duct burner firing capability; ancillary facility equipment. | Existing substation property to be used for new construction of this generating station--4 CTG/HRSG. Additional equipment included in the permit: 315 hp diesel RICE fire pump engine; two natural gas auxiliary boilers < 100 MMBtu/hr; two natural gas fired fuel heaters; two peaker units (natural gas fired simple cycle combustion turbine driving an electrical generator--CTG). | FGAUXBOILERS: Two auxiliary boilers &lt; 100 MMBTU/H heat input each | 13.31 | natural gas | 100 | MMBTU/H heat input each | There are two auxiliary boilers each rated at less than 100 MMBTU/H heat input. Fuel usage limited to not more than 416.3 MMscf of natural gas in each boiler per 12-month rolling timeperiod as determined at the end of each month. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Efficient combustion; natural gas fuel. | 0.007 | LB/MMBTU | HEAT INPUT; TEST PROTOCOL WILL SPECIFY | BACT-PSD | N/A | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is 0.007 LB/MMBTU heat input for each boiler. Test protocol will specify the averaging time. Fuel usage is limited to not more than 416.3 MMscf of natural gas in each boiler per 12 month rolling time period as determined at the end of each month.
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Auxilary boiler | 13.31 | Natural Gas | 92.4 | MMBtu/hr | Operation of the auxiliary boiler shall not exceed 4000 hrs in any continuous 12-month period. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | GCP ULSD and good combustion practices | 0.007 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 1.29 | TPY | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Auxilary boiler | 13.31 | Natural Gas | 92.4 | MMBtu/hr | Operation of the auxiliary boiler shall not exceed 4000 hrs in any continuous 12-month period. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA/OAR Method 201/201A | (Particulate Matter (PM)) | PM | P | GCP ULSD and good combustion practices | 0.007 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 1.29 | TPY | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
*PA-0310 | CPV FAIRVIEW ENERGY CENTER | CPV FAIRVIEW, LLC | CAMBRIA | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 11-00536A | 4911 | 221112 | 110064823721 | 09/15/2015 &nbsp;ACT | 09/02/2016 &nbsp;ACT | 2017-07-18 | 2017-07-31 | A |  | This plan approval authorizes CPV Fairview, LLC to construct and temporarily operate the Fairview Energy Center. Air contamination sources and air cleaning devices authorized for construction and temporary operation under this plan approval include: A combined cycle electric generating unit consisting of two (2) General Electric (&quot;GE&quot;) 7HA.02 &quot;H&quot;-class combustion turbines each with maximum fuel type-based heat input of 3,338-MMBtu/hr (natural gas), 3,274-MMBtu/hr (ULSD), 3,199 MMBtu/hr (ethane blend), and equipped with dry low-NOx combustors and evaporative turbine intake cooling; two (2) heat recovery steam generators (HRSGs) each equipped with a low-NOx duct burner with maximum heat input of 425-MMBtu/hr, and a common steam turbine generator. Exhaust emissions from each combined cycle electric generating unit will be controlled by oxidation catalyst and selective catalytic reduction (SCR). - One (1) up to 12-cell mechanical draft wet cooling tower with high-efficiency drift eliminator. - One (1) natural gas-fired auxiliary boiler with maximum heat input of 92.4 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 12.8 MMBtu/hr. - One (1) natural gas-fired dew point heater with maximum heat input of 3.2 MMBtu/hr. - Two (2) 1,500-ekW diesel-fired emergency genset engines. - One (1) 422-bhp diesel-fired fire water pump engine. - One (1) 1,000,000-gallon ULSD storage tank. - Eight (8) sulfur hexafluoride (SF6) circuit breakers. - Plant roadways. - Natural gas and ethane blend piping components. |  | Auxilary boiler | 13.31 | Natural Gas | 92.4 | MMBtu/hr | Operation of the auxiliary boiler shall not exceed 4000 hrs in any continuous 12-month period. | Particulate matter, total (TPM) | Other - EPA/OAR Method 201/201A and 202 | (Particulate Matter (PM)) | PM | P | GCP ULSD and good combustion practices | 0.007 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 1.29 | TPY | 12-MONTH ROLLING BASIS | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler A (EUAUXBOILERA) | 13.31 | natural gas | 55 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 55 MMBTU/hr fuel heat input (EUAUXBOILERA within flexible group FGAUXBOILERS). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.007 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler B (EUAUXBOILERB) | 13.31 | natural gas | 95 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 95 MMBtu/hr fuel heat input (EUAUXBOILERB within flexible group FGAUXBOILERS). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.007 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler A (EUAUXBOILERA) | 13.31 | natural gas | 55 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 55 MMBTU/hr fuel heat input (EUAUXBOILERA within flexible group FGAUXBOILERS). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.007 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Auxiliary Boiler B (EUAUXBOILERB) | 13.31 | natural gas | 95 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 95 MMBtu/hr fuel heat input (EUAUXBOILERB within flexible group FGAUXBOILERS). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.007 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0229 | SHINTECH PLAQUEMINE PLANT 2 | SHINTECH LOUISIANA LLC | IBERVILLE | LA | 70764 | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-731 | 2821 | 325211 | UNKNOWN | 11/19/2010 &nbsp;ACT | 07/10/2008 &nbsp;ACT | 2009-04-02 | 2009-04-20 | B |  | A PROPOSED 1.81 BILLION LBS/YR PVC PRODUCTION COMPLEX WHICH WILL CONSIST OF A CHLORALKALI PLANT, AN EDC/VCM PLANT, AND A PVC PLANT | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | EQT122-EQT125 - FOUR VCM CRACKING FURNACES | 13.31 | NATURAL GAS | 90 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND CLEAN BURNING FUELS | 0.007 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0204 | PLAQUEMINE PVC PLANT | SHINTECH LOUISIANA LLC | IBERVILLE | LA |  | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: ANTHONY RANDALL, 225-219-3181 | PSD-LA-709(M-1) | 2821 | 325211 | 110020900104 | 03/03/2008 &nbsp;ACT | 02/27/2009 &nbsp;ACT | 2006-06-25 | 2009-08-06 | A |  | NEW 1.3 BILLION POUND PER YEAR PVC PLANT CONSISTING OF A CHLOR-ALKALI UNIT, AND EDC/VCM UNIT, AND A PVC UNIT. | VINYL CHLORIDE - 28.82 TPY. VINYL CHLORIDE (VC) WAS REGULATED AS A PSD POLLUTANT (SIGNIFICANCE LEVEL OF 1 TPY) IN LOUISIANA WHEN THIS PERMIT WAS ISSUED. LOUISIANA'S NSR REFORM RULES, ADOPTED DECEMBER 20, 2005, DELISTED VC. HAPS FROM THE PVC UNIT WERE SUBJECTED TO A 112(J) MACT DETERMINATION AFTER VACATURE OF 40 CFR 63 SUBPART J ON APRIL 19, 2005. BACT FOR VC IS EQUIVALENT TO MACT FOR VC. NNSR: BECAUSE VOC AND NOX EMISSIONS ARE LESS THAN 100 TPY, LAER WAS NOT REQUIRED. OFFSETS WERE REQUIRED PURSUANT TO A STATE-ONLY PROVISION IN LAC 33:III.504. PSD-LA-709(M-1) IS FOR 1) REMOVING A COOLING TOWER (M-8), CORRECTING CAPACITY OF COOLING TOWER M-7, AND 3) INCLUDING 19 EMERGENCY ENGINES AND THREE LOADING HOPPERS. | CRACKING FURNACES A-D | 13.31 |  | 90 | MMBTU/H EA. |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND USE OF NATURAL GAS AS FUEL | 0.007 | LB/MMBTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUAUXBOILER: Auxiliary Boiler | 13.31 | Natural gas | 99.9 | MMBTU/H | A natural gas-fired auxiliary boiler, rated at 99.9 MMBTU/H to facilitate startup of the CTG/HRSG trains and to provide steam to the steam turbine generator seals. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, low sulfur fuel | 0.007 | LB/MMBTU | HOURLY | BACT-PSD | SIP | N | 0 | N | 0.7 | LB/H | HOURLY | 0 |  |  | 0 | 0 | N
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUAUXBOILER: Auxiliary Boiler | 13.31 | Natural gas | 99.9 | MMBTU/H | A natural gas-fired auxiliary boiler, rated at 99.9 MMBTU/H to facilitate startup of the CTG/HRSG trains and to provide steam to the steam turbine generator seals. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, low sulfur fuel | 0.007 | LB/MMBTU | HOURLY | BACT-PSD | SIP | N | 0 | N | 0.7 | LB/H | HOURLY | 0 |  |  | 0 | 0 | N
*MI-0435 | BELLE RIVER COMBINED CYCLE POWER PLANT | DTE ELECTRIC COMPANY | ST. CLAIR | MI | 48054 | USA | MATTHEW PAUL | 313-235-3374 | MATTHEW.PAUL@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact the permit engineer, Mr. John Vial, at 517-284-6805 or at vialj@michigan.gov. Thank you. | 19-18 | 4911 | 221112 | Not Found | 06/22/2018 &nbsp;ACT | 07/16/2018 &nbsp;ACT | 2018-08-23 | 2018-08-24 | B |  | Natural gas combined-cycle power plant | The new combined cycle plant is proposed to be located near DTE's existing Belle River and St. Clair coal fired power plants. The three plants will be considered a single stationary source. It will have a capacity of 1,150 megawatts. | EUAUXBOILER: Auxiliary Boiler | 13.31 | Natural gas | 99.9 | MMBTU/H | A natural gas-fired auxiliary boiler, rated at 99.9 MMBTU/H to facilitate startup of the CTG/HRSG trains and to provide steam to the steam turbine generator seals. The auxiliary boiler is equipped with low NOx burners (LNB) and flue gas recirculation (FGR). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, low sulfur fuel | 0.007 | LB/MMBTU | HOURLY | BACT-PSD | SIP | N | 0 | N | 0.7 | LB/H | HOURLY | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Fuel pre-heater (EUFUELHTR) | 13.31 | natural gas | 3.7 | MMBTU/H | One natural gas-fired dew point heater for warming the natural gas fuel (EUFUELHTR). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.007 | LB/MMBTU | TEST PROTOCOL | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUFUELHTR (Fuel pre-heater) | 13.31 | Natural gas | 3.7 | MMBTU/H | One natural gas fired dew point heater for warming the natural gas fuel (EUFUELHTR). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.007 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUAUXBOILER (Auxiliary boiler) | 13.31 | natural gas | 83.5 | MMBTU/H | One natural gas fired auxiliary boiler rated at 83.5 MMBTU/hr fuel heat input (EUAUXBOILER). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.007 | LB/MMBTU | TEST PROTOCOL WIL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUAUXBOILER (Auxiliary boiler) | 13.31 | natural gas | 83.5 | MMBTU/H | One natural gas fired auxiliary boiler rated at 83.5 MMBTU/hr fuel heat input (EUAUXBOILER). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.007 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME. | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002A | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002B | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002C | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002D | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002E | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Regeneraton Heater - 51B001 | 13.31 | Natural Gas | 61 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.99 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Reactor Charge Heater - 53B001 | 13.31 | Natural Gas | 10.1 | MMBTU/HR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0.33 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002A | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002B | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002C | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002D | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Recycle Gas Heater - 51B002E | 13.31 | Natural Gas | 33 | MMBTU/HR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.06 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Regeneraton Heater - 51B001 | 13.31 | Natural Gas | 61 | MMBTU/HR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.00745 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.99 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Month Rolling Average)
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | AUXILIARY BOILER | 13.31 | PIPELINE QUALITY NATURAL GAS | 93 | MMBTU/H | ONE AUXILIARY BOILER WITH ULTRA-LOW NOX BURNER (ULNB) AND FLUE GAS RECIRCULATION (FGR) SUBJECT TO NSPS SUBPART DC RECORDKEEPING AND REPORTING REQUIREMENTS | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP EFFICIENT BOILER DESIGN, EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS, AND APPLICATION OF GOOD COMBUSTION PRACTICES | 0.0075 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0046 | KEYS ENERGY CENTER | KEYS ENERGY CENTER, LLC | PRINCE GEORGE'S | MD | 20613 | USA | JOHN J. DORAN | 5084282757 | DORAN4@NETZERO.NET | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE NO. 9297 | 4911 | 221119 | unknown | 07/03/2012 &nbsp;ACT | 10/31/2014 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 735 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANT NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | AUXILIARY BOILER | 13.31 | PIPELINE QUALITY NATURAL GAS | 93 | MMBTU/H | ONE AUXILIARY BOILER WITH ULTRA-LOW NOX BURNER (ULNB) AND FLUE GAS RECIRCULATION (FGR) SUBJECT TO NSPS SUBPART DC RECORDKEEPING AND REPORTING REQUIREMENTS | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP EFFICIENT BOILER DESIGN, EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS, AND APPLICATION OF GOOD COMBUSTION PRACTICES | 0.0075 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | AUXILLARY BOILER | 13.31 | NATURAL GAS | 45 | MMBTU/H | NATURAL GAS FUEL ONLY, OPERATION OF ULTRA LOW-NOX BURNER TECHNOLOGY, GOOD COMBUSTION PRACTICES, MAX HEAT INPUT OF 90,000 MMBUT/HR PER 12-MONTH ROLLING PERIOD | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES | 0.0075 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | AUXILLARY BOILER | 13.31 | NATURAL GAS | 45 | MMBTU/H | NATURAL GAS FUEL ONLY, OPERATION OF ULTRA LOW-NOX BURNER TECHNOLOGY, GOOD COMBUSTION PRACTICES, MAX HEAT INPUT OF 90,000 MMBUT/HR PER 12-MONTH ROLLING PERIOD | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES | 0.0075 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*MD-0042 | WILDCAT POINT GENERATION FACILITY | OLD DOMINION ELECTRIC CORPORATION (ODEC) | CECIL | MD | 17563 | USA | DAVID N. SMITH | 8049684045 | DSMITH@ODEC.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | CPCN CASE NO. 9327 | 4911 | 221119 | 110062854834 | 04/08/2014 &nbsp;ACT | 04/08/2014 &nbsp;ACT | 2015-07-31 | 2018-03-23 | A |  | 1000 MEGAWATT COMBINED CYCLE NATURAL GAS-FIRED POWER PLANTFACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | FACILITY-WIDE PM10 EMISSION LIMIT = 278 TONS/YR FACILITY-WIDE PM2.5 EMISSION LIMIT = 272 TONS/YR FACILITY-WIDE SAM EMISSION LIMIT = 96 TONS/YR FACILITY-WIDE CO2E EMISSION LIMIT = 3,498,026 TONS/YR | AUXILLARY BOILER | 13.31 | NATURAL GAS | 45 | MMBTU/H | NATURAL GAS FUEL ONLY, OPERATION OF ULTRA LOW-NOX BURNER TECHNOLOGY, GOOD COMBUSTION PRACTICES, MAX HEAT INPUT OF 90,000 MMBUT/HR PER 12-MONTH ROLLING PERIOD | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP EXCLUSIVE USE OF PIPELINE QUALITY NATURAL GAS AND GOOD COMBUSTION PRACTICES | 0.0075 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 42 | MMBTU/H | PIPELINE QUALITY NATURAL GAS FUEL ONLY, OPERATION OF ULTRA LOW-NOX BURNER TECHNOLOGY SUBJECT TO NSPS SUBPART DC RECORDKEEPING AND REPORTING REQUIREMENTS | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.0075 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MD-0045 | MATTAWOMAN ENERGY CENTER | MATTAWOMAN ENERGY, LLC | PRINCE GEORGE'S | MD | 20613 | USA | STEVEN TESSEM | SYSNULL | STESSEM@PANDAFUNDS.COM | 3 | MD001 | MARYLAND DEPARTMENT OF THE ENVIRONMENT | MR. WILLIAM PAUL | (410)537-3276 | bpaul@mde.state.md.us | WILLIAM PAUL 410-537-3276 BILL.PAUL@MARYLAND.GOV | PSC CASE. NO. 9330 | 4911 | 221119 | unknown | 07/19/2013 &nbsp;ACT | 11/13/2015 &nbsp;ACT | 2015-12-23 | 2016-05-13 | A | HTTP: | 990 MW COMBINED-CYCLE NATURAL GAS-FIRED POWER PLANTNOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE) | NOTE: PARTICULATE MATTER FACILITYWIDE EMISSIONS ARE PARTICULATE MATTER (FILTERABLE). THE FACILITY INCLUDES A WET MECHANICAL DRAFT COOLING TOWER (12 CELL) with 0.0005% RECIRCULATING WATER FLOW. | AUXILIARY BOILER | 13.31 | NATURAL GAS | 42 | MMBTU/H | PIPELINE QUALITY NATURAL GAS FUEL ONLY, OPERATION OF ULTRA LOW-NOX BURNER TECHNOLOGY SUBJECT TO NSPS SUBPART DC RECORDKEEPING AND REPORTING REQUIREMENTS | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.0075 | LB/MMBTU | 3-HOUR BLOCK AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Fuel pre-heater (EUFUELHTR) | 13.31 | natural gas | 3.7 | MMBTU/H | One natural gas-fired dew point heater for warming the natural gas fuel (EUFUELHTR). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion pracitces. | 0.0075 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUFLTOS1 in FGTOH | 13.31 | Natural gas | 10.2 | MMBTU/H | One natural gas-fired thermal oil system for thermally fused lamination lines rated at 10.2 MMBTU/H fuel heat input (EUFLTOS1 in FGTOH). Note: The throughput capacity, 10.2 MMBTU/H, is not a change but instead a correction from the previous entry. The previous entry is under MI-0421 for the original permit. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0075 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 0 | N | 0.33 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0421 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions related to the permit. Thank you. | 59-16 | 2493 | 321219 | Not Found | 06/30/2016 &nbsp;ACT | 08/26/2016 &nbsp;ACT | 2017-01-27 | 2017-07-20 | A |  | Particleboard manufacturing |  | EUTOH (In FGTOH)--Thermal Oil Heater | 13.31 | Natural gas | 34 | MMBTU/H | One natural gas fired thermal oil heater for press and sifter rated at 34 MMBTU/H fuel heat input (EUTOH in FGTOH). All falls under RBLC Process Type Code 30.590. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0075 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 1.1 | T/YR | BASED UPON A 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0425 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions regarding this permit. Thank you. | 59-16A | 2493 | 321219 | Not Found | 03/06/2017 &nbsp;ACT | 05/09/2017 &nbsp;ACT | 2017-08-02 | 2017-11-15 | A |  | Particleboard manufacturing. |  | EUTOH in FGTOH | 13.31 | Natural gas | 38 | MMBTU/H | One natural gas-fired thermal oil heater for press and sifter rated at 38 MMBTU/hr fuel heat input (EUTOH in FGTOH). Also falls under the RBLC Process Type Code 30.590. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0075 | LB/MMBTU | TEST PROTOCOL SHALL SPECIFY | BACT-PSD |  | N | 0 | N | 1.2 | T/YR | 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0412 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin, at 517-284-6786 or at AsselinC@michigan.gov, for technical questions regarding this permit. Thank you. | 107-13 | 4931 | 221112 | 26139P0465 | 10/17/2013 &nbsp;ACT | 12/04/2013 &nbsp;ACT | 2014-08-15 | 2016-05-05 | A |  | Natural gas combined heat and power plant. |  | Fuel pre-heater (EUFUELHTR) | 13.31 | natural gas | 3.7 | MMBTU/H | One natural gas-fired dew point heater for warming the natural gas fuel (EUFUELHTR). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0075 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
AL-0280 | LENZING FIBERS, INC. | LENZING FIBERS, INC. | MOBILE | AL | 36505 | USA | MR. KEVIN, PLANT MANAGER ALLEN | 251-679-2814 | K.ALLEN@LENZING.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-0047-X011 | 2823 | 325221 | 110043792278 | 09/15/2011 &nbsp;ACT | 12/06/2011 &nbsp;ACT | 2015-03-17 | 2016-05-09 | D |  | Production of lyocell cellulose fiber by solvent spinning process. | NAICS Code: 325220 | Natural Gas Fired Broiler #3 | 13.31 | Natural Gas | 100 | MMBTU/Hr |  | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 0.0075 | LB/MMBTU | LB/MM SCF OF NATURAL GAS USED | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.0075 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) NATURAL GAS AUXILIARY BOILERS | 13.31 | NATURAL GAS | 80 | MMBTU/H | BOTH BOILERS, LABELED AS B001 AND B002, ARE EQUIPPED WITH LOW NOX BURNERS WITH FLUE GAS REGULATION. THIS IS CONSIDERED A STEAM GENERATING UNIT. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND FUEL SPECIFICATIONS | 0.0075 | LB/MMBTU | 3 HOURS | BACT-PSD |  |  | 0 |  | 0.6 | LB/H | 3 HOURS | 0 |  |  | 0 | 0 | N |  | LIMIT ONE AND TWO ARE FOR EACH BOILER
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) NATURAL GAS AUXILIARY BOILERS | 13.31 | NATURAL GAS | 80 | MMBTU/H | BOTH BOILERS, LABELED AS B001 AND B002, ARE EQUIPPED WITH LOW NOX BURNERS WITH FLUE GAS REGULATION. THIS IS CONSIDERED A STEAM GENERATING UNIT. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND FUEL SPECIFICATIONS | 0.0075 | LB/MMBTU | 3 HOURS | BACT-PSD |  |  | 0 |  | 0.6 | LB/H | 3 HOURS | 0 |  |  | 0 | 0 | N |  | LIMIT ONE AND TWO ARE FOR EACH BOILER
IN-0158 | ST. JOSEPH ENEGRY CENTER, LLC | ST. JOSEPH ENERGY CENTER, LLC | ST. JOSEPH | IN | 46552 | USA | MR. WILLARD LADD | 9144682404 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 141-31003-00579 | 4911 | 221112 | 110054881963 | 10/03/2011 &nbsp;ACT | 12/03/2012 &nbsp;ACT | 2013-08-15 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/31003F.PDF | STATIONARY ELECTRIC UTILITY GENERATING STATION |  | TWO (2) NATURAL GAS AUXILIARY BOILERS | 13.31 | NATURAL GAS | 80 | MMBTU/H | BOTH BOILERS, LABELED AS B001 AND B002, ARE EQUIPPED WITH LOW NOX BURNERS WITH FLUE GAS REGULATION. THIS IS CONSIDERED A STEAM GENERATING UNIT. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND FUEL SPECIFICATIONS | 0.0075 | LB/MMBTU | 3 HOURS | BACT-PSD |  |  | 0 |  | 0.6 | LB/H | 3 HOURS | 0 |  |  | 0 | 0 | N |  | LIMIT ONE AND TWO ARE FOR EACH BOILER.
MI-0420 | DTE GAS COMPANY--MILFORD COMPRESSOR STATION | DTE GAS COMPANY | OAKLAND | MI | 48042 | USA | BARRY MARIETTA | 313-235-5611 | MARIETTAB@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For permit related questions, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786. | 185-15 | 4922 | 486210 | Not Found | 04/12/2016 &nbsp;ACT | 06/03/2016 &nbsp;ACT | 2016-09-16 | 2017-04-28 | B |  | Natural gas compressor station. |  | FGAUXBOILERS | 13.31 | Natural gas | 6 | MMBTU/H | Two natural gas-fired auxiliary boilers, each rated at 6 MMBTU/H fuel heat input. The boilers are identified as EUAUXBOIL2 and EUAUXBOIL3 within the flexible group FGAUXBOILERS. The boilers are subject to 40 CFR Part 63 Subpart DDDDD, which requires tune ups. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuel (pipeline quality natural gas). | 0.0075 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 0.0075 lb/MMBTU for each boiler. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM10 emissions were assumed the same as PM2.5, so the cost analysis was equivalent. *Pulse jet fabric filter baghouse: minimum of $43,942 per ton *Dry ESP (Wire-plate type): minimum of $31,291 per ton *Wet ESP (Wire-plate type): minimum of $54,758 per ton *Venturi Scrubber: minimum of $37,237 per ton.
MI-0420 | DTE GAS COMPANY--MILFORD COMPRESSOR STATION | DTE GAS COMPANY | OAKLAND | MI | 48042 | USA | BARRY MARIETTA | 313-235-5611 | MARIETTAB@DTEENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For permit related questions, please contact the permit engineer Ms. Catherine Asselin at 517-284-6786. | 185-15 | 4922 | 486210 | Not Found | 04/12/2016 &nbsp;ACT | 06/03/2016 &nbsp;ACT | 2016-09-16 | 2017-04-28 | B |  | Natural gas compressor station. |  | FGAUXBOILERS | 13.31 | Natural gas | 6 | MMBTU/H | Two natural gas-fired auxiliary boilers, each rated at 6 MMBTU/H fuel heat input. The boilers are identified as EUAUXBOIL2 and EUAUXBOIL3 within the flexible group FGAUXBOILERS. The boilers are subject to 40 CFR Part 63 Subpart DDDDD, which requires tune ups. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and low sulfur fuel (pipeline quality natural gas). | 0.0075 | LB/MMBTU | TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 0.0075 lb/MMBTU for each boiler. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM10 emissions were assumed the same as PM2.5, so the cost analysis was equivalent. *Pulse jet fabric filter baghouse: minimum of $43,942 per ton *Dry ESP (Wire-plate type): minimum of $31,291 per ton *Wet ESP (Wire-plate type): minimum of $54,758 per ton *Venturi Scrubber: minimum of $37,237 per ton.
MI-0421 | GRAYLING PARTICLEBOARD | ARAUCO NORTH AMERICA | CRAWFORD | MI | 49738 | USA | RICH WEBER | 803-431-2046 | RICH.WEBER@ARAUCO-NA.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Mr. Andrew Drury, at 517-284-6792 or at drurya@michigan.gov for technical questions related to the permit. Thank you. | 59-16 | 2493 | 321219 | Not Found | 06/30/2016 &nbsp;ACT | 08/26/2016 &nbsp;ACT | 2017-01-27 | 2017-07-20 | A |  | Particleboard manufacturing |  | EUFLTOS1 in FGTOH (Thermal Oil System for Thermally Fused Lamination Lines) | 13.31 | Natural gas | 34 | MMBTU/H | One natural gas fired thermal oil system for thermally fused lamination lines rated at 10.2 MMBTU/H fuel heat input (EUFLTOS1 in FGTOH). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0075 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0.33 | T/YR | BASED UPON A 12-MO ROLLING TIME PERIOD | 0 |  |  | 0 | 0 | N |  | No add on control identified.
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUFUELHTR (Fuel pre-heater) | 13.31 | Natural gas | 3.7 | MMBTU/H | One natural gas fired dew point heater for warming the natural gas fuel (EUFUELHTR). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0075 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0424 | HOLLAND BOARD OF PUBLIC WORKS - EAST 5TH STREET | HOLLAND BOARD OF PUBLIC WORKS | OTTAWA | MI | 49423 | USA | DAVID KOSTER | 616-355-1562 | DKOSTER@HOLLANDBPW.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | For technical questions regarding the permit, please contact: Michelle Rogers at 517-284-6799; ROGERSM13@michigan.gov; OR Catherine Asselin at 517-284-6786; ASSELINC@michigan.gov Thank you. | 107-13C | 4931 | 221112 | Not Found | 10/17/2016 &nbsp;ACT | 12/05/2016 &nbsp;ACT | 2017-07-28 | 2018-03-08 | A |  | Natural gas combined heat and power plant. | Permit Number 107-13E revised Permit 107-13C as follows: 1) All ppmdv limits were changed to ppmvd in the CTGHRSG section for NOx, CO and VOC. Also, 2) The process notes for the natural gas emergency engine and the diesel fire pump emergency engine were revised as well. No other changes were made. As such, this RBLC entry includes the updated information as identified above. Additionally, this is an updated determination for this facility, which is still under construction and has not yet operated. The original RBLC determination for the facility is identified as MI-0412. | EUFUELHTR (Fuel pre-heater) | 13.31 | Natural gas | 3.7 | MMBTU/H | One natural gas fired dew point heater for warming the natural gas fuel (EUFUELHTR). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0075 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME. | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
SC-0112 | NUCOR STEEL - BERKELEY | NUCOR STEEL | BERKELEY | SC | 29450 | USA | RAY SIMS | 8433366123 | SIMSR@NUCORSTEEL.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MR. DENNIS CAMIT | (803)898-4284 | camitdr@dhec.sc.gov | WANDA PARNELL (803) 898-4123 | 0420-0060-DO | 3312 | 331111 | 110000353527 | 12/06/2007 &nbsp;ACT | 05/05/2008 &nbsp;ACT | 2012-05-09 | 2013-10-30 | D |  | SCRAP STEEL RECYCLING MILL |  | TUNNEL FURNACE BURNERS | 13.31 | NATURAL GAS | 58 | MMBTU/H | THIS PROJECT IS ADDING AN ADDITIONAL 58 MILLION BTU/HR HEAT INPUT TO EXISTING TUNNEL FURNACE SYSTEM. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP NATURAL GAS COMBUSTION WITH GOOD COMBUSTION PRACTICES PER MANUFACTURER'S GUIDANCE | 0.0076 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0.0076 | LB/MMBTU |  | 0 | 0 | N
OK-0128 | MID AMERICAN STEEL ROLLING MILL | MID AMERICAN STEEL AND WIRE COMPANY | MARSHALL | OK | 73446 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2003-106-C(M-1) PSD | 3312 | 331111 | 110022524062 | 03/26/2008 &nbsp;ACT | 09/08/2008 &nbsp;ACT | 2008-12-31 | 2010-12-17 | B |  | THE FACILITY WAS CONSTRUCTED UNDER PERMIT NO. 2003-106-C ISSUED MARCH 25, 2003, AND IS CURRENTLY OPERATED UNDER PERMIT NO. 2003-106-O ISSUED JANUARY 3, 2005. THE FACILITY CURRENTLY OPERATES A SINGLE 74 MMBTUH GAS-FIRED FURNACE FOR SOFTENING STEEL BILLETS SO THAT THEY CAN BE DRAWN IN TO WIRE. | MID AMERICAN PROPOSES TO INSTALL TWO ELECTRIC ARC STEEL MELTING FURNACES. THE FURNACES WERE FABRICATED IN 2000 FOR INSTALLATION AT ANOTHER COMPANY SITE THAT WAS NOT CONSTRUCTED, THE PROPOSED GRIFFIN WHEEL PLANT AT TULSA. THE PROPOSED FURNACES WILL BE CAPABLE OF PRODUCING A TOTAL OF APPROXIMATELY 80 TONS/HR (640,000 TONS PER YEAR) OF Â¿BILLETÂ¿ Â¿ (BAR-SHAPED INGOTS) STEEL. THE STEEL MAY BE USED ON-SITE IN THE EXISTING WIRE PRODUCTION UNIT OR SOLD TO OTHER MILLS. | Ladle pre-heater and refractory drying | 13.31 | natural gas | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.0076 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0173 | CMC STEEL OKLAHOMA | COMMERCIAL METALS COMPANY | BRYAN | OK | 74701 | USA | RANDALL WALKER | 830-372-8507 | RANDALL.WALKER@CMC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2015-0643-C PSD | 3312 | 331111 | 013-00047 | 09/09/2015 &nbsp;ACT | 01/19/2016 &nbsp;ACT | 2016-01-19 | 2016-07-07 | A |  | In this steel mill, CMC will manufacture steel products from scrap steel. Iron ore will not be processed at the mill. Scrap metal will be transported into the facility to be used as feedstock for the Melt Shop. Once the molten steel reaches the desired conditions, it will be transferred to a large refractory-lined vessel known as a ladle. The ladle will be transported to a continuous caster, where the steel will be poured into a refractory-lined surge vessel called a tundish and subsequently into a water-cooled mold. After casting, the continuous steel strand will be rolled to the desired shape. After rolling, the steel will be cooled, bundled, and stored. To produce some structural material such as angles and channels, the rebar will be unbundled and passed through a straightener roller process. The finished products will be shipped off-site by truck as needed for use by customers. | Emissions of NOx, CO, VOC, SO2,PM10/PM2.5, and GHG exceed the applicable SER. Therefore, each is subject to PSD review. | Heaters (Gas-Fired) | 13.31 | Natural Gas | 0 |  | Numerous gas-fired heaters will be installed. The application requested that the sizes all be kept confidential. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.0076 | LB/MMBTU |  | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0173 | CMC STEEL OKLAHOMA | COMMERCIAL METALS COMPANY | BRYAN | OK | 74701 | USA | RANDALL WALKER | 830-372-8507 | RANDALL.WALKER@CMC.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2015-0643-C PSD | 3312 | 331111 | 013-00047 | 09/09/2015 &nbsp;ACT | 01/19/2016 &nbsp;ACT | 2016-01-19 | 2016-07-07 | A |  | In this steel mill, CMC will manufacture steel products from scrap steel. Iron ore will not be processed at the mill. Scrap metal will be transported into the facility to be used as feedstock for the Melt Shop. Once the molten steel reaches the desired conditions, it will be transferred to a large refractory-lined vessel known as a ladle. The ladle will be transported to a continuous caster, where the steel will be poured into a refractory-lined surge vessel called a tundish and subsequently into a water-cooled mold. After casting, the continuous steel strand will be rolled to the desired shape. After rolling, the steel will be cooled, bundled, and stored. To produce some structural material such as angles and channels, the rebar will be unbundled and passed through a straightener roller process. The finished products will be shipped off-site by truck as needed for use by customers. | Emissions of NOx, CO, VOC, SO2,PM10/PM2.5, and GHG exceed the applicable SER. Therefore, each is subject to PSD review. | Heaters (Gas-Fired) | 13.31 | Natural Gas | 0 |  | Numerous gas-fired heaters will be installed. The application requested that the sizes all be kept confidential. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.0076 | LB/MMBTU |  | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
SC-0112 | NUCOR STEEL - BERKELEY | NUCOR STEEL | BERKELEY | SC | 29450 | USA | RAY SIMS | 8433366123 | SIMSR@NUCORSTEEL.COM | 4 | SC001 | SOUTH CAROLINA DEPT OF HEALTH & ENV CTRL, BUREAU OF AIR QUALITY | MR. DENNIS CAMIT | (803)898-4284 | camitdr@dhec.sc.gov | WANDA PARNELL (803) 898-4123 | 0420-0060-DO | 3312 | 331111 | 110000353527 | 12/06/2007 &nbsp;ACT | 05/05/2008 &nbsp;ACT | 2012-05-09 | 2013-10-30 | D |  | SCRAP STEEL RECYCLING MILL |  | VACUUM DEGASSER BOILER | 13.31 | NATURAL GAS | 50.21 | MMBTU/H |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES PER MANUFACTURER'S GUIDANCE | 0.0076 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0.0076 | LB/MMBTU |  | 0 | 0 | N
OH-0352 | OREGON CLEAN ENERGY CENTER | ARCADIS, US, INC. | LUCAS | OH | 43616 | USA | LYNN GRESOCK | 978-322-4520 | LYNN.GRESOCK@ARCADIS-US.CO | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0110840 | 4931 | 221112 | 110064669737 | 04/03/2013 &nbsp;ACT | 06/18/2013 &nbsp;ACT | 2013-07-15 | 2016-05-04 | A |  | 799 Megawatt Combined Cycle Combustion Turbine Power Plant | The permit is set up to install either 2 Mitsubishi M501 GAC units or 2 Siemens SGT-8000H units, not both; with dedicated heat recovery steam generators (HRSG), steam turbine generator, and electric generator. | Auxillary Boiler | 13.31 | Natural Gas | 99 | MMBtu/H | 99 MMBTU/H auxillary boiler with low-NOx burners and flue gas re-circulation, burning only natural gas. Boiler restricted to 2000 hours of operation per rolling 12-months. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Clean burning fuel, only burning natural gas | 0.008 | LB/MMBTU |  | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.79 | T/YR | PER ROLLING 12-MONTHS | 0.008 | LB/MMBTU |  | 0 | 0 | N |  | Limit is for PM10 and PM2.5 together. BACT: 0.008 LB/MMBTU. Restricted to 2000 hours of operation per rolling 12-months.
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Reactor Charge Heater - 53B001 | 13.31 | Natural Gas | 10.1 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Combustion controls (proper burner design and operation using natural gas) | 0.008 | LB/MMBTU | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0.33 | T/YR | ANNUAL MAXIMUM | 0 |  |  | 0 | 0 | N |  | BACT Limit = 0.00745 LB/MMBTU (12-Hour Rolling Average)
*WV-0029 | HARRISON COUNTY POWER PLANT | ESC HARRISON COUNTY POWER, LLC | HARRISON | WV | 26301 | USA | ANDREW DORN | 7163121042 | DREWDORN@ENSOLCONSORTIUM.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Engineer: Mr. Steve Pursley 304-926-0499 x1218 steven.r.pursley@wv.gov | R14-0036 | 4911 | 221112 | Not Found | 04/26/2017 &nbsp;ACT | 03/27/2018 &nbsp;ACT | 2018-06-25 | 2018-06-25 | A | https://dep.wv.gov/daq/Documents/March 2018 Permits and Evals/033-00264_PERM_R14-0036.pdf | Nominal 640 mWe natural gas-fired combined-cycle power plant. Small sources: Emergency Generator, Fire Water Pump, Fuel Gas Heater not included in RBLC - may request info or see permit for details. |  | Auxiliary Boiler | 13.31 | Natural Gas | 77.8 | mmBtu/hr | Annual emission based on 4600 hours/year. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GCP Natural gas fired exclusively | 0.008 | LB/MMBTU |  | BACT-PSD | SIP | U | 0 | U | 1.38 | TONS/YEAR |  | 0.008 | LB/MMBTU |  | 0 | 0 | N
OK-0156 | NORTHSTAR AGRI IND ENID | NORTHSTAR AGRI INDUSTRIES | GARFIELD | OK | 73701 | USA | JIM DUDLEY | 701-478-5848 | JDUDLEY@NORTHSTARAGRI.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2013-0109-C PSD | 2076 | 311223 | Not Found | 01/31/2013 &nbsp;ACT | 07/31/2013 &nbsp;ACT | 2014-06-19 | 2018-05-11 | A |  | The new Northstar Agri Industries â€“ Enid facility will be designed to convert 2,500 TPD of seeds into crude oil and RBD oil. The facility consists of several processing steps to prepare seed and remove up to 100 million gallons per year of crude oil and RBD oil. | FRS Entered as &lsquo;&lsquo;047-00098&lsquo;&lsquo;. Too short for a FRS. The new Northstar Agri Industries â€“ Enid facility will be designed to convert 2,500 TPD of seeds into crude oil and RBD oil. The facility consists of several processing steps to prepare seed and remove up to 100 million gallons per year of crude oil and RBD oil. | Gas-fired Boiler | 13.31 | Natural Gas | 95 | MMBTUH |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion | 0.0126 | LB/MMBTU |  | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Mfg Data (3 boilers)
OK-0156 | NORTHSTAR AGRI IND ENID | NORTHSTAR AGRI INDUSTRIES | GARFIELD | OK | 73701 | USA | JIM DUDLEY | 701-478-5848 | JDUDLEY@NORTHSTARAGRI.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2013-0109-C PSD | 2076 | 311223 | Not Found | 01/31/2013 &nbsp;ACT | 07/31/2013 &nbsp;ACT | 2014-06-19 | 2018-05-11 | A |  | The new Northstar Agri Industries â€“ Enid facility will be designed to convert 2,500 TPD of seeds into crude oil and RBD oil. The facility consists of several processing steps to prepare seed and remove up to 100 million gallons per year of crude oil and RBD oil. | FRS Entered as &lsquo;&lsquo;047-00098&lsquo;&lsquo;. Too short for a FRS. The new Northstar Agri Industries â€“ Enid facility will be designed to convert 2,500 TPD of seeds into crude oil and RBD oil. The facility consists of several processing steps to prepare seed and remove up to 100 million gallons per year of crude oil and RBD oil. | Gas-fired Boiler | 13.31 | Natural Gas | 95 | MMBTUH |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion | 0.013 | LB/MMBTU | 3-HOUR AVG | BACT-PSD | N/A | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Mfg Data (3 boilers)
WY-0075 | CHEYENNE PRAIRIE GENERATING STATION | BLACK HILLS POWER, INC | LARAMIE | WY | 82009 | USA | TIM ROGERS | (605) 721-2286 | TIM.ROGERS@BLACKHILLSCORP.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | MD-16173 | 491 | 221122 | Not Found | 05/01/2014 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2014-06-16 | 2018-05-11 | B |  | Nominal 220 megawatt (MW) gross electrical facility. | Installation of a 25.06 MMBtu/hr Auxiliary Boiler (Cleaver Brooks CBEX Elite 600). Subject to PSD based on project aggregation. | Auxiliary Boiler | 13.31 | natual gas | 25.06 | MMBtu/h |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0175 | LB/MMBTU | 3 HOUR AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0.4 | LB/H | 3 HOUR AVERAGE | 0 |  |  | 0 | 0 | N