## Al Pollutants_Medium Gas Boiler
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT START-UP HEATER | 12.31 | NATURAL GAS | 38 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATING PRACTICES | 117 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | START-UP BOILER | 12.31 | NATURAL GAS | 240 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATING PRACTICES | 117 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | TUNNEL FURNACES SN-20 AND 21 | 12.31 | NATURAL GAS | 234 | MMBTU/H | 2 TUNNEL FURNCE SECTIONS 234 MMBTU/HR AND 192 MMBTU/HR MADE UP OF A SERIES OF INDIVIDUAL 3 MMBTU BURNERS. | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATING PRACTICES | 117 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Startup Heater | 12.31 | Natural gas | 110.12 | MMBTU/H |  | Carbon Dioxide | EPA/OAR Mthd 3A | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | good combustion practices | 117 | LB/MMBTU | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | FOUR (4) NATURAL GAS-FIRED BOILERS | 12.31 | NATURAL GAS | 218 | MMBTU/HR, EACH | FUEL INPUT TO ALL FOUR BOILERS SHALL NOT EXCEED 2,802 MMCF/YEAR | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | PROPER DESIGN AND GOOD COMBUSTION; ENERGY EFFICIENT DESIGN: AIR INLET CONTROLS, HEAT RECOVERY, CONDENSATE RECOVERY AND BLOWDOWN HEAT RECOVERY | 59.61 | TONS/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | MUST ACHIEVE A THERMAL EFFICIENCY OF 80% BASED ON THE HIGHER HEATING VALUE.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | NATURAL GAS AUXILIARY BOILERS (EU-012A, EU-012B, EU-012C) | 12.31 | NATURAL GAS | 218.6 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD COMBUSTION PRACTICES AT ALL TIMES THE BOILERS ARE IN OPERATION. | 59.61 | TON/MMCF EACH | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 1877.39 | MMCF/12 MONTH EACH | ROLLING AVERAGE | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: SHALL COMBUST NATURAL GAS LIMIT 4: EACH SHALL BE DESIGNED TO ACHIEVE A MINIMUM 80% THERMAL EFFICIENCY LIMIT 5: EACH SHALL BE EQUIPPED WITH THE FOLLOWING ENERGY EFFICIENCY DESIGN FEATURES (1) AIR INLET CONTROLS, (2) HEAT RECOVERY, (3) CONDENSATE RECOVERY, (4) BLOW DOWN HEAT RECOVERY
TX-0629 | BASF TOTAL PETROCHMICALS LP | BASF TOTAL PETROCHMICALS LP | JEFFERSON | TX | 77643 | USA | RYAN JOES | 409-960-5245 | RYAN.J.JOES@BASF.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA REGION 6 PERMIT WRITER: AIMEE WILSON, EPA REGION 6, AIR PERMITTING SECTION (6PD-R), 1445 ROSS AVENUE, DALLAS, TX 75202 | PSD-TX-903-GHG | 2869 | 325110 | 110006134691 | 06/17/2011 &nbsp;ACT | 08/24/2012 &nbsp;ACT | 2013-06-26 | 2013-09-25 | D | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | THIS PROJECT AUTHORIZES BASF TO ADD A 10TH ETHYLENE CRACKING FURNACE TO THE EXISTING FURNACE BANK, AND MODIFY OTHER EXISTING SUPPORTING UNITS TO PRODUCE UTILITIES (ELECTRICITY AND STEAM) CONSUMED BY THE SITE FROM MULTIPLE FUEL STREAMS, INCLUDING PRODUCED HIGH HYDROGEN GAS. THE 10TH FURNACE IS CAPABLE OF CRACKING MULTIPLE HYDROCARBON FEEDSTOCKS BUT WILL BE OPTIMIZED TO HANDLE ETHANE GAS. WITH THIS PERMIT THE TOTAL PRODUCTION OF ETHYLENE WILL BE INCREASED TO 2.87 BILLION POUNDS PER YEAR. FURNACE 10 WILL BE CAPABLE OF PRODUCING 420,000,000 POUNDS OF ETHYLENE PER YEAR, BASED ON MAXIMUM PRODUCTION FROM NAPHTHA FEED. |  | Gas Turbine Auxiliary Duct Burners | 12.31 | Natural gas | 310.4 | MMbtu/H | For Process IDs:N-20A and N-20B. | Carbon Dioxide | Other - Equation C-2b in 40 CFR Part 98 Subpart C. | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | A | Selective Catalytic Reduction Control (SCR). | 117786 | T/YR | 365-DAY ROLLING AVERAGE. | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The permittee shall maintain a minimum overall thermal efficiency of 60% on a 12â€“month rolling average basis, calculated monthly.
*TX-0638 | MONT BELVIEU COMPLEX | ENTERPRISE PRODUCTS OPERATING LLC | CHAMBERS | TX | 77580 | USA | TERRY HURLBURT | 713-381-6595 | SNOLAN@EPROD.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | PSD-TX-1286-GHG | 1321 | 325110 |  | 06/06/2012 &nbsp;ACT | 10/12/2012 &nbsp;ACT | 2013-10-25 | 2015-03-16 | D |  | the facility will add two new natural gas liquids (NGL) fractionation (Eagleford Fractionation) units and a deisobutanizer (DIB) unit at the Enterprise Mont Belvieu Complex in Mont Belvieu, Texas. The Eagleford Fractionation units will be capable of separating an NGL feed into separate ethane, propane, butane, and gasoline fractions. Each fractionation unit will have a nominal feed capacity of 110,000 barrels per day. The DIB unit will be capable of separating isobutene and normal butane from mixed butane streams. The Eagleford Fractionation and DIB unit will consist of two fractionation unit deethanizer distillation columns, two fractionation unit debutanizer distillation columns, two depropanizer colwnns, two hot oil heaters, two regenerant gas heaters, one flare, one deisobutanizer distillation column, and supporting equipment. |  | Hot Oil Heaters | 12.31 | Natural Gas | 140 | MMBTU/H | 2 Hot Oil Heaters (Combustion Unit). HRI5.001A and HR1 5.001B Each unit has a maximum design heat input rate of 140 MMBTU/HR, and is fired with natural gas. | Carbon Dioxide | Other - Equation C-2a in 40 CFR Part 98 Subpart C. | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | N |  | 72987 | T/YR | 12-MONTH ROLLING BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Minimum Thermal Efficiency of 85%. Permittee shall calculate, on a monthly basis, the amount of C02 emitted from combustion in tons/yr using equation C-2a in 40 CPR Part 98 Subpart C, converted to short tons. The emission rate is for each of the two heaters.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | AMMONIA CATALYST STARTUP HEATER | 12.39 | NATURAL GAS | 106.3 | MMBTU/H | ANNUAL NATURAL GAS USAGE LIMITED TO 20.84 MMCF. | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | NATURAL GAS COMBUSTION ONLY, PROPER DESIGN AND GOOD COMBUSTION PRACTICES | 59.61 | TON/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, VACUUM DEGASSER | 13.29 | NATURAL GAS | 51.2 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATING PRACTICES MINIMUM BOILER EFFICIENCY 75% | 117 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACE, ANNEALING PICKLING LINE | 13.29 | NATURAL GAS | 66 | MMBTU/H | ANNEALING PICKLING LINE FURNACE SN-47; ANNEALING COATING LINE FURNACE , SN 51; | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATING PRACTICES | 117 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILERS SN-26 AND 27, GALVANIZING LINE | 13.31 | NATURAL GAS | 24.5 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATING PRACTICES MINIMUM BOILER EFFICIENCY 75% | 117 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATING PRACTICES | 117 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER EU-002 | 13.31 | NATURAL GAS | 70 | MMBTU/HR |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD COMBUSTION PRACTICES AND THE USE OF INLET AIR CONTROL SENSORS THAT LIMIT EXCESS AIR | 8184 | LB/H | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 200 | H/YR |  | 0 |  |  | 0 | 0 | N | 2016 | SHALL COMBUST NATURAL GAS
*TX-0638 | MONT BELVIEU COMPLEX | ENTERPRISE PRODUCTS OPERATING LLC | CHAMBERS | TX | 77580 | USA | TERRY HURLBURT | 713-381-6595 | SNOLAN@EPROD.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | PSD-TX-1286-GHG | 1321 | 325110 |  | 06/06/2012 &nbsp;ACT | 10/12/2012 &nbsp;ACT | 2013-10-25 | 2015-03-16 | D |  | the facility will add two new natural gas liquids (NGL) fractionation (Eagleford Fractionation) units and a deisobutanizer (DIB) unit at the Enterprise Mont Belvieu Complex in Mont Belvieu, Texas. The Eagleford Fractionation units will be capable of separating an NGL feed into separate ethane, propane, butane, and gasoline fractions. Each fractionation unit will have a nominal feed capacity of 110,000 barrels per day. The DIB unit will be capable of separating isobutene and normal butane from mixed butane streams. The Eagleford Fractionation and DIB unit will consist of two fractionation unit deethanizer distillation columns, two fractionation unit debutanizer distillation columns, two depropanizer colwnns, two hot oil heaters, two regenerant gas heaters, one flare, one deisobutanizer distillation column, and supporting equipment. |  | 2 Regenerant Heaters | 15.11 |  | 28.8 |  | 2 Regenerant Heaters (Combustion Units). Each unit has a maximum design beat input rate of28.5 MMBTU/HR and fired with natural gas, tired with natural gas. HR15.002A and HR15.002B. | Carbon Dioxide | Other - equation C-2a in 40 CPR Part 98 Subpart C | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | N |  | 14858 | T/YR | 12-MONTH ROLLING BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Minimum Thermal Efficiency of 85%. The emission rate is for each of the two regenerant heaters.
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Emergency Generator | 17.11 | diesel fuel | 142 | GAL/H | rated @ 2,000 KW | Carbon Dioxide | EPA/OAR Mthd 3A | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | good combustion practices | 1.55 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY GENERATOR | 17.11 | NO. 2 FUEL OIL | 4690 | B-HP | ANNUAL HOURS OF OPERATION NOT TO EXCEED 200 HOURS. | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD COMBUSTION PRACTICES | 526.39 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | EMERGENCY GENERATORS (EU014A AND EU-014B) | 17.11 | DISTILLATE OIL | 3600 | HP EACH |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD COMBUSTION PRACTICES | 1044 | TON/12 CONSEC. MONTH | EACH | BACT-PSD |  | N | 0 |  | 500 | H/YR EACH |  | 0 |  |  | 0 | 0 | N | 2016
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Carbon Dioxide | EPA/OAR Mthd 3A | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | good combustion practices | 1.55 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD COMBUSTION PRACTICES | 527.4 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | SMALL HEATERS AND DRYERS SN-05 THROUGH 19 | 17.23 | NATURAL GAS | 0 |  | RH VESSEL PREHEATER STATION, VESSEL TOP PART DRYER, RH VESSEL NOZZLE DRYER RH DEGASSER BURNER/LANCE LADLE PREHEATERS LADLE DRYOUT STATION VERTICAL LADLE HOLDING STATION TUNDISH PREHEATERS #1 THROUGH #4 | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATING PRACTICES | 117 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT AMMONIA VENT FLARE | 19.31 | NATURAL GAS | 0.26 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD COMBUSTION PRACTICE | 117 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT PROCESS SSM FLARE | 19.31 | NATURAL GAS | 0.05 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD COMBUSTION PRACTICE | 117 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA STORAGE FLARE | 19.31 | NATURAL GAS | 0.05 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD AND EFFICIENT OPERATING PRACTICES | 117 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Ammonia Flare | 19.31 | natural gas | 0.4 | MMBTU/H | There are four (4) natural gas pilots | Carbon Dioxide | EPA/OAR Mthd 3A | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | work practice/good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | There is no numeric emission limit in the permit.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | FRONT END PROCESS FLARE | 19.31 | NATURAL GAS PILOT | 0.25 | MMBTU/H | HEAT INPUT IS FOR NATURAL GAS PILOT ONLY. SSM EMISSIONS ARE CONTROLLED BY THE FLARE AND ARE LIMITED TO 336 HOURS OF VENTING PER YEAR. | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 116.89 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 511.8 | TON/H, SSM VENTING | 3-HR AVERAGE | 0 |  |  | 0 | 0 | N |  | SSM VENTING LIMITED TO 336 HOURS PER YEAR.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | BACK END AMMONIA FLARE | 19.31 | NATURAL GAS | 0.25 | MMBTU/H | HEAT INPUT IS FOR PILOT ONLY. SSM EMISSIONS ARE CONTROLLED BY THE FLARE AND ARE LIMITED TO 336 HR/YR. | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 116.89 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 127.12 | TON/H, SSM VENTING | 3-HR AVERAGE | 0 |  |  | 0 | 0 | N |  | SSM VENTING LIMITED TO 336 HR PER YEAR.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | AMMONIA STORAGE FLARE | 19.31 | NATURAL GAS | 0.13 | MMBTU/H | HEAT INPUT IS FOR PILOT ONLY. SSM EVENTS HAVE SEPARATE LIMITS. SSM VENTING IS LIMITED TO 168 HOURS PER YEAR. | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 52.02 | LB/H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | UAN PLANT VENT FLARE | 19.31 |  | 0.19 | MMBTU/H | HEAT INPUT IS FOR NATUAL GAS PILOT. SSM EMISSIONS HAVE SEPARATE LIMITS. SSM VENTING LIMITED TO 336 HOURS PER YEAR. | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 116.89 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 5.59 | TON/H, SSM VENTING | 3-HR AVERAGE | 0 |  |  | 0 | 0 | N |  | SSM VENTING LIMITED TO 336 HR PER YEAR.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | AMMONIA STORAGE FLARE (EU-016) | 19.39 | NATURAL GAS | 1.1 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | N |  | 563 | TON/12 CONSEC. MONTH |  | BACT-PSD |  | N | 0 |  | 168 | H/12 CONSEC. MONTH | COMPLIANCE DETERMINED AT END OF EA MONTH | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS USED SHALL BE NATURAL GAS LIMIT 4: COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUTDOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ROOT CAUSE ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DUING ANY 2 CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMOCOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FRONT END FLARE EU-017 | 19.39 | NATURAL GAS | 1.12 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | N |  | 116.89 | LB/MMBTU | NORMAL OPS. 3 HR AVG | BACT-PSD |  | N | 0 |  | 512.2 | TON/H | VENTING OPS., 3 HR AVG. | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS USED SHALL BE NATURAL GAS LIMIT 4: COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUTDOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ROOT CAUSE ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DUING ANY 2 CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMOCOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE. LIMIT 6: SHALL NOT EXCEED 336 HOURS PER TWELVE CONSECUTIVE MONTH PERIOD WITH COMPLIANCE DETERMINED AT THE END OF EACH MONTH.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | BACK END FLARE (EU-018) | 19.39 | NATURAL GAS | 1.12 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | N |  | 116.89 | LB/MMBTU | NORMAL OPS. 3 HR AVG | BACT-PSD |  | N | 0 |  | 573 | TON/12 CONSEC. MONTH |  | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS USED SHALL BE NATURAL GAS LIMIT 4: COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUTDOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ROOT CAUSE ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DUING ANY 2 CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMOCOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE. LIMIT 6: SHALL NOT EXCEED 336 HOURS PER 12 CONSECUTIVE MONTH PERIOD WITH COMPLIANCE DETERMINED AT END OF EACH MONTH.
*TX-0638 | MONT BELVIEU COMPLEX | ENTERPRISE PRODUCTS OPERATING LLC | CHAMBERS | TX | 77580 | USA | TERRY HURLBURT | 713-381-6595 | SNOLAN@EPROD.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | PSD-TX-1286-GHG | 1321 | 325110 |  | 06/06/2012 &nbsp;ACT | 10/12/2012 &nbsp;ACT | 2013-10-25 | 2015-03-16 | D |  | the facility will add two new natural gas liquids (NGL) fractionation (Eagleford Fractionation) units and a deisobutanizer (DIB) unit at the Enterprise Mont Belvieu Complex in Mont Belvieu, Texas. The Eagleford Fractionation units will be capable of separating an NGL feed into separate ethane, propane, butane, and gasoline fractions. Each fractionation unit will have a nominal feed capacity of 110,000 barrels per day. The DIB unit will be capable of separating isobutene and normal butane from mixed butane streams. The Eagleford Fractionation and DIB unit will consist of two fractionation unit deethanizer distillation columns, two fractionation unit debutanizer distillation columns, two depropanizer colwnns, two hot oil heaters, two regenerant gas heaters, one flare, one deisobutanizer distillation column, and supporting equipment. |  | Flare | 19.39 |  | 0 |  | Flare, EPA: SK25.001 | Carbon Dioxide | Other - equation C-2a in 40 CPR Part 98 Subpart C | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | N |  | 62494 | T/PY | 12-MONTH ROLLING BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Use Good Combustion Practices
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EMERGENCY GENERATOR SN-62 | 19.8 | DIESEL | 625 | HP |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD COMBUSTION PRACTICES | 163 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Steam Methane Reformer | 50.002 | NATURAL GAS | 10 | MMSCFH | Steam Methane Reformer, equipped with low NOx burners, SCR, and CO oxidation catalyst | Carbon Dioxide | Other - CEMS | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | N |  | 0.23 | T/T OF H2 | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 418562 | T/YR | 12-MONTH ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | Steam Methane Reformer, equipped with low NOx burners, SCR, and CO oxidation catalyst
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT PRIMARY REFORMER | 61.012 | NATURAL GAS | 1400 | T/D AMMONIA | 824 MMBTU/HR | Carbon Dioxide | EPA/OAR Mthd 3A | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATING PRACTICES | 117 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | PERIODIC STACK TESTING TO VERIFY COMPLIANCE
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT CO2 REGENERATOR | 61.012 |  | 1400 | T/D AMMONIA PRODUCTION |  | Carbon Dioxide | EPA/OAR Mthd 3A | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD AND EFFICIENT OPERATING PRACTICES | 146262.6 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD |  | N | 0 | N | 640669.2 | T/YR | ROLLING 12 MONTH AVERAGE | 2507.5 | LB/TON | ROLLING 3 HOUR AVERAGE | 0 | 0 | N |  | PERIODIC STACK TESTING TO VERIFY COMPLIANCE
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Primary Reformer | 61.012 | natural gas | 1.13 | million cubic feet/h |  | Carbon Dioxide | EPA/OAR Mthd 3A | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | good combustion practices | 117 | LB/MMBTU | ROLLING 30 DAY AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | CO2 Regenerator | 61.012 |  | 3012 | metric tons/day |  | Carbon Dioxide | EPA/OAR Mthd 3A | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | good operational practices | 1.26 | TONS/TON OF AMMONIA | ROLLING 30 DAY AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Urea Ammonia Nitrate (UAN) Mixing Tank | 61.012 |  | 0 |  | The maximum capacity of the tank is 5,400 metric tons and it has an Acid Scrubber to control ammonia. | Carbon Dioxide | EPA/OAR Mthd 3A | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | good operational practices | 1.1 | LB/H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Urea Synthesis | 61.012 |  | 2500 | metric tons/day | There is an Acid Scrubber for ammonia control | Carbon Dioxide | EPA/OAR Mthd 3A | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | good operational practices | 165.4 | LB/H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | PRIMARY REFORMER | 61.012 | NATURAL GAS | 1006.4 | MMBTU/H | NOX CEMS | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD COMBUSTION PRACTICES; PROPER DESIGN: AIR INLET CONTROLS, AND FLUE GAS HEAT RECOVERY. | 59.61 | TONS/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | MUST ACHIEVE A THERMAL EFFICIENCY OF 90% BASED ON THE HIGHER HEATING VALUE CO2 EMISSIONS SHALL NOT EXCEED 515,246 TONS PER YEAR.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | CO2 PURIFICATION PROCESS | 61.012 |  | 3570 | TON CO2 PER DAY | AMMONIA PRODUCTION LIMITED TO 1,022,000 TONS PER YEAR. | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATIONAL PRACTICES | 1.275 | TON CO2/TON AMMONIA | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | TWO (2) AMMONIUM NITRATE UNITS | 61.012 |  | 798 | TON AN PER DAY, EACH | UAN PRODUCTION IS LIMITED TO 1,314,000 TONS PER YEAR. | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATIONAL PRACTICES | 132.31 | LB/TON UAN | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | UREA SYNTHESIS PLANT (EU-006) | 61.012 |  | 2640 | METRIC TON/DAY |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATIONAL PRACTICES | 387 | T/YR |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N | 2016
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | UREA AMMONIUM NITRATE PLANT (EU-007) | 61.012 |  | 5160 | METRIC TON/DAY |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATIONAL PRACTICES AND EFFICIENT DESIGN | 1173 | TONS/12 MONTH | ROLLING AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N | 2016
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT CONDENSATE STEAM STRIPPER | 61.999 |  | 1400 | T/D AMMONIA PRODUCTION |  | Carbon Dioxide | EPA/OAR Mthd 3A | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD AND EFFICIENT OPERATING PRACTICES | 396.64 | LB/H | ROLLING 24 HOUR AVERAGE | BACT-PSD |  | N | 0 | N | 6.8 | LB/TON | ROLLING 24 HOUR AVERAGE | 0 |  |  | 0 | 0 | N |  | PERIODIC STACK TESTING TO VERIFY COMPLIANCE
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | RH DEGASSER | 81.29 | NATURAL GAS | 0 |  |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATING PRACTICES | 117 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-39, ANNEALING | 81.29 | NATURAL GAS | 98.25 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATING PRACTICES | 117 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | ANNEALING COATING LINE FURNACE SECTION | 81.29 | NATURAL GAS | 50 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATING PRACTICES | 117 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACE, SN-53, ANNEALING COATING LINE DRYING | 81.29 | NATURAL GAS | 38 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATING PRACTICES | 117 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | DRYERS, MGO COATING LINE | 81.29 | NATURAL GAS | 38 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATING PRACTICES | 117 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-58 AND 60, FINAL ANNEALING AND COATING LINE | 81.29 | NATURAL GAS | 32 | MMBTU/H |  | Carbon Dioxide | Unspecified | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | P | GOOD OPERATING PRACTICES | 117 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
DE-0025 | DE CITY REFINING COMPANY, LLC | DE CITY REFINING COMPANY, LLC | NEW CASTLE | DE | 19706 | USA | HEATHER CHELPATY | (302) 834-6488 |  | 3 | DE001 | DELAWARE DEPT OF NATURAL RES & ENV CTRL | MR. PAUL FOSTER | (302)323-4542 | PAUL.FOSTER@STATE.DE.US | Ravi Rangan | PERMIT: APC-2015/0058-C(NSPS) | 2911 | 324110 | 110001148598 | 01/15/2015 &nbsp;ACT | 07/13/2015 &nbsp;ACT | 2015-11-19 | 2016-07-06 | B |  | Oil Refinery |  | Steam-Methane Reformer with Pressure Swing Adsorption System | 12.31 | NG | 372 | MMBTU/H |  | Carbon Dioxide | Other - Record Keeping and Monitoring | (Acid Gasses/Mist,Greenhouse Gasses (GHG),InOrganic Compounds) | 124-38-9 | N |  | 33.2 | TONS CO2/MMDSCF H2 |  | OTHER CASE-BY-CASE | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Three (3) Package Boilers | 12.31 | Natural Gas | 243 | MMBTU/H | Three (3) New Natural Gas-Fired 243 MMBtu/hr Package Boilers | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 59.61 | TONS/MMCF | 3-HR AVG | BACT-PSD |  | U | 0 | U | 376500 | TONS/YEAR | COMBINED | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Startup Heater | 12.31 | Natural Gas | 101 | MMBTU/H | Natural Gas-Fired 101 MMBtu/hr Startup Heater. Installed in 1976. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Limited Use (200 hr/yr) | 59.61 | TONS/MMCF |  | BACT-PSD |  | U | 0 | U | 1200 | TONS/YEAR |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT START-UP HEATER | 12.31 | NATURAL GAS | 38 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | GOOD OPERATING PRACTICES | 1115.31 | T/YR | ROLLING 12 MONTH AVERAGE | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | START-UP BOILER | 12.31 | NATURAL GAS | 240 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | GOOD OPERATING PRACTICES | 123411 | T/YR | ROLLING 12 MONTH AVERAGE | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 110 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | ANNUAL BOILER TUNE-UPS | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Startup Heater | 12.31 | Natural gas | 110.12 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Other - recordkeeping | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 638 | TONS/YR | ROLLING 12 MONTH TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Startup Heater | 12.31 | natural gas | 104 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 871 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0260 | GEISMAR ETHYLENE PLANT | WILLIAMS OLEFINS, LLC | ASCENSION | LA | 70734 | USA | DOUG BADON | 225-642-2114 | DOUG.BADON@WILLIAMS.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | dan nguyen (225-219-3181) | PSD-LA-759 | 2869 | 325110 | 110000746337 | 12/13/2011 &nbsp;ACT | 04/11/2012 &nbsp;ACT | 2012-05-08 | 2012-10-16 | B |  | Project to install 2 cracking furnaces at the Ethylene Plant to increase production from 1.4 to 1.95 billion lbs/yr | Complete application date = Administrative Complete date | Cracking Furnaces 95 and 96 | 12.31 | natural gas | 180 | MMBTU/H | (each) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | 1) low-emitting feedstocks, 2) energy efficient equipment, 3) process design improvement, 4) lew-emitting and low- carbon fuel (>25 vol% hydrogen, annual ave.) | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0271 | PLAQUEMINE NGL FRACTIONATION PLANT | CROSSTEX PROCESSING SERVICES, LLC | IBERVILLE | LA | 70764 | USA | BLAKE PHILLIPS | (469) 308-6225 | EHSDEPT@CROSSTEXENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Pemit writer: Doug McCurry, (225) 219-3417 | PSD-LA-771 | 1321 | 211112 | 110055592345 | 11/07/2012 &nbsp;ACT | 05/24/2013 &nbsp;ACT | 2013-10-10 | 2016-05-04 | A |  | Facility fractionates inlet natural gas liquids into constituent product streams for sale. |  | Heat Medium Oil (HMO) Heaters (HMO-01 &amp; HMO-02) | 12.31 | Natural gas | 177 | MMBTU/H | Natural gas: 175 MM Btu/hr Process gas: 2 MM Btu/hr | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Improved combustion measures: heater tuning, optimization, and installation of instrumentation and controls; insulation installed according to the heater manufacturerâ€™s specifications; operational monitoring as well as proper maintenance in order to minimize air infiltration. | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Auxiliary boilers | 12.31 | natural gas | 171 | mm btu/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion/operating/maintenance practices and fueled by natural gas | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | boiler A and B (010 and 011) | 12.31 | natural gas/fuel gas | 248 | mm btu/hr (each) |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices and proper operation and maintenance; gaseous fuels; economizers & Insulation; combustion air preheating; condensate return system | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | boiler B-201 | 12.31 | natural gas/fuel gas | 229 | mm btu |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices and proper operation and maintenance; gaseous fuels; economizers & Insulation; combustion air preheating; condensate return system | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUAUXBOILER (Auxiliary Boiler) | 12.31 | natural gas | 182 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 182 MMBTU/H fuel heat input. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures and the use of a low carbon fuel (pipeline quality natural gas). | 93346 | T/YR | 12-MO ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUAUXBOILER (Auxiliary boiler) | 12.31 | Natural gas | 182 | MMBTU/H | A natural gas fired auxiliary boiler, rated at 182 MMBTU/H to provide auxiliary steam when the plant is off-line, used to maintain warm drums on the HRSG and maintain the steam turbine generator seals. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices. | 93346 | T/YR | 12-MO.ROLL. TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CCS is estimated to cost $128 per ton CO2e (annual costs of over $12 million), and terrestrial sequestration is estimated to cost $162 per ton CO2e (annual costs of over $15 million).
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Boiler, Nat Gas Fired | 12.31 | NATURAL GAS | 261 | MMBTU/H | 261 MMBTU/H natrual gas-fired boiler, equipped with low-NOx burners, SCR, and CO catalytic oxidation | Carbon Dioxide Equivalent (CO2e) | Other - calculations | (Greenhouse Gasses (GHG)) | CO2e | N |  | 127981 | T/YR | 12-MONTH ROLLING TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 261 MMBtU/H natural gas-fired boiler, equipped with natural gas-fired boiler, equipped with low-NOx burners, SCR, and CO catalytic oxidation
NM-0052 | ZIA II GAS PLANT | DCP MIDSTREAM L.P. | LEA | NM | 88255 | USA | JENNIFER HANNA | 4326205460 | JHANNA@DCPMIDSTREAM.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Joseph Kimbrell, 505-476-4300, joseph.kimbrell@state.nm.us | PSD-5217 | 1311 | 211111 | 110056438083 | 11/13/2013 &nbsp;ACT | 04/25/2014 &nbsp;ACT | 2015-11-19 | 2016-07-07 | A | https://www.env.nm.gov/aqb/ | Natural Gas Processing plant using cryogenic process and designed to operate at 230 MMscf/day of natural gas. | The permittee submitted an application on 5/13/2015 to revise the permit. Most BACT determinations will not change. | Industrial Sized Boilers/Furnaces &gt;100 mmBtu/hr | 12.31 | Natural gas | 114 | mmBtu/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD | NSPS , SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NY-0112 | WESTROCK-SOLVAY LLC | WESTROCK-SOLVAY LLC | ONONDAGA | NY | 13204-1035 | USA |  | 315-484-9050 |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 7 315-426-7400 | 7-3132-00055/00037 | 2631 | 322213 | 110009824547 | 11/02/2012 &nbsp;ACT | 11/02/2012 &nbsp;ACT | 2017-09-11 | 2017-09-28 | B | http://www.dec.ny.gov/chemical/32249.html | WestRock-Solvay LLC is a linerboard and corrugated medium facility utilizing three paper machines capable of producing a variety of linerboard and corrugated medium products. The facility also operates a wastewater treatment facility to treat the effluent from the paper making process and plans to add boilers for steam supply with this application. Up to three (3) permanent, large package boilers (&lt; 250 mmBtu/hr) capable of firing natural gas, No. 2 Fuel Oil (ULSD), or Biogas. In additionally, up to two (2) back-up medium size package boilers (&lt; 100 mmBtu/hr) capable of firing natural gas and No. 2 fuel Oil (ULSD) as a back-up. Total annual oil use for all boilers shall not exceed 164,640 mmBtu/yr (figure based on 336 hrs/yr x 490 mmBtu/hr). | State Facility Permit | Boilers - NG | 12.31 | natural gas | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of low CO2 emitting fuels (primary natural gas with limited ultra low sulfur diesel) and boiler design efficiency measures to achieve not greater than 1.3 MMBTU/MLB (million British thermal units per thousand pounds of steam) from each boiler on rolling 12-month basis, or per the final boiler manufactureâ€™s specification. | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | MR. RANDY THOMPSON | (615) 532-6825 | randall.thompson@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000370535 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Two Natural Gas-Fired Auxiliary Boilers | 12.31 | Natural Gas | 450 | MMBtu/hr | Two 450 MMBtu/hr natural gas-fired auxiliary boilers will provide steam generation during threshold transitional periods and during malfunction events when the CT and HRSG are not able to operate. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Efficient design (including insulation to reduce ambient heat loss), good combustion practices, good operating and maintenance practices. | 117 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0638 | MONT BELVIEU COMPLEX | ENTERPRISE PRODUCTS OPERATING LLC | CHAMBERS | TX | 77580 | USA | TERRY HURLBURT | 713-381-6595 | SNOLAN@EPROD.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | PSD-TX-1286-GHG | 1321 | 325110 |  | 06/06/2012 &nbsp;ACT | 10/12/2012 &nbsp;ACT | 2013-10-25 | 2015-03-16 | D |  | the facility will add two new natural gas liquids (NGL) fractionation (Eagleford Fractionation) units and a deisobutanizer (DIB) unit at the Enterprise Mont Belvieu Complex in Mont Belvieu, Texas. The Eagleford Fractionation units will be capable of separating an NGL feed into separate ethane, propane, butane, and gasoline fractions. Each fractionation unit will have a nominal feed capacity of 110,000 barrels per day. The DIB unit will be capable of separating isobutene and normal butane from mixed butane streams. The Eagleford Fractionation and DIB unit will consist of two fractionation unit deethanizer distillation columns, two fractionation unit debutanizer distillation columns, two depropanizer colwnns, two hot oil heaters, two regenerant gas heaters, one flare, one deisobutanizer distillation column, and supporting equipment. |  | Hot Oil Heaters | 12.31 | Natural Gas | 140 | MMBTU/H | 2 Hot Oil Heaters (Combustion Unit). HRI5.001A and HR1 5.001B Each unit has a maximum design heat input rate of 140 MMBTU/HR, and is fired with natural gas. | Carbon Dioxide Equivalent (CO2e) | Other - Part 98, Subpart A, Table A-1 | (Greenhouse Gasses (GHG)) | CO2e | N |  | 73058 | T/YR | 12-MONTH ROLLING BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Permittee shall calculate the CO2e emissions on a 12-month rolling basis, based on the procedures and Global Warming Potentials (GWP) contained in Greenhouse Gas Regulations, 40 CFR Part 98, Subpart A, Table A-1, as published on October 30, 2009 (74 FR 56395). The emission rate is for each of the two heaters.
TX-0766 | GOLDEN PASS LNG EXPORT TERMINAL | GOLDEN PASS PRODUCTS, LLC | JEFFERSON | TX |  | USA | BOB TOMLINSON | 713-860-6348 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 116055, PSDTX1386, GHGPSDTX100 | 4922 | 486210 | UNKNOWN | 04/03/2015 &nbsp;ACT | 09/11/2015 &nbsp;ACT | 2015-09-21 | 2016-07-06 | B |  | Liquefied natural gas (LNG) export terminal. |  | Auxiliary Boiler | 12.31 | natural gas | 240 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Equipment specifications & work practices - Good combustion practices and use of low carbon fuel | 1440 | HR/YR |  | BACT-PSD |  | N | 77 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0812 | CRUDE OIL PROCESSING FACILITY | GRAVITY MIDSTREAM CORPUS CHRISTI LLC | NUECES | TX |  | USA | ANTONIO MARTINEZ | 361-537-1782 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, 512-239-1284, jesse.lovegren@tceq.texas.gov | 9342A, 9343A, PSDTX963M1, GHGP | 2911 | 324110 | Not Found | 09/23/2016 &nbsp;ACT | 10/31/2016 &nbsp;ACT | 2016-10-06 | 2017-11-16 | D |  | Marine Terminal and Condensate Splitter |  | Industrial Boilers and Furnaces (Natural gas fired) | 12.31 | natural gas | 104 | MMBTU/H | Direct-fired process heater | Carbon Dioxide Equivalent (CO2e) | Other - 40 CFR 98.34(a) | (Greenhouse Gasses (GHG)) | CO2e | P | An automated air-fuel controller shall be used to ensure a minimum net thermal efficiency of 80%. | 54800 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0813 | ODESSA PETROCHEMICAL PLANT | REXTAC, LLC | ECTOR | TX |  | USA | STEVE MCHANEY | 432-332-0058 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, 512-239-1541, joseph.janecka@tceq.texas.gov | 16963, PSDTX1478, GHGPSDTX148 | 2821 | 325211 | Not Found | 09/23/2016 &nbsp;ACT | 11/22/2016 &nbsp;ACT | 2016-11-30 | 2017-11-16 | D |  | Petrochemical Manufacturing Facility |  | Boilers | 12.31 | natural gas | 223 | MMBTU/H | 2 boilers | Carbon Dioxide Equivalent (CO2e) | Other - 40 CFR 98.34(a) | (Greenhouse Gasses (GHG)) | CO2e | P | Minimum thermal design efficiency of 75 percent | 63796 | T/YR |  | BACT-PSD | MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | MACT DDDDD
TX-0814 | AMMONIA AND UREA PLANT | AGRIUM US, INC | HUTCHINSON | TX |  | USA | JOSH REGAN | (806) 468-0605 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ramiro Cruz, (512)239-1302, Ramiro.Cruz@tceq.texas.gov | 19778 AND GHGPSDTX155 | 2873 | 325311 | Not Found | 11/04/2016 &nbsp;ACT | 01/05/2017 &nbsp;ACT | 2017-01-17 | 2017-11-16 | C |  | Anhydrous Ammonia and Urea Manufacturing Plant |  | Package Boiler 1 | 12.31 | NATURAL GAS | 0 | 240 MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Agrium uses good engineering practices to minimize CO2 e emissions. | 123059 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0827 | PRAXAIR CLEAR LAKE PLANT | PRAXAIR INC | HARRIS | TX |  | USA | TODD DUNN | 281-203-3606 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 | 144239, PSDTX1512, GHGPSDTX164 | 2813 | 325120 | Not FOUND | 08/22/2017 &nbsp;ACT | 10/19/2017 &nbsp;ACT | 2017-10-19 | 2017-11-02 | A |  | Hydrogen-Carbon Monoxide plant using an auto-thermal reformer to produce hydrogen and carbon monoxide. |  | HyCO Heater | 12.31 | natural gas | 180 | MM BTU/HR |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Annual tune-ups. Emissions are based on a plantwide grouped limit. | 1148305 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0830 | PRAXIAR CLEAR LAKE | PRAXIAR INC | HARRIS | TX |  | USA | TODD DUNN | 281-203-3606 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 144239, PSDTX1512, AND GHGPSDT | 2813 | 325120 | not found | 09/22/2017 &nbsp;ACT | 10/20/2017 &nbsp;ACT | 2018-04-25 | 2018-05-02 | A |  | HYCO USING AUTO-THERMAL REFORMER |  | HYCO HEATER | 12.31 | NATURAL GAS | 180 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Annual tune-ups. Emissions are based on a plantwide grouped limit | 1148305 | TON/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WI-0260 | EXPERA SPECIALTY SOLUTIONS | EXPERA SPECIALTY SOLUTIONS | BROWN | WI | 54115-2220 | USA | KENT HUBBARD | (920) 337-1299 | KENT.HUBBARD@EXPERASPECIALTY.COM | 5 | WI001 | WISCONSIN DEPT OF NATURAL RESOURCES; AIR MGMT. PROGRAM | MS. KRISTIN HART | (608)266-6876 | kristin.hart@wisconsin.gov |  | 12-DMM-186 | 2621 | 322121 | 110000420884 | 10/22/2012 &nbsp;ACT | 11/30/2012 &nbsp;ACT | 2016-01-05 | 2016-07-06 | B | http://dnr.wi.gov/cias/am/amexternal/AM_DownloadObject.aspx?id=320248 | Paper Making Facility |  | B25 - B&amp;W Natural Gas-Fired Boiler | 12.31 | Natural Gas | 217.11 | MMBtu per hour |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | (a) The use of natural gas; (b) The boiler heat conversion efficiency shall be 73% or greater, as determined by a 12-month average; (c) Emissions of carbon dioxide (CO2) may not exceed 160 pounds of CO2 per 1,000 pounds of steam produced, as determined by a 12-month average; and (d) The use of low-NOx burners.
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Auxiliary Boiler | 12.31 | Natural Gas | 100 | mmBtu/hr | Limited to 2,000 hours of operation per year. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of Natural Gas | 12081 | LB/H |  | BACT-PSD |  | U | 0 | U | 120.81 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Waste Heat Boilers | 13.31 | Natural Gas | 50 | MMBTU/H | Five (5) Natural Gas-Fired 50 MMBtu/hr Waste Heat Boilers. Installed in 1986. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 59.61 | TONS/MMCF | 3-HR AVG | BACT-PSD |  | U | 0 | U | 131405 | TONS/YEAR | COMBINED | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, PICKLE LINE | 13.31 | NATURAL GAS | 67 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | GOOD OPERATING PRACTICES MINIMUM BOILER EFFICIENCY 75% | 117 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0271 | PLAQUEMINE NGL FRACTIONATION PLANT | CROSSTEX PROCESSING SERVICES, LLC | IBERVILLE | LA | 70764 | USA | BLAKE PHILLIPS | (469) 308-6225 | EHSDEPT@CROSSTEXENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Pemit writer: Doug McCurry, (225) 219-3417 | PSD-LA-771 | 1321 | 211112 | 110055592345 | 11/07/2012 &nbsp;ACT | 05/24/2013 &nbsp;ACT | 2013-10-10 | 2016-05-04 | A |  | Facility fractionates inlet natural gas liquids into constituent product streams for sale. |  | Mol Sieve Dehy Regen Heater (H-01) | 13.31 | Natural gas | 30 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Improved combustion measures: heater tuning, optimization, and installation of instrumentation and controls; insulation installed according to the heater manufacturerâ€™s specifications; operational monitoring as well as proper maintenance in order to minimize air infiltration. | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Regenerative Heaters | 13.31 | natural gas | 7.37 | mm btu/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion/operating/maintenance practices and fueled by natural gas | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGFUELHTR (Two fuel pre-heaters identified as EUFUELHTR1 &amp; EUFUELHTR2) | 13.31 | Natural gas | 27 | MMBTU/H | Two natural gas fired dew point heaters for warming the natural gas fuel (EUFUELHTR1 & EUFUELHTR2 in flexible group FGFUELHTR). The total combined heat input during operation shall not exceed 27 MMBTU/H (each) as well. The CO2e limit is for both units combined; however the other limits are per unit. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures and the use of a low carbon fuel (pipeline quality natural gas). | 13848 | T/YR | 12-MO ROLLING TIME PERIOD; COMBINED LIMI | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The CO2e limit is for both units combined.
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Regeneration Heater, methanol to gasoline | 13.31 | NATURAL GAS | 13 | MMBTU/H | 13 MMBTU/H methanol-to-gasoline regeneration heater, equipped with low-NOx burner | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | good combustion practices (continuous oxygen trim or annual tune-ups) 13 MMBTU/H methanol-to-gasoline regeneration heater, equipped with low-NOx burner
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Reactor Heater, 5 | 13.31 | NATURAL GAS | 12 | MMBTU/H | Five 12 MMBTU/H reactor heaters, equipped with low-NOx burners | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | good combustion practices (continuous oxygen trim or annual tune-ups) Five 12 MMBTU/H reactor heaters, equipped with low-NOx burners
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Dryer Regenerator Heater - 005 | 13.39 | process fuel gas | 29 | mm btu/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices and proper operation and maintenance; gaseous fuels; Insulation | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Gas Turbines (8 units) | 15.11 | natural gas | 333 | mm btu/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion/operating/maintenance practices and fueled by natural gas; use intake air chiller | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0638 | MONT BELVIEU COMPLEX | ENTERPRISE PRODUCTS OPERATING LLC | CHAMBERS | TX | 77580 | USA | TERRY HURLBURT | 713-381-6595 | SNOLAN@EPROD.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | PSD-TX-1286-GHG | 1321 | 325110 |  | 06/06/2012 &nbsp;ACT | 10/12/2012 &nbsp;ACT | 2013-10-25 | 2015-03-16 | D |  | the facility will add two new natural gas liquids (NGL) fractionation (Eagleford Fractionation) units and a deisobutanizer (DIB) unit at the Enterprise Mont Belvieu Complex in Mont Belvieu, Texas. The Eagleford Fractionation units will be capable of separating an NGL feed into separate ethane, propane, butane, and gasoline fractions. Each fractionation unit will have a nominal feed capacity of 110,000 barrels per day. The DIB unit will be capable of separating isobutene and normal butane from mixed butane streams. The Eagleford Fractionation and DIB unit will consist of two fractionation unit deethanizer distillation columns, two fractionation unit debutanizer distillation columns, two depropanizer colwnns, two hot oil heaters, two regenerant gas heaters, one flare, one deisobutanizer distillation column, and supporting equipment. |  | 2 Regenerant Heaters | 15.11 |  | 28.8 |  | 2 Regenerant Heaters (Combustion Units). Each unit has a maximum design beat input rate of28.5 MMBTU/HR and fired with natural gas, tired with natural gas. HR15.002A and HR15.002B. | Carbon Dioxide Equivalent (CO2e) | Other - Part 98, Subpart A, Table A-1 | (Greenhouse Gasses (GHG)) | CO2e | N |  | 14872 | T/PY | 12-MONTH ROLLING BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission rate is for each of the two regenerant heaters.
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Carbon Dioxide Equivalent (CO2e) | Other - EPA METHOD 3B | (Greenhouse Gasses (GHG)) | CO2e | N |  | 774 | LB/MW-H | 365-DAY ROLLING AVG (FACILITYWIDE) | BACT-PSD |  | U | 0 | U | 7319 | BTU/KW-H | 365-DAY ROLLING AVG (FACILITYWIDE) | 0 |  |  | 0 | 0 | N |  | USE EPA METHOD 3B FOR CO2 EMISSIONS.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures and the use of a low carbon fuel (pipeline quality natural gas). | 2097001 | T/YR | 12-MONTH ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is for EACH CTGHRSG. The proposed permit also contains a 802 lb CO2 per MW-hour (lb/MWh) emission limit that serves as BACT due to energy efficiency, which is equivalent to a net heat rate of 6,855 Btu/kW-hr per 2x1 block and is more stringent than the required NSPS limit of the same units. The amine-based CCS technologies were used since these are generally considered to be the most feasible near-term deployable technology for possible future CO2 removal. CCS is assumed to be about 90 percent effective. Using the lowest capital cost range, the estimated capital cost for CCS for the proposed project is approximately $629,000,000. The cost of a pipeline to transport the CO2 was added to the result to estimate the total capital cost of the CO2 control system. The operating and maintenance and indirect operating costs were estimated to be around $53,000,000. Based on 90 percent CO2 removal and the control being applied to the facility-wide emissions, not just the CTG/HRSG trains, the resulting cost is estimated to be $30/ton and was not considered economically feasible.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures and the use of a low carbon fuel (pipeline quality natural gas). | 992286 | T/YR | 12-MO.ROLL.TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CCS was estimated to cost over $240 per ton of CO2 removed, with an estimated annual cost of over $246 million. Terrestrial sequestration was estimated to cost over $160 per ton of CO2 removed, with an estimated annual cost of over $160 million. Thus, both of these options are ruled out, as they are not economically feasible.
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | Large combustion turbine | 15.21 | Natural Gas | 0 |  | This process entry is for operations with the duct burner. Limits entered are for each turbine. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 1881905 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | MR. RANDY THOMPSON | (615) 532-6825 | randall.thompson@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000370535 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Natural Gas-Fired Combustion Turbine with HRSG | 15.21 | Natural Gas | 1339 | MMBtu/hr | Turbine throughput is 1019.7 MMBtu/hr when burning natural gas and 1083.7 MMBtu/hr when burning No. 2 oil. Duct burner throughput is 319.3 MMBtu/hr. Duct burner firing will occur during natural gas combustion only. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion design and practices | 1800 | LB/MWH | 12-MONTH MOVING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0766 | GOLDEN PASS LNG EXPORT TERMINAL | GOLDEN PASS PRODUCTS, LLC | JEFFERSON | TX |  | USA | BOB TOMLINSON | 713-860-6348 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 116055, PSDTX1386, GHGPSDTX100 | 4922 | 486210 | UNKNOWN | 04/03/2015 &nbsp;ACT | 09/11/2015 &nbsp;ACT | 2015-09-21 | 2016-07-06 | B |  | Liquefied natural gas (LNG) export terminal. |  | Refrigeration Compression Turbines | 15.21 | natural gas | 15.6 | MMtpy | Six GE Frame 7 Turbines at site. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Equipment specifications & work practices - Good combustion practices and use of low carbon fuel | 614533 | TPY |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Combined Cycle Turbine/Duct Burner | 15.21 | Natural Gas | 2419.61 | mmBtu/Hr | This entry is for both of two identical units at the facility. Nominal 197 mW General Electric Frame 7FA.04 Turbine w/ Duct Burner - throughput denotes aggregate heat input of turbine and duct burner (HHV). | Carbon Dioxide Equivalent (CO2e) | Other - Test Method 3A/B (CO2) | (Greenhouse Gasses (GHG)) | CO2e | P | Use of GE Frame 7EA CT Low Carbon Fuel | 272556 | LB/H |  | BACT-PSD |  | U | 0 | U | 792 | LB/MW/H |  | 0 |  |  | 0 | 0 | N |  | CO2e limit is applicable with and without duct firing.
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Natural Gas Fired Combustion Turbines | 16.11 | Natural Gas | 37.6 | MMBTU/H | Five (5) Natural Gas-Fired Solar Combustion Turbines rated at 37.6 MMBtu/hr each. Installed in 1976. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 59.61 | TONS/MMCF | 3-HR AVG | BACT-PSD |  | U | 0 | U | 91500 | TONS/YEAR | COMBINED | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Emergency Generator | 17.11 | diesel fuel | 142 | GAL/H | rated @ 2,000 KW | Carbon Dioxide Equivalent (CO2e) | Other - recordkeeping | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 788.5 | TONS/YR | ROLLING 12 MONTH TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Emergency Generator | 17.11 | distillate fuel oil | 3755 | HP |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 432 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Diesel Engines | 17.11 | Diesel | 0 |  | Water Pumps (2 units) = 355 hp Tank Deluge Pumps (2 units) = 800 hp Generator = 1340 hp | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion/operating/maintenance practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUEMENGINE (Diesel fuel emergency engine) | 17.11 | Diesel Fuel | 22.68 | MMBTU/H | a 2,922 horsepower (HP) (2,179 kilowatts (kW)) diesel fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Restricted to 4 hours/day, except during emergency conditions and stack testing, and 500 hours/year on a 12-month rolling time period basis. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 928 | T/YR | 12-MO. ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0766 | GOLDEN PASS LNG EXPORT TERMINAL | GOLDEN PASS PRODUCTS, LLC | JEFFERSON | TX |  | USA | BOB TOMLINSON | 713-860-6348 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 116055, PSDTX1386, GHGPSDTX100 | 4922 | 486210 | UNKNOWN | 04/03/2015 &nbsp;ACT | 09/11/2015 &nbsp;ACT | 2015-09-21 | 2016-07-06 | B |  | Liquefied natural gas (LNG) export terminal. |  | Emergency Engine Generators | 17.11 | Diesel | 750 | hp | Six diesel engines at site. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Equipment specifications & work practices - Good combustion practices and limited operational hours | 40 | HR/YR |  | BACT-PSD |  | N | 0 | U | 123 | TPY |  | 0 |  |  | 0 | 0 | N
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Emergency Generator | 17.11 | Diesel | 2015.7 | HP | Nominal 1,500 kW. Limited to 100 hours/year. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 2416 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Diesel Fired Well Pump | 17.21 | Diesel | 2.7 | MMBTU/H | 2.7 MMBtu/hr Diesel Fired Well Pump. Installed in 1966. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Limited Operation of 168 hr/yr. | 37.2 | TONS/YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Carbon Dioxide Equivalent (CO2e) | Other - recordkeeping | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 91 | TONS/YR | ROLLING 12 MONTH TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 72 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel Firewater pump engines (6 units) | 17.21 | diesel | 425 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel emergency generator engine - EGEN | 17.21 | diesel | 350 | hp |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices | 13.58 | T/YR | 12 MO. ROLLING TIME PERIOD | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Fire Pump Engine | 17.21 | Diesel | 251 | HP | Limited to 100 Hours/year. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 309 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Gasoline Fired Fire Pump Engine | 17.22 | Gasoline | 2.1 | MMBTU/H | 2.1 MMBtu/hr Gasoline-Fired Fire Pump Engine. Installed in 1978. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Limited Operation of 168 hr/yr. | 27.2 | TONS/YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Three (3) Flares | 19.31 | Natural Gas | 1.25 | MMBTU/H | 1.25 MMBtu/hr Ammonia Tank Flare, 0.4 MMBtu/hr Emergency Flare, and 1.25 MMBtu/hr Small Flare | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Work Practice Requirements and Limited Use (limit venting to 168 hr/yr each during startup, shutdown, and maintenance events) | 59.61 | TONS/MMCF |  | BACT-PSD |  | U | 0 | U | 1500 | TONS/YEAR | COMBINED | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT AMMONIA VENT FLARE | 19.31 | NATURAL GAS | 0.26 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | GOOD COMBUSTION PRACTICE | 719.9 | T/YR | ROLLING 12 MONTH AVERAGE | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT PROCESS SSM FLARE | 19.31 | NATURAL GAS | 0.05 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | GOOD COMBUSTION PRACTICE | 5179.8 | T/YR | ROLLING 12 MONTH AVERAGE | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA STORAGE FLARE | 19.31 | NATURAL GAS | 0.05 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | GOOD AND EFFICIENT OPERATING PRACTICES | 89.99 | T/YR | ROLLING 12 MONTH AVERAGE | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Ammonia Flare | 19.31 | natural gas | 0.4 | MMBTU/H | There are four (4) natural gas pilots | Carbon Dioxide Equivalent (CO2e) | Other - recordkeeping | (Greenhouse Gasses (GHG)) | CO2e | P | work practice/good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | There is no numeric emission limit in the permit.
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Flare No. 1 - 008 | 19.31 | natural gas | 85097 | MM BTU/yr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good management practices, good combustion practices, proper flare design | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Pyrolysis Gasoline Tank Flare - 009 | 19.31 | natural gas | 0.66 | mm btu/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good management practices, good combustion practices, proper flare design | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | vessel evacuation flare - 018 | 19.31 | natural gas | 3.04 | mm btu/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Insulation, Gaseous fuels, good combustion practices, and proper operation and maintenance | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0814 | AMMONIA AND UREA PLANT | AGRIUM US, INC | HUTCHINSON | TX |  | USA | JOSH REGAN | (806) 468-0605 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ramiro Cruz, (512)239-1302, Ramiro.Cruz@tceq.texas.gov | 19778 AND GHGPSDTX155 | 2873 | 325311 | Not Found | 11/04/2016 &nbsp;ACT | 01/05/2017 &nbsp;ACT | 2017-01-17 | 2017-11-16 | C |  | Anhydrous Ammonia and Urea Manufacturing Plant |  | Ammonia Emergency Flare | 19.31 | NATURAL GAS | 0.31 | MMBTU/HR | 2715 MMBTU/YR | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Agrium uses good engineering practices to minimize CO2 e emissions. | 157 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0814 | AMMONIA AND UREA PLANT | AGRIUM US, INC | HUTCHINSON | TX |  | USA | JOSH REGAN | (806) 468-0605 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ramiro Cruz, (512)239-1302, Ramiro.Cruz@tceq.texas.gov | 19778 AND GHGPSDTX155 | 2873 | 325311 | Not Found | 11/04/2016 &nbsp;ACT | 01/05/2017 &nbsp;ACT | 2017-01-17 | 2017-11-16 | C |  | Anhydrous Ammonia and Urea Manufacturing Plant |  | Urea Emergency Flare | 19.31 | NATURAL GAS | 2.76 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good engineering practices to minimize CO2 e emissions. | 1418 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0814 | AMMONIA AND UREA PLANT | AGRIUM US, INC | HUTCHINSON | TX |  | USA | JOSH REGAN | (806) 468-0605 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ramiro Cruz, (512)239-1302, Ramiro.Cruz@tceq.texas.gov | 19778 AND GHGPSDTX155 | 2873 | 325311 | Not Found | 11/04/2016 &nbsp;ACT | 01/05/2017 &nbsp;ACT | 2017-01-17 | 2017-11-16 | C |  | Anhydrous Ammonia and Urea Manufacturing Plant |  | Process Name Urea Emergency Flare (maintenance) | 19.31 | NATURAL GAS | 0 |  | 2,000 kg/event, 36 hrs/event, 4 events/yr | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good engineering practices to minimize CO2 e emissions | 5.9 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NM-0052 | ZIA II GAS PLANT | DCP MIDSTREAM L.P. | LEA | NM | 88255 | USA | JENNIFER HANNA | 4326205460 | JHANNA@DCPMIDSTREAM.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Joseph Kimbrell, 505-476-4300, joseph.kimbrell@state.nm.us | PSD-5217 | 1311 | 211111 | 110056438083 | 11/13/2013 &nbsp;ACT | 04/25/2014 &nbsp;ACT | 2015-11-19 | 2016-07-07 | A | https://www.env.nm.gov/aqb/ | Natural Gas Processing plant using cryogenic process and designed to operate at 230 MMscf/day of natural gas. | The permittee submitted an application on 5/13/2015 to revise the permit. Most BACT determinations will not change. | Units FL1 &amp; FL2: Refinery Flares (Inlet Gas Flare &amp; Acid Gas Flare) | 19.33 | natural gas, acid gas | 2.3 | mmBtu/hr | Only for routine or predictable Startup, Shutdown, or Maintenance of units controlled by Flares (Blowdown/Venting, Amine Unit-Acid Gas Injection well maintenance) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | NOx, CO, PM10, PM2.5, SO2 controlled through Good Combustion Practices (GCP), pipeline quality natural gas for pilot; limits on flaring events. VOC & CO2e controlled through GCP, limits on flaring and meet 40 CFR 60.18. | 5626 | PPH |  | BACT-PSD | NSPS , SIP , OPERATING PERMIT | N | 98 | U | 69 | PPH |  | 0 |  |  | 0 | 0 | N |  | The emission limits above represent CO2e from SSM for Units FL1 & FL2. Additional limits for CO2e from pilot & purge are 1331.0 pph from unit FL1 and 1331.0 pph from Unit FL2.
LA-0271 | PLAQUEMINE NGL FRACTIONATION PLANT | CROSSTEX PROCESSING SERVICES, LLC | IBERVILLE | LA | 70764 | USA | BLAKE PHILLIPS | (469) 308-6225 | EHSDEPT@CROSSTEXENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Pemit writer: Doug McCurry, (225) 219-3417 | PSD-LA-771 | 1321 | 211112 | 110055592345 | 11/07/2012 &nbsp;ACT | 05/24/2013 &nbsp;ACT | 2013-10-10 | 2016-05-04 | A |  | Facility fractionates inlet natural gas liquids into constituent product streams for sale. |  | Process Flare (FLARE-01) | 19.39 | Waste gas | 26 | MMBTU/H | Waste gas: 21 MM Btu/hr Amine regenerator overhead gas: 4 MM Btu/hr Natural gas (pilot): 1 MM Btu/hr | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Clean burning fuels, proper design and operation, and good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0271 | PLAQUEMINE NGL FRACTIONATION PLANT | CROSSTEX PROCESSING SERVICES, LLC | IBERVILLE | LA | 70764 | USA | BLAKE PHILLIPS | (469) 308-6225 | EHSDEPT@CROSSTEXENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Pemit writer: Doug McCurry, (225) 219-3417 | PSD-LA-771 | 1321 | 211112 | 110055592345 | 11/07/2012 &nbsp;ACT | 05/24/2013 &nbsp;ACT | 2013-10-10 | 2016-05-04 | A |  | Facility fractionates inlet natural gas liquids into constituent product streams for sale. |  | Emergency Flare (FLARE-02) | 19.39 | Natural gas | 2 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Clean burning fuels, proper design and operation, and good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | flares | 19.39 | natural gas | 7.33 | kg/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion/operating/maintenance practices and fueled by natural gas | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0766 | GOLDEN PASS LNG EXPORT TERMINAL | GOLDEN PASS PRODUCTS, LLC | JEFFERSON | TX |  | USA | BOB TOMLINSON | 713-860-6348 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 116055, PSDTX1386, GHGPSDTX100 | 4922 | 486210 | UNKNOWN | 04/03/2015 &nbsp;ACT | 09/11/2015 &nbsp;ACT | 2015-09-21 | 2016-07-06 | B |  | Liquefied natural gas (LNG) export terminal. |  | Flares | 19.39 | natural gas | 0 |  | One ground flare and one elevated flare at site | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Equipment specifications & work practices- good combustion practices | 0 |  |  | BACT-PSD |  | U | 99 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Designed to meet 40 CFR 60.18
TX-0827 | PRAXAIR CLEAR LAKE PLANT | PRAXAIR INC | HARRIS | TX |  | USA | TODD DUNN | 281-203-3606 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 | 144239, PSDTX1512, GHGPSDTX164 | 2813 | 325120 | Not FOUND | 08/22/2017 &nbsp;ACT | 10/19/2017 &nbsp;ACT | 2017-10-19 | 2017-11-02 | A |  | Hydrogen-Carbon Monoxide plant using an auto-thermal reformer to produce hydrogen and carbon monoxide. |  | HyCO Flare | 19.39 | natural gas | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Meet the design and operating requirements of 40 CFR 60.18. Emissions are based on a plantwide grouped LIMIT. | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emissions included in Grouped limit
*TX-0830 | PRAXIAR CLEAR LAKE | PRAXIAR INC | HARRIS | TX |  | USA | TODD DUNN | 281-203-3606 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 144239, PSDTX1512, AND GHGPSDT | 2813 | 325120 | not found | 09/22/2017 &nbsp;ACT | 10/20/2017 &nbsp;ACT | 2018-04-25 | 2018-05-02 | A |  | HYCO USING AUTO-THERMAL REFORMER |  | HYCO FLARE | 19.39 | NATURAL GAS | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Meet the design and operating requirements of 40 CFR 60.18. Emissions are based on a plantwide grouped limit. | 1148305 | TON/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | AUXILIARY HEATER | 19.6 | NATURAL GAS | 40 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS
TX-0766 | GOLDEN PASS LNG EXPORT TERMINAL | GOLDEN PASS PRODUCTS, LLC | JEFFERSON | TX |  | USA | BOB TOMLINSON | 713-860-6348 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 116055, PSDTX1386, GHGPSDTX100 | 4922 | 486210 | UNKNOWN | 04/03/2015 &nbsp;ACT | 09/11/2015 &nbsp;ACT | 2015-09-21 | 2016-07-06 | B |  | Liquefied natural gas (LNG) export terminal. |  | Thermal Oxidizers | 19.9 | natural gas | 0 |  | Four thermal oxidizers at site. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Equipment specifications & work â€“ good combustion practices | 374114 | TPY |  | BACT-PSD |  | U | 99.5 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0271 | PLAQUEMINE NGL FRACTIONATION PLANT | CROSSTEX PROCESSING SERVICES, LLC | IBERVILLE | LA | 70764 | USA | BLAKE PHILLIPS | (469) 308-6225 | EHSDEPT@CROSSTEXENERGY.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Pemit writer: Doug McCurry, (225) 219-3417 | PSD-LA-771 | 1321 | 211112 | 110055592345 | 11/07/2012 &nbsp;ACT | 05/24/2013 &nbsp;ACT | 2013-10-10 | 2016-05-04 | A |  | Facility fractionates inlet natural gas liquids into constituent product streams for sale. |  | Fugitive Emissions (FUG-01) | 50.002 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Compliance with LDAR programs under 40 CFR 60 Subpart OOOO, LAC 33:III.2111, and LAC 33:III.2122 | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NM-0052 | ZIA II GAS PLANT | DCP MIDSTREAM L.P. | LEA | NM | 88255 | USA | JENNIFER HANNA | 4326205460 | JHANNA@DCPMIDSTREAM.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Joseph Kimbrell, 505-476-4300, joseph.kimbrell@state.nm.us | PSD-5217 | 1311 | 211111 | 110056438083 | 11/13/2013 &nbsp;ACT | 04/25/2014 &nbsp;ACT | 2015-11-19 | 2016-07-07 | A | https://www.env.nm.gov/aqb/ | Natural Gas Processing plant using cryogenic process and designed to operate at 230 MMscf/day of natural gas. | The permittee submitted an application on 5/13/2015 to revise the permit. Most BACT determinations will not change. | Petroleum Refining Seperation Processes (distallation and light ends recovery) | 50.005 | N/A | 230 | MMscf/d | TEG Glycol Dehydrator Still Vent/Flash Tank. No cost information for chosen BACT. Catalytic/Thermal Oxidation not technically feasible. Condenser & vapor combustion device for still vent. Flash tank is recycled to inlet stream closed system. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | Condenser (80% efficiency) & vapor combustion device (98% efficiency) for still vent. Flash tank is recycled to inlet stream closed system. | 0 | TPY |  | BACT-PSD | MACT , SIP , OPERATING PERMIT | U | 80 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Thermal oxidizers (2 units) | 50.008 | natural gas | 21 | mm btu/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion/operating/maintenance practices and fueled by natural gas | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0766 | GOLDEN PASS LNG EXPORT TERMINAL | GOLDEN PASS PRODUCTS, LLC | JEFFERSON | TX |  | USA | BOB TOMLINSON | 713-860-6348 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Erik Hendrickson, (512) 239-1095, Erik.Hendrickson@TCEQ.Texas.gov | 116055, PSDTX1386, GHGPSDTX100 | 4922 | 486210 | UNKNOWN | 04/03/2015 &nbsp;ACT | 09/11/2015 &nbsp;ACT | 2015-09-21 | 2016-07-06 | B |  | Liquefied natural gas (LNG) export terminal. |  | Fugitive Emissions | 50.999 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Work practice â€“leak detection and repair program | 2569 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT PRIMARY REFORMER | 61.012 | NATURAL GAS | 1400 | T/D AMMONIA | 824 MMBTU/HR | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | GOOD OPERATING PRACTICES | 96737.6 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 423714.2 | T/YR | ROLLING 12 MONTH AVERAGE | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT CO2 REGENERATOR | 61.012 |  | 1400 | T/D AMMONIA PRODUCTION |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | GOOD AND EFFICIENT OPERATING PRACTICES | 146262.6 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 640669.2 | T/YR | ROLLING 12 MONTH AVERAGE | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Primary Reformer | 61.012 | natural gas | 1.13 | million cubic feet/h |  | Carbon Dioxide Equivalent (CO2e) | Other - recordkeeping | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 596905 | TONS/YR | ROLLING 12 MONTH TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | CO2 Regenerator | 61.012 |  | 3012 | metric tons/day |  | Carbon Dioxide Equivalent (CO2e) | Other - recordkeeping | (Greenhouse Gasses (GHG)) | CO2e | P | good operational practices | 1211847 | TONS/YR | ROLLING 12 MONTH TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Urea Ammonia Nitrate (UAN) Mixing Tank | 61.012 |  | 0 |  | The maximum capacity of the tank is 5,400 metric tons and it has an Acid Scrubber to control ammonia. | Carbon Dioxide Equivalent (CO2e) | Other - recordkeeping | (Greenhouse Gasses (GHG)) | CO2e | P | good operational practices | 4.92 | TONS/YR | ROLLING 12 MONTH TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Urea Synthesis | 61.012 |  | 2500 | metric tons/day | There is an Acid Scrubber for ammonia control | Carbon Dioxide Equivalent (CO2e) | Other - recordkeeping | (Greenhouse Gasses (GHG)) | CO2e | P | good operational practices | 724.5 | TONS/YR | ROLLING 12 MONTH TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Ammonia Plant, Flares | 61.012 | natural gas | 2789 | tpd |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 25971 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Ammonia Pressure Tanks | 61.012 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | Flare; flare minimization | 479 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Components (valves, flanges, etc.) | 61.012 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | B | LDAR; &lsquo;&lsquo;leakless&lsquo;&lsquo; component | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Integrated Plant GHG Limit | 61.012 | natural gas | 2789 | tpd | bact for ghg is based on emissions from the ammonia plant co2 vent, urea plant co2 vent, reformer furnace and boiler, since all these units are integrated in the production of ammonia. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Variable Limit. E = {(Pu x Ru) + (Pa x Ra)} Ã· (Pu + Pa) Where E = Limit on GHG emissions, as CO2e, tons/ton ammonia produced, annual average, rolled monthly. Pu = Ammonia production sent to the urea plant (tons/year, rolled monthly). Pa = Ammonia production for direct sale (tons/year, rolled monthly), determined as ammonia sent to storage. Ru = 0.92 tons per ton of ammonia sent to the urea plant. Ra = 2.22 tons per ton of ammonia sent to storage.
TX-0814 | AMMONIA AND UREA PLANT | AGRIUM US, INC | HUTCHINSON | TX |  | USA | JOSH REGAN | (806) 468-0605 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ramiro Cruz, (512)239-1302, Ramiro.Cruz@tceq.texas.gov | 19778 AND GHGPSDTX155 | 2873 | 325311 | Not Found | 11/04/2016 &nbsp;ACT | 01/05/2017 &nbsp;ACT | 2017-01-17 | 2017-11-16 | C |  | Anhydrous Ammonia and Urea Manufacturing Plant |  | CO2 Stripper Vent | 61.012 |  | 730000 | T/YR | 730,000 TPY Urea and 702,625 TPY Ammonia Greenhouse gas (GHG) will be controlled by using Carbon dioxide (CO2) as a raw material to produce urea. If the Urea Plant is not operating, the CO2 generated in the ammonia process will be vented to the atmosphere | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Agrium uses good engineering practices to minimize CO2 e emissions, with emissions limited to releasing to the atmosphere the CO2 which cannot be sold. This is BACT for this source. | 843150 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT CONDENSATE STEAM STRIPPER | 61.999 |  | 1400 | T/D AMMONIA PRODUCTION |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | GOOD AND EFFICIENT OPERATING PRACTICES | 396.7 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 1737.4 | T/YR | ROLLING 12 MONTH AVERAGE | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | DM WEATHERLY NITRIC ACID PLANT # 2 | 62.014 |  | 1265 | T/D | 461,725 TON/YR OF 100% HNO3 | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | GOOD OPERATING PRACTICES | 6371.5 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 27911.3 | T/YR | ROLLING 12 MONTH AVERAGE | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Nitric Acid Plant | 62.014 |  | 1905 | metric tons/day |  | Carbon Dioxide Equivalent (CO2e) | Other - recordkeeping | (Greenhouse Gasses (GHG)) | CO2e | A | De-N2O system | 29543 | TONS/YR | ROLLING 12 MONTH TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Ammonia Plant, CO2 Vent | 62.999 | Natural Gas | 1800 | T/D | The CO2 vent, vents excess CO2 from ammonia process. During times when ammonia plant is operating and Urea plant is not operating, all CO2 generated by ammonia plant operations is vented through this vent. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 845486 | TONS/YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | fugitives | 64.002 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good piping design/maintenance/work practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0827 | PRAXAIR CLEAR LAKE PLANT | PRAXAIR INC | HARRIS | TX |  | USA | TODD DUNN | 281-203-3606 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 | 144239, PSDTX1512, GHGPSDTX164 | 2813 | 325120 | Not FOUND | 08/22/2017 &nbsp;ACT | 10/19/2017 &nbsp;ACT | 2017-10-19 | 2017-11-02 | A |  | Hydrogen-Carbon Monoxide plant using an auto-thermal reformer to produce hydrogen and carbon monoxide. |  | HyCO FUGITIVES | 64.002 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emissions included in Grouped limit
*TX-0830 | PRAXIAR CLEAR LAKE | PRAXIAR INC | HARRIS | TX |  | USA | TODD DUNN | 281-203-3606 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 144239, PSDTX1512, AND GHGPSDT | 2813 | 325120 | not found | 09/22/2017 &nbsp;ACT | 10/20/2017 &nbsp;ACT | 2018-04-25 | 2018-05-02 | A |  | HYCO USING AUTO-THERMAL REFORMER |  | HYCO FUGITIVES | 64.002 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Modular Ethylene Cracking Furnaces - 001 | 64.003 | natural gas/fuel gas | 1028 | MM BTU/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices and proper operation and maintenance; gaseous fuels; economizers & Insulation | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Ethylene Cracking Furnace - 015 | 64.003 | natural gas/fuel gas | 168 | mm btu |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices and proper operation and maintenance; gaseous fuels; economizers & insulation | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | MELT SHOP GHG | 81.21 | NATURAL GAS | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | ENERGY EFFICIENCY IMPROVEMENTS | 0.155 | LB/TON OF STEEL |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | ENCLOSED PRESSURE SF6 CIRCUIT BREAKERS | 99.999 |  | 0 |  | 0.5% BY WT ANNUAL LEAKAGE RATE 10% BY WT LEAK DETECTION SYSTEM | Carbon Dioxide Equivalent (CO2e) | Other - EPA METHOD 3B FOR CO2 | (Greenhouse Gasses (GHG)) | CO2e | N |  | 9.56 | T/YR | 12-MONTH ROLLING TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0827 | PRAXAIR CLEAR LAKE PLANT | PRAXAIR INC | HARRIS | TX |  | USA | TODD DUNN | 281-203-3606 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 | 144239, PSDTX1512, GHGPSDTX164 | 2813 | 325120 | Not FOUND | 08/22/2017 &nbsp;ACT | 10/19/2017 &nbsp;ACT | 2017-10-19 | 2017-11-02 | A |  | Hydrogen-Carbon Monoxide plant using an auto-thermal reformer to produce hydrogen and carbon monoxide. |  | HyCO Analyzer Vents | 99.999 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emissions included in Grouped limit
TX-0827 | PRAXAIR CLEAR LAKE PLANT | PRAXAIR INC | HARRIS | TX |  | USA | TODD DUNN | 281-203-3606 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 | 144239, PSDTX1512, GHGPSDTX164 | 2813 | 325120 | Not FOUND | 08/22/2017 &nbsp;ACT | 10/19/2017 &nbsp;ACT | 2017-10-19 | 2017-11-02 | A |  | Hydrogen-Carbon Monoxide plant using an auto-thermal reformer to produce hydrogen and carbon monoxide. |  | HyCO Process Condensate Stripper MSS | 99.999 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | emissions part of grouped limit
TX-0827 | PRAXAIR CLEAR LAKE PLANT | PRAXAIR INC | HARRIS | TX |  | USA | TODD DUNN | 281-203-3606 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 | 144239, PSDTX1512, GHGPSDTX164 | 2813 | 325120 | Not FOUND | 08/22/2017 &nbsp;ACT | 10/19/2017 &nbsp;ACT | 2017-10-19 | 2017-11-02 | A |  | Hydrogen-Carbon Monoxide plant using an auto-thermal reformer to produce hydrogen and carbon monoxide. |  | HyCO CO2 Stripper MSS | 99.999 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emissions included in sitewide grouped limit
*TX-0830 | PRAXIAR CLEAR LAKE | PRAXIAR INC | HARRIS | TX |  | USA | TODD DUNN | 281-203-3606 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 144239, PSDTX1512, AND GHGPSDT | 2813 | 325120 | not found | 09/22/2017 &nbsp;ACT | 10/20/2017 &nbsp;ACT | 2018-04-25 | 2018-05-02 | A |  | HYCO USING AUTO-THERMAL REFORMER |  | HYCO ANALYZER VENTS | 99.999 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0830 | PRAXIAR CLEAR LAKE | PRAXIAR INC | HARRIS | TX |  | USA | TODD DUNN | 281-203-3606 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 144239, PSDTX1512, AND GHGPSDT | 2813 | 325120 | not found | 09/22/2017 &nbsp;ACT | 10/20/2017 &nbsp;ACT | 2018-04-25 | 2018-05-02 | A |  | HYCO USING AUTO-THERMAL REFORMER |  | HyCO Process Condensate Stripper MSS | 99.999 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0830 | PRAXIAR CLEAR LAKE | PRAXIAR INC | HARRIS | TX |  | USA | TODD DUNN | 281-203-3606 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 144239, PSDTX1512, AND GHGPSDT | 2813 | 325120 | not found | 09/22/2017 &nbsp;ACT | 10/20/2017 &nbsp;ACT | 2018-04-25 | 2018-05-02 | A |  | HYCO USING AUTO-THERMAL REFORMER |  | HyCO CO2 Stripper MSS | 99.999 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0354 | KRATON POLYMERS U.S. LLC | KRATON POLYMERS U.S. LLC | WASHINGTON | OH | 45714-0235 | USA | DALE LOUDERMILK | 740-423-2299 | DALE.LOUDERMILK@KRATON.CC | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0108853 | 2822 | 325212 | 110030900997 | 08/29/2012 &nbsp;ACT | 01/15/2013 &nbsp;ACT | 2013-09-27 | 2016-05-04 | B |  | Thermoplastic elastomer manufacturing facility | Two new 249 MMBtu/hour natural gas, distillate oil, and belpre naphtha-fired boilers installed to replace 2 existing coal, distillate oil, and belpre naphtha-fired boilers. | Two 249 MMBtu/H boilers | 12.31 | Natural Gas | 249 | MMBtu/H | Two boilers, burning natural gas or distillate oil w/ less than 0.05% sulfur; and co-fired with maximum of 54.8 MMBtu/H Belpre naphtha. Fitted with low-NOx burners with flue gas recirculation, as needed. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 357522 | T/YR |  | N/A | SIP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Netted out for CO2e by replacing old coal/oil-fired boilers.
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | AUXILIARY BOILER (1) AND FUEL GAS HEATERS (6) | 12.31 | NATURAL GAS | 185 | MMBTU/HR | The auxiliary boiler will provide steam to the steam turbine at startup and at cold starts to warm up the ST rotor. The steam from the auxiliary boiler will not be used to augment the power generation of the combustion turbines or steam turbine. The boiler is proposed to operate 8760 hrs/yr but will be limited by an annual fuel throughput based on a capacity factor of 10%. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Natural gas and fuel and high efficiency design and operation. | 117.1 | LB/MMBTU |  | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | DIESEL-FIRED EMERGENCY GENERATOR 3000 kW (1) | 17.11 | DIESEL FUEL | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Other - NA | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices/Maintenance | 163.6 | LB/MMBTU |  | N/A |  | U | 0 | U | 1178 | T/YR | 12 MO ROLLING TOTAL | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | DIESEL-FIRED WATER PUMP 376 bph (1) | 17.21 | DIESEL FUEL | 0 |  | FWP-1: 104.0 tons/year (12-month rolling total) | Carbon Dioxide Equivalent (CO2e) | Other - NA | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices/Maintenance | 104 | T/YR | 12 MO ROLLING TOTAL | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | PROPANE-FIRED EMERGENCY GENERATORS 150 kW (2) | 17.23 | PROPANE | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Other - NA | (Greenhouse Gasses (GHG)) | CO2e | P | Good Combustion Practices/Maintenance | 136.1 | LB/MMBTU |  | N/A |  | U | 0 | U | 121 | T/YR | 12 MO ROLLING AVG | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | CIRCUIT BREAKERS (3) | 99.999 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Enclosed pressure type breaker and leak detector | 19 | T/YR |  | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | GAS PIPING COMPONENTS-FUGITIVE LEAKS | 99.999 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Audible/visual/olfactory (AVO) monitoring and leak repair | 0 |  |  | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | CIRCUIT BREAKERS (11) | 99.999 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Enclosed pressure type breaker and leak detection | 1032 | T/YR |  | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | COMBUSTION TURBINE GENERATOR WITH DUCT-FIRED HEAT RECOVERY STEAM GENERATORS (3) | 15.21 | natural gas | 3227 | MMBTU/HR | 3227 MMBTU/HR CT with 500 MMBTU/HR Duct Burner, 3 on 1 configuration. | Carbon Dioxide Equivalent (CO2e) | Other - 3C | (Greenhouse Gasses (GHG)) | CO2e | N |  | 890 | LB/MWH | NET OUTPUT AFTER 30 YEARS OF OPERATION | OTHER CASE-BY-CASE |  | U | 0 | U | 1911596 | TONS/YR |  | 0 |  |  | 0 | 0 | N
*IN-0218 | SABIC INNOVATIVE PLASTICS MT. VERNON, LC | SABIC INNOVATIVE PLASTICS MT. VERNON, LC | POSEY | IN | 47620 | USA | GREGORY MICHAEL | 8128314732 | GREGORY.MICHAEL@SABIC-IP.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI P. SINHA 317-234-4907 | 091-34002-00002 | 2821 | 325211 | 110000403670 | 12/20/2013 &nbsp;ACT | 12/11/2014 &nbsp;ACT | 2015-08-14 | 2017-07-12 | D | HTTP://PERMITS.AIR.IDEM.IN.GOV/34002F.PDF | PLASTIC MANUFACTURING PLANT |  | NATURAL GAS-FIRED AUXILIARY BOILER (AUX BOILER) | 12.31 | NATURAL GAS | 249 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 133521 | T/YR |  |  |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | THE BOILER SHALL ACHEIVE A MINIMUM 80% THERMAL EFFICIENCY (HHV); THE BOILER SHALL FIRE NATURAL GAS ONLY; BOILER INSULATION; EFFICIENT BURNER DESIGN; IMPROVED COMBUSTION MEASURES:OPTIMIZATION & DIGITAL CONTROL SYSTEM; MINIMIZATION OF AIR INFILTRATION; IMPROVED COMBUSTION MEASURES: COMBUSTION TUNING; OPERATING AND MAINTENANCE (O&M) PRACTICES; STEAM LINE MAINTENANCE.
*IN-0218 | SABIC INNOVATIVE PLASTICS MT. VERNON, LC | SABIC INNOVATIVE PLASTICS MT. VERNON, LC | POSEY | IN | 47620 | USA | GREGORY MICHAEL | 8128314732 | GREGORY.MICHAEL@SABIC-IP.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI P. SINHA 317-234-4907 | 091-34002-00002 | 2821 | 325211 | 110000403670 | 12/20/2013 &nbsp;ACT | 12/11/2014 &nbsp;ACT | 2015-08-14 | 2017-07-12 | D | HTTP://PERMITS.AIR.IDEM.IN.GOV/34002F.PDF | PLASTIC MANUFACTURING PLANT |  | NATURAL GAS-FIRED AUXILIARY BOILER (AUX 2 BOILER) | 12.31 | NATURAL GAS | 249 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 133521 | T/YR |  |  |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | THE BOILER SHALL ACHEIVE A MINIMUM 80% THERMAL EFFICIENCY (HHV); THE BOILER SHALL FIRE NATURAL GAS ONLY; BOILER INSULATION; EFFICIENT BURNER DESIGN; IMPROVED COMBUSTION MEASURES:OPTIMIZATION & DIGITAL CONTROL SYSTEM; MINIMIZATION OF AIR INFILTRATION; IMPROVED COMBUSTION MEASURES: COMBUSTION TUNING; OPERATING AND MAINTENANCE (O&M) PRACTICES; STEAM LINE MAINTENANCE.
*IN-0218 | SABIC INNOVATIVE PLASTICS MT. VERNON, LC | SABIC INNOVATIVE PLASTICS MT. VERNON, LC | POSEY | IN | 47620 | USA | GREGORY MICHAEL | 8128314732 | GREGORY.MICHAEL@SABIC-IP.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI P. SINHA 317-234-4907 | 091-34002-00002 | 2821 | 325211 | 110000403670 | 12/20/2013 &nbsp;ACT | 12/11/2014 &nbsp;ACT | 2015-08-14 | 2017-07-12 | D | HTTP://PERMITS.AIR.IDEM.IN.GOV/34002F.PDF | PLASTIC MANUFACTURING PLANT |  | NATURAL GAS-FIRED BOILER (CG1 BOILER) | 12.31 | NATURAL GAS | 249 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 133521 | T/YR |  |  |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | THE BOILER SHALL ACHEIVE A MINIMUM 80% THERMAL EFFICIENCY (HHV); THE BOILER SHALL FIRE NATURAL GAS ONLY; BOILER INSULATION; EFFICIENT BURNER DESIGN; IMPROVED COMBUSTION MEASURES:OPTIMIZATION & DIGITAL CONTROL SYSTEM; MINIMIZATION OF AIR INFILTRATION; IMPROVED COMBUSTION MEASURES: COMBUSTION TUNING; OPERATING AND MAINTENANCE (O&M) PRACTICES; STEAM LINE MAINTENANCE. IF CG1 BOILER OPERATES AS AN AUXILIARY BOILER, NO ADDITIONA BACT REQUIREMENTS APPLY. BUT IF CG1 BOILER IS A PRIMARY USE BOILER, THE FOLLOWING ITEM WILL BE INCLUDED AS BACT: AIR PREHEATER OR ECONOMIZER
*IN-0218 | SABIC INNOVATIVE PLASTICS MT. VERNON, LC | SABIC INNOVATIVE PLASTICS MT. VERNON, LC | POSEY | IN | 47620 | USA | GREGORY MICHAEL | 8128314732 | GREGORY.MICHAEL@SABIC-IP.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI P. SINHA 317-234-4907 | 091-34002-00002 | 2821 | 325211 | 110000403670 | 12/20/2013 &nbsp;ACT | 12/11/2014 &nbsp;ACT | 2015-08-14 | 2017-07-12 | D | HTTP://PERMITS.AIR.IDEM.IN.GOV/34002F.PDF | PLASTIC MANUFACTURING PLANT |  | COMBUSTION TURBINE:COGEN | 15.11 | NATURAL GAS | 1812 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 937379 | T/YR |  |  |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | COGEN SHALL USE NATURAL GAS ONLY; COGEN SHALL ACHEIVE A MINIMUM NET PLANT EFFICIENCY OF 85% (LHV)
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Boiler, Nat Gas Fired | 12.31 | NATURAL GAS | 261 | MMBTU/H | 261 MMBTU/H natrual gas-fired boiler, equipped with low-NOx burners, SCR, and CO catalytic oxidation | Carbon Monoxide | Other - CEMS | (InOrganic Compounds) | 630-08-0 | A | Oxidation Catalyst | 5 | PPMV @ 3% O2 | 3-HR ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 261 MMBtU/H natural gas-fired boiler, equipped with natural gas-fired boiler, equipped with low-NOx burners, SCR, and CO catalytic oxidation
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, VACUUM DEGASSER | 13.29 | NATURAL GAS | 51.2 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | B | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.0824 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACE, ANNEALING PICKLING LINE | 13.29 | NATURAL GAS | 66 | MMBTU/H | ANNEALING PICKLING LINE FURNACE SN-47; ANNEALING COATING LINE FURNACE , SN 51; | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.0824 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, PICKLE LINE | 13.31 | NATURAL GAS | 67 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.0824 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILERS SN-26 AND 27, GALVANIZING LINE | 13.31 | NATURAL GAS | 24.5 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.0824 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.0824 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0238 | ALLIANCE REFINERY | CONOCOPHILLIPS COMPANY | PLAQUEMINES | LA | 70037 | USA | CHRIS CHANDLER | 5046567711 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CORBET MATHIS - PHONE: 225-219-3181 | PSD-LA-75(M3) | 2911 | 324110 | 2207500003 | 01/22/2008 &nbsp;ACT | 07/10/2009 &nbsp;ACT | 2009-09-11 | 2012-05-18 | C |  | A PETROLEUM REFINERY IN BELLE CHASSE, LA. | PSD-LA-75 (OCTOBER 22, 1978): TO EXPAND THE FCCU CAPACITY FROM 78,000 TO 89,000 BPD. PSD-LA-75(M3): INCLUDING STARTUP SHUTDOWN EMISSIONS, RECONCILE SO2 AND CO EMISSIONS FROM HEATER AND BOILERS | FCCU FEED HEATER | 12.31 | REFINERY GAS | 181.7 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | EQUIPPED WITH VORTOMETRIC HIGH INTENSITY COMBUSTION UNIT | 0.55 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | START-UP BOILER | 12.31 | NATURAL GAS | 240 | MMBTU/H |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | GOOD AND EFFICIENT OPERATING PRACTICES | 8.88 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.037 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 |  |  | 0 | 0 | N |  | PERIODIC STACK TESTING TO VERIFY COMPLIANCE
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | MR. RANDY THOMPSON | (615) 532-6825 | randall.thompson@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000370535 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Two Natural Gas-Fired Auxiliary Boilers | 12.31 | Natural Gas | 450 | MMBtu/hr | Two 450 MMBtu/hr natural gas-fired auxiliary boilers will provide steam generation during threshold transitional periods and during malfunction events when the CT and HRSG are not able to operate. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion design and practices | 0.084 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT START-UP HEATER | 12.31 | NATURAL GAS | 38 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICE | 0.76 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.19 | T/YR | ROLLING 12 MONTH AVERAGE | 0.01 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 | 0 | N
TX-0731 | CORPUS CHRISTI TERMINAL CONDENSATE SPLITTER | MAGELLAN PROCESSING LP | NUECES | TX |  | USA | SHAHANA BANOO | 918-574-7767 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, 512-239-1284, jesse.lovegren@tceq.texas.gov | 118270 AND PSDTX1398 | 2911 | 324110 | 110017840782 | 02/19/2015 &nbsp;ACT | 04/10/2015 &nbsp;ACT | 2015-04-14 | 2016-05-16 | B |  | 100 MBpd topping refinery |  | Industrial-Size Boilers/Furnaces | 12.31 | natural gas | 0 |  | (2) 129 Million British Thermal Units per hour (MMBtu/hr) direct-fired process heaters and (2) 106 MMBtu/hr thermal fluid heaters (one pair for each train) | Carbon Monoxide | Other - 40 CFR Pt. 60, Appendices B, F | (InOrganic Compounds) | 630-08-0 | P | Good combustion practice to ensure complete combustion | 50 | PPMVD @ 3% O2 | 1-HR AVG | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | 250 MMBTU/H STEAM SUPERHEATER BOILER, SRC31 | 12.3 | NAT GAS & PSA TAILGAS | 250 | MMBTU/H | OPERATED DURING STEADY-STATE PRODUCTION ON NATURAL GAS AND (HYDROGEN-RICH) PRESSURE SWING ADSORBER (PSA) TAILGAS. BALANCED WITH PACKAGE BOILER AT STARTUP/SHUTDOWN SO COMBINED HEAT INPUT <= 250 MMBTU/H. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N | GOOD COMBUSTION PRACTICES | 0.074 | LB/MMBTU |  | BACT-PSD | NSPS | Y | 0 |  | 18.5 | LB/H |  | 0 |  |  | 0 | 0 | N |  | LIMITS APPLY TO PACKAGE BOILER AND STEAM SUPERHEATER COMBINED EMISSIONS.
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Startup Heater | 12.31 | Natural gas | 110.12 | MMBTU/H |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | good combustion practices | 0.0194 | LB/MMBTU | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.1 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | 250 MMBTU/H PACKAGE BOILER, SRC24 | 12.31 | NAT GAS | 250 | MMBTU/H | OPERATED ONLY DURING STARTUP AND SHUTDOWN, RAMPS DOWN/UP AS STEAM SUPERHEATER BOILER RAMPS UP/DOWN. COMBINED HEAT INPUT BALANCED <= 250 MMBTU/HR. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 0.074 | LB/MMBTU |  | BACT-PSD |  | Y | 0 |  | 18.5 | LB/H |  | 0 |  |  | 0 | 0 | N |  | LIMITS APPLY TO PACKAGE BOILER AND STEAM SUPERHEATER COMBINED EMISSIONS.
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Startup Heater | 12.31 | natural gas | 104 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion practices | 0.037 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*IN-0287 | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING STATION | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING | KNOX | IN | 47528 | USA | PATRICK COUGHLIN | 317-838-2108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Mehul Sura 317-233-6868 msura@IDEM.IN.gov Section Chief - Tripurari P. Sinha Ph. D. 317-234-4907 | 083-38023-00003 | 4911 | 22 | Not Entered | 12/22/2016 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2018-07-25 | 2018-07-25 | C | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | stationary electric utility generating station |  | Auxiliary Boiler | 12.31 | natural gas | 213 | MMBtu/hr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion practices | 0.036 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This BACT is for Startup and Shutdown emissions only
LA-0229 | SHINTECH PLAQUEMINE PLANT 2 | SHINTECH LOUISIANA LLC | IBERVILLE | LA | 70764 | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-731 | 2821 | 325211 | UNKNOWN | 11/19/2010 &nbsp;ACT | 07/10/2008 &nbsp;ACT | 2009-04-02 | 2009-04-20 | B |  | A PROPOSED 1.81 BILLION LBS/YR PVC PRODUCTION COMPLEX WHICH WILL CONSIST OF A CHLORALKALI PLANT, AN EDC/VCM PLANT, AND A PVC PLANT | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | EQT112, EQT113 - TWO UTIL. BOILERS (2U-1, 2U-2) | 12.31 | NATURAL GAS | 250 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 0.0362 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Auxiliary boilers | 12.31 | natural gas | 171 | mm btu/hr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUAUXBOILER (Auxiliary boiler) | 12.31 | Natural gas | 182 | MMBTU/H | A natural gas fired auxiliary boiler, rated at 182 MMBTU/H to provide auxiliary steam when the plant is off-line, used to maintain warm drums on the HRSG and maintain the steam turbine generator seals. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices | 0.04 | LB/MMBTU |  | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The cost for catalytic reduction is estimated to be over $26,000 per ton of CO and VOC emissions combined.
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | 245 MMBtu natural gas fired Auxiliary boiler | 12.31 | Natural Gas | 1052 | MMscf/yr | Total fuel usage of the auxiliary boiler shall not exceed 1052 MMsch/yr on a 12-month rolling basis | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices | 0.037 | LB/MMBTU |  | BACT-PSD | NSPS | U | 0 | U | 19.85 | LB/HR |  | 0 |  |  | 0 | 0 | N
TX-0708 | LA PALOMA ENERGY CENTER | LA PALOMA ENERGY CENTER, LLC | CAMERON | TX |  | USA | GARY NEUS | (281) 682-8448 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 101542 PSDTX1288 | 4911 | 221112 | unknown | 03/15/2012 &nbsp;ACT | 02/07/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is a new electric power plant, fueled by pipeline quality natural gas. The design of the plant is standard combined cycle (CC) technology. |  | boiler | 12.31 | natural gas | 150 | MMBTU/H | annual usage limitation to 876 hours per year | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion practices | 75 | PPMVD | @3% O2, 3-HR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Auxiliary Boiler | 12.31 | Natural Gas | 100 | mmBtu/hr | Limited to 2,000 hours of operation per year. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good Combustion Practices | 4 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0.04 | LB/MMBTU |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER EU-002 | 13.31 | NATURAL GAS | 70 | MMBTU/HR |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 2.556 | LB/H | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 200 | H/YR |  | 0 |  |  | 0 | 0 | N | 2016 | SHALL COMBUST NATURAL GAS
LA-0229 | SHINTECH PLAQUEMINE PLANT 2 | SHINTECH LOUISIANA LLC | IBERVILLE | LA | 70764 | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-731 | 2821 | 325211 | UNKNOWN | 11/19/2010 &nbsp;ACT | 07/10/2008 &nbsp;ACT | 2009-04-02 | 2009-04-20 | B |  | A PROPOSED 1.81 BILLION LBS/YR PVC PRODUCTION COMPLEX WHICH WILL CONSIST OF A CHLORALKALI PLANT, AN EDC/VCM PLANT, AND A PVC PLANT | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | EQT122-EQT125 - FOUR VCM CRACKING FURNACES | 13.31 | NATURAL GAS | 90 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES | 0.046 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Regenerative Heaters | 13.31 | natural gas | 7.37 | mm btu/hr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | boiler A and B (010 and 011) | 12.31 | natural gas/fuel gas | 248 | mm btu/hr (each) |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion practices and proper operation and maintenance | 0.082 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | boiler B-201 | 12.31 | natural gas/fuel gas | 229 | mm btu |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion practices and proper operation and maintenance | 0.037 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Dryer Regenerator Heater - 005 | 13.39 | process fuel gas | 29 | mm btu/hr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | good combustion practices and proper operation and maintenance | 0.082 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | NATURAL GAS AUXILIARY BOILERS (EU-012A, EU-012B, EU-012C) | 12.31 | NATURAL GAS | 218.6 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | GOOD COMBUSTION PRACTICES AT ALL TIMES THE BOILERS ARE IN OPERATION | 37.22 | LB/MMCF EACH | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 1877.39 | MMCF/12 MONTH EACH | ROLLING AVERAGE | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: SHALL COMBUST NATURAL GAS
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUAUXBOILER (Auxiliary Boiler) | 12.31 | natural gas | 182 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 182 MMBTU/H fuel heat input. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices. | 0.04 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | An oxidation catalyst is greater than $40,000/ton for CO and VOC together.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGFUELHTR (Two fuel pre-heaters identified as EUFUELHTR1 &amp; EUFUELHTR2) | 13.31 | Natural gas | 27 | MMBTU/H | Two natural gas fired dew point heaters for warming the natural gas fuel (EUFUELHTR1 & EUFUELHTR2 in flexible group FGFUELHTR). The total combined heat input during operation shall not exceed 27 MMBTU/H (each) as well. The CO2e limit is for both units combined; however the other limits are per unit. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Good combustion practices. | 2.22 | LB/H | HOURLY; EACH UNIT | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit of 2.22 lb/hr is for each fuel heater. An oxidation catalyst is greater than $40,000/ton for CO and VOC together, factoring in the redundancy of the heaters (limited joint operation).
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Startup Heater | 12.31 | Natural Gas | 101 | MMBTU/H | Natural Gas-Fired 101 MMBtu/hr Startup Heater. Installed in 1976. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | Limited Use (200 hr/yr) | 0.082 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | TUNNEL FURNACES SN-20 AND 21 | 12.31 | NATURAL GAS | 234 | MMBTU/H | 2 TUNNEL FURNCE SECTIONS 234 MMBTU/HR AND 192 MMBTU/HR MADE UP OF A SERIES OF INDIVIDUAL 3 MMBTU BURNERS. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.0824 | LB/MMBRU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | AMMONIA CATALYST STARTUP HEATER | 12.39 | NATURAL GAS | 106.3 | MMBTU/H | ANNUAL NATURAL GAS USAGE LIMITED TO 20.84 MMCF. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | NATURAL GAS COMBUSTION ONLY, PROPER DESIGN AND GOOD COMBUSTION PRACTICES | 37.23 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROL TYPICALLY CONSIDERED NOT FEASIBLE FOR LIMITED USE EMISSION UNITS.
*TX-0641 | PINECREST ENERGY CENTER | PINECREST ENERGY CENTER LLC | ANGELINA | TX |  | USA | KATHLEEN SMITH | 281-253-4385 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | PSDTX1298 | 4911 |  |  | 06/22/2012 &nbsp;ACT | 11/12/2013 &nbsp;ACT | 2013-11-21 | 2017-11-17 | A |  | Combinec Cycle Electric Generating Plant | 103839 | Auxiliary boiler | 12.31 | natural gas | 150 | MMBTU/H | limited to 876 hours per year of operation | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | pipeline quality natural gas and good combustion | 75 | PPMVD | INITIAL STACK TEST, 3% OXYGEN | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | FOUR (4) NATURAL GAS-FIRED BOILERS | 12.31 | NATURAL GAS | 218 | MMBTU/HR, EACH | FUEL INPUT TO ALL FOUR BOILERS SHALL NOT EXCEED 2,802 MMCF/YEAR | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | PROPER DESIGN AND GOOD COMBUSTION PRACTICES | 37.22 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0827 | PRAXAIR CLEAR LAKE PLANT | PRAXAIR INC | HARRIS | TX |  | USA | TODD DUNN | 281-203-3606 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Sean O'Brien 512-239-1137 | 144239, PSDTX1512, GHGPSDTX164 | 2813 | 325120 | Not FOUND | 08/22/2017 &nbsp;ACT | 10/19/2017 &nbsp;ACT | 2017-10-19 | 2017-11-02 | A |  | Hydrogen-Carbon Monoxide plant using an auto-thermal reformer to produce hydrogen and carbon monoxide. |  | HyCO Heater | 12.31 | natural gas | 180 | MM BTU/HR |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | The use of gaseous fuel and good combustion practices | 50 | PPMVD | @ 3% O2 | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Db
*TX-0830 | PRAXIAR CLEAR LAKE | PRAXIAR INC | HARRIS | TX |  | USA | TODD DUNN | 281-203-3606 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien, (512) 239-1137, Sean.OBrien@tceq.texas.gov | 144239, PSDTX1512, AND GHGPSDT | 2813 | 325120 | not found | 09/22/2017 &nbsp;ACT | 10/20/2017 &nbsp;ACT | 2018-04-25 | 2018-05-02 | A |  | HYCO USING AUTO-THERMAL REFORMER |  | HYCO HEATER | 12.31 | NATURAL GAS | 180 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | The use of gaseous fuel and good combustion practices | 50 | PPMVD@3% O2 |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Db
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Heating Medium Heaters | 12.31 | natural gas | 130 | MMBTU/H | There are (5) heaters each at 130 MMBtu/hr which operate when the turbine exhaust is not providing enough heat for the amine regenrating heating oil system | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | P | ultra-low NOx burners | 25 | PPMVD | @3% O2 AND 1 HOUR BASED ON STACK TEST | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0354 | KRATON POLYMERS U.S. LLC | KRATON POLYMERS U.S. LLC | WASHINGTON | OH | 45714-0235 | USA | DALE LOUDERMILK | 740-423-2299 | DALE.LOUDERMILK@KRATON.CC | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0108853 | 2822 | 325212 | 110030900997 | 08/29/2012 &nbsp;ACT | 01/15/2013 &nbsp;ACT | 2013-09-27 | 2016-05-04 | B |  | Thermoplastic elastomer manufacturing facility | Two new 249 MMBtu/hour natural gas, distillate oil, and belpre naphtha-fired boilers installed to replace 2 existing coal, distillate oil, and belpre naphtha-fired boilers. | Two 249 MMBtu/H boilers | 12.31 | Natural Gas | 249 | MMBtu/H | Two boilers, burning natural gas or distillate oil w/ less than 0.05% sulfur; and co-fired with maximum of 54.8 MMBtu/H Belpre naphtha. Fitted with low-NOx burners with flue gas recirculation, as needed. | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | P | Use of clean fuels and good combustion practices | 0.036 | LB/MMBTU | BURNING DISTILLATE OIL W/ BELPRE NAPHTHA | BACT-PSD | SIP | U | 0 | U | 164 | T/YR | FROM BOTH BOILERS | 0.075 | LB/MMBTU | BURNING NATURAL GAS W/ BELPRE NAPHTHA | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Three (3) Package Boilers | 12.31 | Natural Gas | 243 | MMBTU/H | Three (3) New Natural Gas-Fired 243 MMBtu/hr Package Boilers | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 50 | PPMV | 3-HR AVG @ 3% O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 110 | MMBTU/H |  | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | N |  | 50 | PPMVD | @3% O2, 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
GA-0127 | PLANT MCDONOUGH COMBINED CYCLE | SOUTHERN COMPANY/GEORGIA POWER | COBB | GA | 30080 | USA |  |  |  | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us | JOHN YNTEMA 404-363-7117 JOHN.YNTEMA@DNR.STATE.GA.US | 4911-067-0003-V-02-2 | 4911 | 221112 | 110000355972 | 03/08/2007 &nbsp;ACT | 01/07/2008 &nbsp;ACT | 2008-06-17 | 2008-10-09 | B |  | THREE NATURAL GAS FIRED COMBINED CYCLE POWER BLOCKS. EACH BLOCK CONSISTS OF TWO COMBUSTION TURBINES, TWO HEAT RECOVERY STEAM GENERATORS WITH DUCT BURNERS AND A STEAM TURBINE. TWO TURBINES WILL BE CAPABLE OF FIRING ULTRA LOW SULFUR DIESEL AS BACKUP FUEL. EACH COMBINED-CYCLE BLOCK WILL HAVE OUTPUT OF 840 MW. TURBINES ARE REPLACING TWO COAL-FIRED UTILITY BOILERS |  | AUXILLARY BOILERS | 12.31 | NATURAL GAS | 200 | MMBTU/H | THREE 200 MMBTU/H BOILERS, EACH LIMITED TO 10% ANNUAL CAPACITY FACTOR | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 0.037 | LB/MMBTU | 3-HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NM-0052 | ZIA II GAS PLANT | DCP MIDSTREAM L.P. | LEA | NM | 88255 | USA | JENNIFER HANNA | 4326205460 | JHANNA@DCPMIDSTREAM.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Joseph Kimbrell, 505-476-4300, joseph.kimbrell@state.nm.us | PSD-5217 | 1311 | 211111 | 110056438083 | 11/13/2013 &nbsp;ACT | 04/25/2014 &nbsp;ACT | 2015-11-19 | 2016-07-07 | A | https://www.env.nm.gov/aqb/ | Natural Gas Processing plant using cryogenic process and designed to operate at 230 MMscf/day of natural gas. | The permittee submitted an application on 5/13/2015 to revise the permit. Most BACT determinations will not change. | Industrial Sized Boilers/Furnaces &gt;100 mmBtu/hr | 12.31 | Natural gas | 114 | mmBtu/hr |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 0 |  |  | BACT-PSD | NSPS , SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0310 | AMERICAN MUNICIPAL POWER GENERATING STATION | AMERICAN MUNICIPAL POWER | MEIGS | OH | 45771 | USA | RANDY MEYER | 6143376222 | RMEYER@AMP-OHIO.ORG | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104461 | 4911 | 221112 | 110000384325 | 05/15/2006 &nbsp;ACT | 10/08/2009 &nbsp;ACT | 2008-04-15 | 2009-11-06 | A |  | TWO 5191 MMBTU/HOUR PULVERIZED COAL-FIRED BOILERS; ONE 150 MMBTU/HOUR NATURAL GAS AUXILIARY BOILER, ONE FLY ASH AND GYPSUM LANDFILL, COAL STORAGE, CRUSHERS, FERTILIZER PLANT, LIMESTONE AND FLY ASH HANDLING EQUIPMENT, AND COOLING CELLS. ADMINISTRATIVE MODIFICATION 10/09 TO ADD CASE-BY-CASE MACT FOR BOILERS. 1ST ISSUED 2/7/08 AS PTI#06-08138; STILL INITIAL INSTALLATION | FUGITIVE EMISSIONS FROM STORAGE PILES (COAL,LIMESTONE, UREA), CONVEYING, HANDLING, ROADWAYS, BARGE OR TRUCK UNLOADING WERE NOT ENTERED INTO THE DATABASE DUE TO THE INSIGNIFICANT EMISSIONS (MOST < 1 TON FUGITIVE PM) AND LACK OF PROCESS CODES TO ENTER THEM. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 150 | MMBTU/H |  | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 12.6 | LB/H |  | BACT-PSD | SIP | U | 0 | U | 5.52 | T/YR | PER ROLLING 12 MONTHS | 400 | PPM | BY VOLUME, DRY BASIS TO 3% O2, 3-HR AVG. | 0 | 0 | N
OH-0336 | CAMPBELL SOUP COMPANY | CAMPBELL SOUP COMPANY | HENRY | OH |  | USA | ANN CURNOW | 763-278-5932 | ANN.CURNOW@HDRIC.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0106678 | 2032 | 311422 | 110041176679 | 07/28/2010 &nbsp;ACT | 12/14/2010 &nbsp;ACT | 2011-03-31 | 2011-10-13 | B |  | Canned food maufacturing facility. | Replacing 5 natural gas boilers with 3 new ones. Facility is a Major PSD facility for SO2, NOx, PE, and CO. This permit is PSD for CO. Five old natural gas steam boilers will be decommissioned upon the installation of the 3 new ones. The boilers will burn natural gas and use #2 fuel oil as backup. The facility took a restriction on the #2 fuel oil used to avoid PSD on all but the CO. The boilers are used for steam production for process lines and cogeneration for building heat. | Boilers (3) | 12.31 | Natural Gas | 0 |  | The natural gas throughput is unknown; the limits are based on the potential of 8760 hours of operation. Boilers used for cogeneration of heat to facility. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 0.075 | LB/MMBTU | BASED ON MFG. GUARANTEE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 118.26 | T/YR | ROLLING 12 MO. FROM 3 BOILERS TOGETHER | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Waste Heat Boilers | 13.31 | Natural Gas | 50 | MMBTU/H | Five (5) Natural Gas-Fired 50 MMBtu/hr Waste Heat Boilers. Installed in 1986. | Carbon Monoxide | Unspecified | (InOrganic Compounds) | 630-08-0 | N |  | 50 | PPMV | 3-HR AVG @ 15 % O2 | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Regeneration Heater, methanol to gasoline | 13.31 | NATURAL GAS | 13 | MMBTU/H | 13 MMBTU/H methanol-to-gasoline regeneration heater, equipped with low-NOx burner | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | N |  | 0.08 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 13 MMBTU/H methanol-to-gasoline regeneration heater, equipped with low-NOx burner
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Reactor Heater, 5 | 13.31 | NATURAL GAS | 12 | MMBTU/H | Five 12 MMBTU/H reactor heaters, equipped with low-NOx burners | Carbon Monoxide | EPA/OAR Mthd 10 | (InOrganic Compounds) | 630-08-0 | N |  | 0.08 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Five 12 MMBTU/H reactor heaters, equipped with low-NOx burners
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | 250 MMBTU/H STEAM SUPERHEATER BOILER, SRC31 | 12.3 | NAT GAS & PSA TAILGAS | 250 | MMBTU/H | OPERATED DURING STEADY-STATE PRODUCTION ON NATURAL GAS AND (HYDROGEN-RICH) PRESSURE SWING ADSORBER (PSA) TAILGAS. BALANCED WITH PACKAGE BOILER AT STARTUP/SHUTDOWN SO COMBINED HEAT INPUT <= 250 MMBTU/H. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOX BURNER & SCR, AMMONIA SLIP LIMITED TO 10 PPM (DRY) CORRECTED TO 15% O2. | 0.02 | LB/MMBTU |  | BACT-PSD | NSPS | Y | 97 | N | 5 | LB/H |  | 0 |  |  | 0 | 0 | N |  | LIMITS APPLY TO PACKAGE BOILER AND STEAM SUPERHEATER COMBINED EMISSIONS.
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | Duct Burners (4) | 12.31 | Natural Gas | 140 | MMBTU/H | Each duct burner-turbine pair exhaust through a common stack | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 5 | PPMDV | 4-HOUR AVERAGE | BACT-PSD |  | U | 90 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit is for each turbine-duct burner pair due to common exhaust stack. BACT limit commences 70 minutes after startup of turbines. Cost analysis not conducted since cost was not a factor in BACT determination.
AK-0073 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION | ANCHORAGE | AK | 99518 | USA | GREGORY ARTHUR | 907 762 4492 |  | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Kwame Agyei, Permit Engineer, kwame.agyei@alaska.gov | AQ0164CPT01 | 4911 | 221112 | 110046491854 | 04/14/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2012-02-22 | 2014-01-08 | D |  | Power plant that contains four combustion turbines, four duct burners, a black start generator, and an auxiliary heater. |  | Fuel Combustion | 12.31 | Natural Gas | 140 | MMBTU/H | EU IDs 9-12 Duct Burners | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Duct Burners EU IDs 9 through 12 shall be equipped with Selective Catalytic Reduction (SCR). SCR is a post-combustion gas treatment technique for reduction of nitric oxide (NO) and nitrogen dioxide (NO2) in the turbine exhaust stream to molecular nitrogen, water, and oxygen. This process is accomplished by using ammonia (NH3) as a reducing agent, and is injected into the flue gas upstream of the catalyst bed. By lowering the activation energy of the NOx decomposition removal efficiency of 80 to 90 percent are achievable. | 5 | PPM | 4-HR AVG. | BACT-PSD |  | U | 85 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0073 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION | ANCHORAGE | AK | 99518 | USA | GREGORY ARTHUR | 907 762 4492 |  | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Kwame Agyei, Permit Engineer, kwame.agyei@alaska.gov | AQ0164CPT01 | 4911 | 221112 | 110046491854 | 04/14/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2012-02-22 | 2014-01-08 | D |  | Power plant that contains four combustion turbines, four duct burners, a black start generator, and an auxiliary heater. |  | Fuel Combustion | 12.31 | Diesel | 12.5 | MMBTU/H | Auxiliary Heater | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Auxiliary heater EU 15 shall be equipped with Low NOx Burner/Flue Gas Recirculation (LNB/FGR) designs. LNBs utilize staged combustion to minimize thermal NOx formation by providing a fuel-rich reducing atmosphere in which molecular nitrogen is preferentially formed rather than NOx. FGR involves recycling a portion of the combustion gasses from the stack to the boiler windbox. The low oxygen combustion products, when mixed with combustion air, lower the overall excess oxygen concentration and act as a heat sink to lower the peak flame temperature with results in limiting thermal NOx formation. | 32 | LB/MMSCF | 3-HR AVG | BACT-PSD |  | U | 60 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Three (3) Package Boilers | 12.31 | Natural Gas | 243 | MMBTU/H | Three (3) New Natural Gas-Fired 243 MMBtu/hr Package Boilers | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Ultra Low NOx Burners | 0.01 | LB/MMBTU | 30-DAY AVERAGE | BACT-PSD |  | U | 70 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Startup Heater | 12.31 | Natural Gas | 101 | MMBTU/H | Natural Gas-Fired 101 MMBtu/hr Startup Heater. Installed in 1976. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Limited Use (200 hr/yr) | 0.098 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 55705 | 0 | N | 2014 | The economic analysis indicates the level of NOx reduction does not justify installing selective catalytic reduction. Based on the excessive cost per ton of NOx removed per year, installation of selective catalytic reduction on the startup heater is not considered a feasible option for reducing NOx emissions.
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT START-UP HEATER | 12.31 | NATURAL GAS | 38 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICE | 2.28 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.57 | T/YR | ROLLING 12 MONTH AVERAGE | 0.06 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | START-UP BOILER | 12.31 | NATURAL GAS | 240 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNERS AND FLUE GAS RECIRCULATION | 4.32 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.018 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 |  |  | 0 | 0 | N |  | PERIODIC STACK TESTING TO VERIFY COMPLIANCE
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | TUNNEL FURNACES SN-20 AND 21 | 12.31 | NATURAL GAS | 234 | MMBTU/H | 2 TUNNEL FURNCE SECTIONS 234 MMBTU/HR AND 192 MMBTU/HR MADE UP OF A SERIES OF INDIVIDUAL 3 MMBTU BURNERS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.1 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1206 | STOCKTON COGEN COMPANY | APMC STOCKTON COGEN | SAN JOAQUIN COUNTY | CA | 95206 | USA | GLENN SIZEMORE |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SJ 85-04 | 4911 | 221112 | 110000484930 | 04/24/2009 &nbsp;ACT | 09/16/2011 &nbsp;ACT | 2012-11-11 | 2014-01-14 | C | http://www.epa.gov/region09/air/permit/r9-permits-issued.html | 49.9 MW COGENERATION POWER PLANT OWNED BY AIR PRODUCTS MANUFACTURING CORPORATION (APMC) STOCKTON COGEN AND LOCATED IN STOCKTON, CALIFORNIA | PSD permit amended to allow increased operation of facility's natural gas-fired auxiliary boiler and reduced operation of its coal-fired circulating fluidized bed boiler. Facilitywide emission increases less than the PSD significant thresholds. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 178 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 7 | PPMVD | @3% O2 | BACT-PSD |  | U | 0 | U | 0.0085 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N |  | OTHER LIMITS: AUX BOILER AND CIRCULATING FLUIDIZED BED BOILER MAY ONLY BE OPERATED SIMULTANEOUSLY FOR UP TO 250 HRS PER YEAR, DURING CIRCULATING FLUIDIZED BED BOILER STARTUP AND SHUTDOWN PERIODS, AND PERIODS OF LESS THAN 10 HRS DURATION TO CONDUCT EMISSIONS TESTING
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 110 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 9 | PPMVD | @3% O2, 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Startup Heater | 12.31 | Natural gas | 110.12 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | good combustion practices | 0.119 | LB/MMBTU | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.63 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | 250 MMBTU/H PACKAGE BOILER, SRC24 | 12.31 | NAT GAS | 250 | MMBTU/H | OPERATED ONLY DURING STARTUP AND SHUTDOWN, RAMPS DOWN/UP AS STEAM SUPERHEATER BOILER RAMPS UP/DOWN. COMBINED HEAT INPUT BALANCED <= 250 MMBTU/HR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW-NOX BURNER AND FGR | 0.02 | LB/MMBTU |  | BACT-PSD | NSPS | Y | 95 | N | 5 | LB/H |  | 0 |  |  | 0 | 0 | N |  | LIMITS APPLY TO PACKAGE BOILER AND STEAM SUPERHEATER COMBINED EMISSIONS.
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Startup Heater | 12.31 | natural gas | 104 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | low-nox burners | 0.08 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | FOUR (4) NATURAL GAS-FIRED BOILERS | 12.31 | NATURAL GAS | 218 | MMBTU/HR, EACH | FUEL INPUT TO ALL FOUR BOILERS SHALL NOT EXCEED 2,802 MMCF/YEAR | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | ULTRA LOW NOX BURNERS FLUE GAS RECIRCULATION | 20.4 | LB/MMCF | 24-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | NATURAL GAS AUXILIARY BOILERS (EU-012A, EU-012B, EU-012C) | 12.31 | NATURAL GAS | 218.6 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNERS WITH FLUE GAS RECIRCULATION AND GOOD COMBUSTION PRACTICES | 20.4 | LB/MMCF EACH | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 1877.39 | MMCF/12 MONTH EACH | ROLLING AVERAGE | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: SHALL COMBUST NATURAL GAS
LA-0229 | SHINTECH PLAQUEMINE PLANT 2 | SHINTECH LOUISIANA LLC | IBERVILLE | LA | 70764 | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-731 | 2821 | 325211 | UNKNOWN | 11/19/2010 &nbsp;ACT | 07/10/2008 &nbsp;ACT | 2009-04-02 | 2009-04-20 | B |  | A PROPOSED 1.81 BILLION LBS/YR PVC PRODUCTION COMPLEX WHICH WILL CONSIST OF A CHLORALKALI PLANT, AN EDC/VCM PLANT, AND A PVC PLANT | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | EQT112, EQT113 - TWO UTIL. BOILERS (2U-1, 2U-2) | 12.31 | NATURAL GAS | 250 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS (LNB) IN COMBINATION WITH SELECTIVE CATALYTIC REDUCTION (SCR) | 0.01 | LB/MMBTU | 30 DAY ROLLING AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0.2 | LB/MMBTU | 30 DAY ROLLING AVERAGE | 0 |  |  | 0 | 0 | N
LA-0244 | LAKE CHARLES CHEMICAL COMPLEX - LAB UNIT | SASOL NORTH AMERICA, INC. | CALCASIEU | LA | 70669 | USA | MAGGIE PAGELS | 337-494-5769 | MARGARET.PAGELS@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225) 219-3395 | PSD-LA-291(M3) | 2869 | 325110 | 110017418061 | 09/17/2009 &nbsp;ACT | 11/29/2010 &nbsp;ACT | 2011-03-29 | 2011-07-06 | C |  | Chemical Production Unit for Linear Alkyl Benzene (LAB)production. | Modification to an existing PSD Permit (PSD-LA-291(M2), dated October 18, 1988) to increase operating time of the heater. Emissions will not be increased above the permitted limits. Existing BACT will not be revised. | EQT0029 - Hot Oil Heater H-601 | 12.31 | natural gas | 170 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | low nox burners | 19.69 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT was determined in 1983
LA-0275 | LINEAR ALKYL BENZENE (LAB) UNIT | SASOL CHEMICALS (USA) LLC | CALCASIEU | LA | 70669 | USA | ERIC RODRIGUEZ | 281-588-3761 | ERIC.RODRIGUEZ@SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Dan Nguyen, (225) 219-3395 | PSD-LA-291(M4) | 2865 | 325110 | 110017418061 | 10/06/2015 &nbsp;ACT | 04/29/2016 &nbsp;ACT | 2016-06-23 | 2017-04-28 | C |  | LAB production unit, PSD-LA-291(M2) issued October 18, 1998 - PSD-LA-291(M3) issued November 29, 2010. Permit PSD-LA-291(M4) for emission limits revision, No BACT change. |  | Heaters (3 units) | 12.31 | Natural Gas and Ethane | 0 |  | LH-1(H-201): 87.3 MM BTU/hr - fires CH4 & Ethane LH-2(H-202): 21.0 MM BTU/hr - fires CH4 & Ethane LH-3(H-601): 220.5 MM BTU/hr - fires CH4, Ethane, and hydrogen waste gas | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low NOX burners | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LH-1: 7.15 lbs/hr LH-2: 2.71 lbs/hr LH-3: 19.36 lbs/hr
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Auxiliary boilers | 12.31 | natural gas | 171 | mm btu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low Nox burners | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | boiler A and B (010 and 011) | 12.31 | natural gas/fuel gas | 248 | mm btu/hr (each) |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | good combustion practices; fueled by natural gas or process fuel gas; ULNB (FGR and economizer) | 0.06 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | boiler B-201 | 12.31 | natural gas/fuel gas | 229 | mm btu |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | good combustion practices; fueled by natural gas or process fuel gas; ULNB (FGR and economizer) | 0.06 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0389 | KARN WEADOCK GENERATING COMPLEX | CONSUMERS ENERGY | BAY | MI | 48732-9601 | USA | JAMES M. WALKER | 5177880428 | JMWALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | FOR TECHNICAL QUESTIONS ABOUT THIS PERMIT, PLEASE CONTACT THE PERMIT ENGINEER - DAVID K. RIDDLE RIDDLED@MICHIGAN.GOV (517-373-7081) | 341-07 | 4911 | 221112 | 26-01700033 | 10/15/2007 &nbsp;ACT | 12/29/2009 &nbsp;ACT | 2010-03-08 | 2010-12-16 | U |  | ELECTRICITY GENERATING FACILITY, EXISTING CAPACITY GREATER THAN 2,000 MW. | AFTER CONSTRUCTION CONSUMERS WILL RETIRE 5 TO 7 COAL-FIRED BOILERS (638 - 958 MW) STATEWIDE. FINAL CONDITIONS WILL BE AT WWW.DEQ.STATE.MI.US/APS/FINALCONDITIONS.SHTML. MATERIAL HANDLING - CONTACT PERMIT ENGINEER FOR TECHNICAL INFORMATION (DAVID RIDDLE, 517-373-7081). INCLUDES 9 EMISSION UNITS. COAL, LIMESTONE, SORBENT AND ASH HANDLING PROCESSES. VARIOUS BACT LIMITS FOR OPACITY, PM AND PM10. BACT FOR THE MATERIAL HANDLING EQUIPMENT CONSISTED OF A COMBINATION OF PASSIVE CONTROL EQUIPMENT SUCH AS WET/CHEMICAL SUPPRESSION SYSTEMS AND ENCLOSED CONVEYORS; AND ACTIVE CONTROL SUCH AS FABRIC FILTERS. ACTIVE CONTROL IS LIMITED TO 0.004 GR/DSCF. | AUXILARY BOILER | 12.31 | NATURAL GAS | 220 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER | 0.018 | LB/MMBTU | 30-DAY ROLLING | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | EMISSION LIMIT EQUALS 15 PPM.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUAUXBOILER (Auxiliary Boiler) | 12.31 | natural gas | 182 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 182 MMBTU/H fuel heat input. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low NOx burners/Flue gas recirculation and good combustion practices. | 0.04 | LB/MMBTU | 30 DAY ROLLING AVG TIME PERIOD | BACT-PSD | NSPS , SIP | N | 70 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Selective catalytic reduction (SCR) is greater than $10,000/ton for NOx.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUAUXBOILER (Auxiliary boiler) | 12.31 | Natural gas | 182 | MMBTU/H | A natural gas fired auxiliary boiler, rated at 182 MMBTU/H to provide auxiliary steam when the plant is off-line, used to maintain warm drums on the HRSG and maintain the steam turbine generator seals. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LNB that incorporate internal (within the burner) FGR and good combustion practices. | 0.04 | LB/MMBTU | 30 DAY ROLLING AVERAGE | BACT-PSD | SIP | N | 70 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit as required in 40 CFR 60.44b(l)(1) is 0.20 lb/MMBTU (expressed as NO2) at a high heat release rate. The emission limit above subsumes the NSPS emission limit. Selective catalytic reduction (SCR) is greater than $44,000/ton for NOx.
NM-0052 | ZIA II GAS PLANT | DCP MIDSTREAM L.P. | LEA | NM | 88255 | USA | JENNIFER HANNA | 4326205460 | JHANNA@DCPMIDSTREAM.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Joseph Kimbrell, 505-476-4300, joseph.kimbrell@state.nm.us | PSD-5217 | 1311 | 211111 | 110056438083 | 11/13/2013 &nbsp;ACT | 04/25/2014 &nbsp;ACT | 2015-11-19 | 2016-07-07 | A | https://www.env.nm.gov/aqb/ | Natural Gas Processing plant using cryogenic process and designed to operate at 230 MMscf/day of natural gas. | The permittee submitted an application on 5/13/2015 to revise the permit. Most BACT determinations will not change. | Industrial Sized Boilers/Furnaces &gt;100 mmBtu/hr | 12.31 | Natural gas | 114 | mmBtu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0 |  |  | BACT-PSD | NSPS , SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT PA15 | 12.31 | NATURAL GAS | 21 | MMBTU/H | UNIT PA15 IS A BRYAN BOILER AT PARIS CASINO RESORT. UNIT PA15 IS IDENTICAL TO UNIT PA16. UNIT PA14 IS A BRYAN BOILER RATED AT 17.0 MMBTU/HR. EACH OF THE THREE BOILERS IS SUBJECT TO THE LIMIT OF ANNUAL OPERATING TIME FOR 4,380 HOURS PER YEAR. THEY SHARE THE SAME BACT DETERMINATIONS ON THE PER MMBTU BASIS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER | 0.0366 | LB/MMBTU |  | BACT-PSD | NSPS , SIP , OPERATING PERMIT |  | 0 | Y | 30 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0366 | LB/MMBTU |  | 0 | 0 | N
OH-0310 | AMERICAN MUNICIPAL POWER GENERATING STATION | AMERICAN MUNICIPAL POWER | MEIGS | OH | 45771 | USA | RANDY MEYER | 6143376222 | RMEYER@AMP-OHIO.ORG | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104461 | 4911 | 221112 | 110000384325 | 05/15/2006 &nbsp;ACT | 10/08/2009 &nbsp;ACT | 2008-04-15 | 2009-11-06 | A |  | TWO 5191 MMBTU/HOUR PULVERIZED COAL-FIRED BOILERS; ONE 150 MMBTU/HOUR NATURAL GAS AUXILIARY BOILER, ONE FLY ASH AND GYPSUM LANDFILL, COAL STORAGE, CRUSHERS, FERTILIZER PLANT, LIMESTONE AND FLY ASH HANDLING EQUIPMENT, AND COOLING CELLS. ADMINISTRATIVE MODIFICATION 10/09 TO ADD CASE-BY-CASE MACT FOR BOILERS. 1ST ISSUED 2/7/08 AS PTI#06-08138; STILL INITIAL INSTALLATION | FUGITIVE EMISSIONS FROM STORAGE PILES (COAL,LIMESTONE, UREA), CONVEYING, HANDLING, ROADWAYS, BARGE OR TRUCK UNLOADING WERE NOT ENTERED INTO THE DATABASE DUE TO THE INSIGNIFICANT EMISSIONS (MOST < 1 TON FUGITIVE PM) AND LACK OF PROCESS CODES TO ENTER THEM. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 150 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 21 | LB/H |  | BACT-PSD | SIP | U | 0 | U | 9.2 | T/YR | PER ROLLING 12 MONTHS | 140 | LB/MMCF |  | 0 | 0 | N
OK-0126 | SUNOCO INC TULSA REFINERY | SUNOCO INC | TULSA | OK | 74107 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 98-014-C(M-14) PSD | 2911 | 324110 | 110000454981 | 12/04/2007 &nbsp;ACT | 05/27/2008 &nbsp;ACT | 2008-12-31 | 2009-04-20 | B |  | SUNOCO INCORPORATED (SUNOCO) OWNS AND OPERATES A PETROLEUM REFINERY (SIC 2911, NAICS 32411) IN TULSA, OKLAHOMA (THE TULSA REFINERY). | SUNOCO IS PROPOSING TO CONSTRUCT A DIESEL HYDROTREATING UNIT (DHT) FOR THE PRODUCTION OF ULTRA LOW SULFUR DIESEL (ULSD). | PROCESS HEATER | 12.31 | REFINERY FUEL GAS | 44 | MMBTU/H | THE DIESEL HYDROTREATING UNIT (DHT) WILL CONSIST OF A STANDARD, SINGLE COLD SEPARATOR DESIGN UNIT. THE MAJORITY OF THE ENERGY REQUIRED TO HEAT THE FEED STREAM IN ORDER TO INITIATE THE DESULFURIZATION REACTION WILL BE PROVIDED BY RECOVERY OF THE HEAT OF REACTION IN A SERIES OF FEED-EFFLUENT EXCHANGERS. AN ADDITIONAL AMOUNT OF FEED PREHEAT WILL BE PROVIDED BY A 44.0 MMBTU/H CHARGE HEATER. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | ULTRA LOW-NOX BURNERS | 0.03 | LB/MMBTU | 3 HOUR AVERAGE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0126 | SUNOCO INC TULSA REFINERY | SUNOCO INC | TULSA | OK | 74107 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 98-014-C(M-14) PSD | 2911 | 324110 | 110000454981 | 12/04/2007 &nbsp;ACT | 05/27/2008 &nbsp;ACT | 2008-12-31 | 2009-04-20 | B |  | SUNOCO INCORPORATED (SUNOCO) OWNS AND OPERATES A PETROLEUM REFINERY (SIC 2911, NAICS 32411) IN TULSA, OKLAHOMA (THE TULSA REFINERY). | SUNOCO IS PROPOSING TO CONSTRUCT A DIESEL HYDROTREATING UNIT (DHT) FOR THE PRODUCTION OF ULTRA LOW SULFUR DIESEL (ULSD). | PROCESS HEATER | 12.31 | REFINERY FUEL GAS/NATURAL GAS | 53.7 | MMBTU/H | THE HYDROTREATED DIESEL FROM THE DHT UNIT WILL BE PROCESSED IN A NEW FRACTIONATION COLUMN WHERE H2S GAS AND LIGHT HCS WILL BE STRIPPED FROM THE DIESEL. THE STRIPPER COLUMN WILL HAVE A 53.7 MMBTU/H PROCESS HEATER, AND STRIPPING STEAM WILL BE USED FOR VAPOR LIFT. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | ULTRA LOW-NOX BURNERS | 0.03 | LB/MMBTU | 3 HOUR AVERAGE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | MR. RANDY THOMPSON | (615) 532-6825 | randall.thompson@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000370535 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Two Natural Gas-Fired Auxiliary Boilers | 12.31 | Natural Gas | 450 | MMBtu/hr | Two 450 MMBtu/hr natural gas-fired auxiliary boilers will provide steam generation during threshold transitional periods and during malfunction events when the CT and HRSG are not able to operate. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Good combustion design and practices, selective catalytic reduction (SCR), low-NOX burners with flue gas recirculation | 0.013 | LB/MMBTU |  | BACT-PSD | NSPS | N | 90 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0641 | PINECREST ENERGY CENTER | PINECREST ENERGY CENTER LLC | ANGELINA | TX |  | USA | KATHLEEN SMITH | 281-253-4385 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | PSDTX1298 | 4911 |  |  | 06/22/2012 &nbsp;ACT | 11/12/2013 &nbsp;ACT | 2013-11-21 | 2017-11-17 | A |  | Combinec Cycle Electric Generating Plant | 103839 | Auxiliary boiler | 12.31 | natural gas | 150 | MMBTU/H | limited to 876 hours per year of operation | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | low NOx burners | 16 | PPMVD | INITIAL STACK TEST, 3% OXYGEN | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0708 | LA PALOMA ENERGY CENTER | LA PALOMA ENERGY CENTER, LLC | CAMERON | TX |  | USA | GARY NEUS | (281) 682-8448 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 101542 PSDTX1288 | 4911 | 221112 | unknown | 03/15/2012 &nbsp;ACT | 02/07/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is a new electric power plant, fueled by pipeline quality natural gas. The design of the plant is standard combined cycle (CC) technology. |  | boiler | 12.31 | natural gas | 150 | MMBTU/H | annual usage limitation to 876 hours per year | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | low-NOx burners, limited use | 0.02 | LB/MMBTU | 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0712 | TRINIDAD GENERATING FACILITY | SOUTHERN POWER COMPANY | HENDERSON | TX |  | USA | KELLI MCCULLOUGH | (205) 257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tzvi Shalem 512-239-1310 tzvi.shalem@tceq.texas.gov | 111393 PSDTX1368 | 4911 | 221112 | 110007199735 | 06/27/2013 &nbsp;ACT | 11/20/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | Southern Power Company (SPC) is proposing to construct an electric generating facility near Trinidad, Henderson County, Texas. The Trinidad Generating Facility (TGF) will include a natural gas-fired combined cycle combustion turbine generator (CTG) equipped with heat recovery steam generator (HRSG) and duct burners (DB). |  | boiler | 12.31 | natural gas | 110 | MMBTU/H | limited to a maximum annual operation of 1,500 hours | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | ultra-low NOx burners, limited use | 9 | PPMVD | @15% O2 | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0731 | CORPUS CHRISTI TERMINAL CONDENSATE SPLITTER | MAGELLAN PROCESSING LP | NUECES | TX |  | USA | SHAHANA BANOO | 918-574-7767 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, 512-239-1284, jesse.lovegren@tceq.texas.gov | 118270 AND PSDTX1398 | 2911 | 324110 | 110017840782 | 02/19/2015 &nbsp;ACT | 04/10/2015 &nbsp;ACT | 2015-04-14 | 2016-05-16 | B |  | 100 MBpd topping refinery |  | Industrial-Size Boilers/Furnaces | 12.31 | natural gas | 0 |  | (2) 129 Million British Thermal Units per hour (MMBtu/hr) direct-fired process heaters and (2) 106 MMBtu/hr thermal fluid heaters (one pair for each train) | Nitrogen Oxides (NOx) | Other - 40 CFR Pt. 60, Appendices B, F | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective catalytic reduction (SCR) | 0.006 | LB/MMBTU | 12-MONTH AVG | BACT-PSD |  | N | 0 | U | 0.01 | LB/MMBTU | BLOCK 1-HR AVG | 0 |  |  | 0 | 0 | N
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Auxiliary Boiler | 12.31 | Natural Gas | 100 | mmBtu/hr | Limited to 2,000 hours of operation per year. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Ultra Low-NOx Burners, Flue-Gas Recirculation, & Good Combustion Practices | 2 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0.02 | LB/MMBTU |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | AMMONIA CATALYST STARTUP HEATER | 12.39 | NATURAL GAS | 106.3 | MMBTU/H | ANNUAL NATURAL GAS USAGE LIMITED TO 20.84 MMCF. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | NATURAL GAS COMBUSTION ONLY, PROPER DESIGN AND GOOD COMBUSTION PRACTICES | 183.7 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE TYPICALLY CONSIDERED NOT FEASIBLE FOR LIMITED USE EMISSION UNITS.
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, VACUUM DEGASSER | 13.29 | NATURAL GAS | 51.2 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE LOW NOX BURNERS | 0.035 | LB/MMBTU | 3 HR | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACE, ANNEALING PICKLING LINE | 13.29 | NATURAL GAS | 66 | MMBTU/H | ANNEALING PICKLING LINE FURNACE SN-47; ANNEALING COATING LINE FURNACE , SN 51; | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNERS SCR COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.1 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | Sigma Thermal Auxiliary Heater (1) | 13.31 | Natural Gas | 12.5 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners and Flue Gas Recirculation | 32 | LB/MMSCF | 3-HOUR AVERAGE | BACT-PSD |  | U | 60 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Cost analysis not conducted since cost was not a factor in BACT determination. Proposed BACT limit lowered from poposed uncontrolled limit to controlled emission limit due to addition of LNB/FGR.
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Waste Heat Boilers | 13.31 | Natural Gas | 50 | MMBTU/H | Five (5) Natural Gas-Fired 50 MMBtu/hr Waste Heat Boilers. Installed in 1986. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 7 | PPMV | 3-HR AVG @ 15 % O2 | BACT-PSD |  | U | 81 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, PICKLE LINE | 13.31 | NATURAL GAS | 67 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.035 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILERS SN-26 AND 27, GALVANIZING LINE | 13.31 | NATURAL GAS | 24.5 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.035 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS SCR COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.1 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER EU-002 | 13.31 | NATURAL GAS | 70 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICES | 12.611 | LB/H | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 200 | H/YR |  | 0 |  |  | 0 | 0 | N | 2016 | SHALL COMBUST NATURAL GAS
LA-0229 | SHINTECH PLAQUEMINE PLANT 2 | SHINTECH LOUISIANA LLC | IBERVILLE | LA | 70764 | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-731 | 2821 | 325211 | UNKNOWN | 11/19/2010 &nbsp;ACT | 07/10/2008 &nbsp;ACT | 2009-04-02 | 2009-04-20 | B |  | A PROPOSED 1.81 BILLION LBS/YR PVC PRODUCTION COMPLEX WHICH WILL CONSIST OF A CHLORALKALI PLANT, AN EDC/VCM PLANT, AND A PVC PLANT | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | EQT122-EQT125 - FOUR VCM CRACKING FURNACES | 13.31 | NATURAL GAS | 90 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS (LNB) IN COMBINATION WITH SELECTIVE CATALYTIC REDUCTION (SCR) | 0.009 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0244 | LAKE CHARLES CHEMICAL COMPLEX - LAB UNIT | SASOL NORTH AMERICA, INC. | CALCASIEU | LA | 70669 | USA | MAGGIE PAGELS | 337-494-5769 | MARGARET.PAGELS@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225) 219-3395 | PSD-LA-291(M3) | 2869 | 325110 | 110017418061 | 09/17/2009 &nbsp;ACT | 11/29/2010 &nbsp;ACT | 2011-03-29 | 2011-07-06 | C |  | Chemical Production Unit for Linear Alkyl Benzene (LAB)production. | Modification to an existing PSD Permit (PSD-LA-291(M2), dated October 18, 1988) to increase operating time of the heater. Emissions will not be increased above the permitted limits. Existing BACT will not be revised. | EQT0027 - PACOL CHARGE HEATER H-201 | 13.31 | Natural Gas | 87.3 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low NOX Burners | 7.15 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT was determined in 1983
LA-0244 | LAKE CHARLES CHEMICAL COMPLEX - LAB UNIT | SASOL NORTH AMERICA, INC. | CALCASIEU | LA | 70669 | USA | MAGGIE PAGELS | 337-494-5769 | MARGARET.PAGELS@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225) 219-3395 | PSD-LA-291(M3) | 2869 | 325110 | 110017418061 | 09/17/2009 &nbsp;ACT | 11/29/2010 &nbsp;ACT | 2011-03-29 | 2011-07-06 | C |  | Chemical Production Unit for Linear Alkyl Benzene (LAB)production. | Modification to an existing PSD Permit (PSD-LA-291(M2), dated October 18, 1988) to increase operating time of the heater. Emissions will not be increased above the permitted limits. Existing BACT will not be revised. | EQT0028 - PACOL STARTUP HEATER H-202 | 13.31 | natural gas | 21 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | low nox burners | 2.71 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 | % OPACITY |  | 0 |  |  | 0 | 0 | N |  | BACT was determined in 1983
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Regenerative Heaters | 13.31 | natural gas | 7.37 | mm btu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGFUELHTR (Two fuel pre-heaters identified as EUFUELHTR1 &amp; EUFUELHTR2) | 13.31 | Natural gas | 27 | MMBTU/H | Two natural gas fired dew point heaters for warming the natural gas fuel (EUFUELHTR1 & EUFUELHTR2 in flexible group FGFUELHTR). The total combined heat input during operation shall not exceed 27 MMBTU/H (each) as well. The CO2e limit is for both units combined; however the other limits are per unit. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices. | 2.65 | LB/H | HOURLY; EACH UNIT | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit of 2.65 lb/hr is for each unit. SCR and low NOx burners are each greater than $18,000/ton for NOx, factoring in the redundancy of the heaters (limited operation).
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT FL01 | 13.31 | NATURAL GAS | 14.34 | MMBTU/H | UNIT FL01 IS A JOHNSTON BOILER AT FLAMINGO LAS VEGAS. THIS UNIT MAY OPERATE 8,760 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER AND FLUE GAS RECIRCULATION | 0.0353 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 29 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0353 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | SMALL INTERNAL COMBUSTION ENGINE (&lt;600 HP) - UNIT FL12 | 13.31 | DIESEL OIL | 536 | HP | UNIT FL12 IS A DETROIT DIESEL GENERATOR AT FLAMINGO LAS VEGAS. LIKE ALL THE OTHER DIESEL GENERATORS, THE UNIT IS SUBJECT TO THE LIMIT OF MONTHLY AND ANNUAL OPERATING TIMES FOR 2 HOURS PER MONTH AND 36 HOURS PER YEAR RESPECTIVELY. EMISSION FACTORS LISTED IN AP-42 ARE USED TO CALCULATE THE EMISSION LIMITS FOR EACH AND EVERY DIESEL GENERATOR IN THIS MAJOR STATIONARY SOURCE, AND ARE NOT REPEATED FURTHER FOR REPORTING THE BACT DETERMINATIONS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | THE UNIT IS EQUIPPED WITH A TURBOCHARGER. | 0.031 | LB/HP-H |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 16.62 | LB/H |  | 0.031 | LB/HP-H |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT BA01 | 13.31 | NATURAL GAS | 16.8 | MMBTU/H | UNIT BA01 IS A KEWANEE BOILER AT BALLY'S LAS VEGAS. UNIT BA01 IS IDENTICAL TO UNIT BA02. THE TWO BOILERS ARE SUBJECT TO THE ANNUAL LIMIT OF COMBINED TOTAL OPERATING TIME FOR 10,900 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOX BURNER AND BLUE GAS RECIRCULATION | 0.03 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 25 | PPMVD | CORRECTED TO 3% OXYGEN | 0.03 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT BA03 | 13.31 | NATURAL GAS | 31.38 | MMBTU/H | UNIT BA03 IS A KIWANEE BOLER AT BALLY'S LAS VEGAS. THE ANNUAL OPERATING TIME IS LIMITED TO 2,920 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOX BURNER | 0.0306 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 25 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0306 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP01 | 13.31 | NATURAL GAS | 35.4 | MMBTU/H | UNIT CP01 IS A HURST BOILER AT CAESAR'S PALACE. UNIT CP01 IS IDENTICAL TO UNIT CP02. UNITS CP01 THROUGH CP05 (FIVE BOILERS) ARE SUBJECT TO THE ANNUAL LIMIT OF TOTAL OPERATING TIME FOR 33,520 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER | 0.035 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 29 | PPMVD | CORRECTED TO 3% OXYGEN | 0.035 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP03 | 13.31 | NATURAL GAS | 33.48 | MMBTU/H | UNIT CP03 IS A BURNHAM BOILER AT CAESAR'S PALACE. UNITS CP01 THROUGH CP05 (FIVE BOILERS) ARE SUBJECT TO THE ANNUAL LIMIT OF TOTAL OPERATING TIME FOR 33,520 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER | 0.0367 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 30 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0367 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP26 | 13.31 | NATURAL GAS | 24 | MMBTU/H | UNIT CP26 IS A UNILUX BOILER AT CAESAR'S PALACE. THE UNIT IS ALLOWED TO OPERATE UP TO 8,760 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER | 0.0108 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 9 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0108 | LB/MMBTU |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Dryer Regenerator Heater - 005 | 13.39 | process fuel gas | 29 | mm btu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | good combustion practices; ULNB | 0.06 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Gas Turbines (8 units) | 15.11 | natural gas | 333 | mm btu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Dry Low NOX burners and good combustion practices | 25 | PPMVD | @15 %O2 | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | GE LM6000PF-25 Turbines (4) | 15.21 | Natural Gas | 59900 | hp ISO | Turbine-duct burner pairs exhaust through common stack | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction and Dry Low NOx Combustion | 5 | PPMDV | 4-HOUR AVERAGE | BACT-PSD |  | U | 90 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emission limit is for each turbine-duct burner pair due to common exhaust stack. BACT limit commences 70 minutes after startup. Cost analysis not conducted since cost was not a factor in BACT determination.
AK-0073 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION | ANCHORAGE | AK | 99518 | USA | GREGORY ARTHUR | 907 762 4492 |  | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Kwame Agyei, Permit Engineer, kwame.agyei@alaska.gov | AQ0164CPT01 | 4911 | 221112 | 110046491854 | 04/14/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2012-02-22 | 2014-01-08 | D |  | Power plant that contains four combustion turbines, four duct burners, a black start generator, and an auxiliary heater. |  | Fuel Combustion | 15.21 | Natural Gas | 59900 | HP | EU IDs 5-8 Combined Cycle Natural Gas-fired Combustion Turbines rated at 59,900 hp (44.7 MW) | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Turbines EU IDs 5 through 8 shall be equipped with Selective Catalytic Reduction and Dry Low NOx (SCR and DLN) combustors. SCR is a post-combustion gas treatment technique for reduction of nitric oxide (NO) and nitrogen dioxide (NO2) in the turbine exhaust stream to molecular nitrogen, water, and oxygen. This process is accomplished by using ammonia (NH3) as a reducing agent, and is injected into the flue gas upstream of the catalyst bed. By lowering the activation energy of the NOx decomposition removal efficiency of 80 to 90 percent are achievable. DLN combustors utilize multistage premix combustors where the air and fuel is mixed at a lean fuel to air ratio. The excess air in the lean mixture acts as a heat sink, which lowers peak combustion temperatures and also ensures a more homogeneous mixture, both resulting in greatly reduced NOx formation rates. DLN can reduce emissions by about 60% | 5 | PPM | 4-HOUR | BACT-PSD |  | U | 90 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Nitrogen Oxides (NOx) | Other - EPA METHOD 7E, OR METHOD 7E & 19 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW NOX (DLN) COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR) | 2 | PPMVD | @15% O2, 1-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (STARTUP PERIODS) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW NOX (DLN) COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR) | 96 | LB/EVENT | COLD STARTUP PERIODS | BACT-PSD |  | U | 0 | U | 40 | LB/EVENT | WARM & HOT STARTUP PERIODS | 0 |  |  | 0 | 0 | N |  | DURING STARTUP OR SHUTDOWN, EMISSIONS OF CO FROM BOTH CTGS COMBINED SHALL NOT EXCEED 790 LB/HR; DURATION OF COLD STARTUP NOT TO EXCEED 110 MIN; DURATION OF WARM & HOT STARTUP NOT TO EXCEED 80 MIN
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (SHUTDOWN PERIODS) | 15.21 | NATURAL GAS | 110 | MMBTU/H | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | DRY LOW NOX (DLN) COMBUSTORS, SELECTIVE CATALYTIC REDUCTION (SCR) | 57 | LB/EVENT | SHUTDOWN PERIODS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | DURING STARTUP OR SHUTDOWN, EMISSIONS OF CO FROM BOTH CTGS COMBINED SHALL NOT EXCEED 790 LB/HR; SHUTDOWN NOT TO EXCEED 30 MIN
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (selective catalytic reduction with dry low NOx burners) | 38.1 | LB/H | 24-H ROLLING AVERAGE | BACT-PSD | NSPS , SIP | N | 80 | N | 286 | LB/H | OPERATING HR DURING STARTUP OR SHUTDOWN | 0 |  |  | 0 | 0 | N |  | There are 4 emission limits (2 in the table above) with are for EACH CTGHRSG. They are as follows: Emission Limit 1 = 3 ppmvd at 15%O2 based on a 24-H rolling avg as determined each operating hour except during startup and shutdown. Emission Limit 2 = 15 ppmvd at 15%O2 based on a 30-day rolling avg as determined each operating day. (NSPS KKKK). Emission Limit 3 = 38.1 LB/H based on a 24-H rolling avg as determined during each operating hour except during startup and shutdown. Emission Limit 4 = 286 LB/H based on an operating hour during startup or shutdown. Startup and shutdown operations are limited to 500 hours per 12-month rolling time period for each CTGHRSG train. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the startup and shutdown emission minimization plan. The efficiency range is 80-90 percent.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective catalytic reduction with dry low NOx burners). | 3 | PPM | 24-H ROLL.AVG., EXCEPT STARTUP/SHUTDOWN | BACT-PSD | NSPS , SIP | N | 0 | N | 21.4 | LB/H | 24-H ROLL.AVG., EXCEPT STARTUP/SHUTDOWN | 0 |  |  | 0 | 0 | N |  | There are 3 separate NOx emission limits which do not include startup/shutdown events. Those will be entered as a separate 'Process' in the RBLC determination. Emission limit 1 above is 3 ppmvd at 15% O2 based on a 24-hour rolling average as determined each operating hour and does not include startup/shutdown. Emission Limit 2 above is 21.4 LB/H based on a 24-hour rolling average as determined each operating hour, except startup/shutdown. There is a third emission limit, which is not above, and is 15 ppm at 15% O2 and is based on a 30-day rolling average as determined each operating day. Table 1 of 40 CFR Part 60 Subpart KKKK allows 96 ppm at 15 percent 02 when the turbines are operating at less than 75 percent of peak load or at temperatures less than 0 deg. F.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Startup/Shutdown) | 15.21 | Natural gas | 1934.7 | MMBTU/H | This emission unit is being entered as a separate process to account for the emission limits associated with startup/shutdown events, which could not be included within the previous EUCCT original process name. A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR with DLNB (Selective catalytic reduction with dry low NOx burners). | 32 | POUNDS | PER EVENT | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit is 32 pounds per event and applies at each startup or shutdown event. Startup is defined as the period of time from initiation of the combustion process (flame-on) and continues until the unit reaches 50% load. Shutdown is defined as that period of time from the lowering of the turbine output below 50% load, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated.
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | MR. RANDY THOMPSON | (615) 532-6825 | randall.thompson@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000370535 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Natural Gas-Fired Combustion Turbine with HRSG | 15.21 | Natural Gas | 1339 | MMBtu/hr | Turbine throughput is 1019.7 MMBtu/hr when burning natural gas and 1083.7 MMBtu/hr when burning No. 2 oil. Duct burner throughput is 319.3 MMBtu/hr. Duct burner firing will occur during natural gas combustion only. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Good combustion design and practices, selective catalytic reduction (SCR) | 2 | PPMVD @ 15% O2 | 30 UNIT-OPERATING-DAY MOVING AVERAGE | BACT-PSD | NSPS | N | 90 | U | 8 | PPMVD @ 15% O2 | 15 UNIT-OPERATING-DAY MOVING AVERAGE | 0 |  |  | 0 | 0 | N |  | Emission limit #1 is for natural gas combustion, emission limit #2 is for No. 2 oil combustion.
*TX-0641 | PINECREST ENERGY CENTER | PINECREST ENERGY CENTER LLC | ANGELINA | TX |  | USA | KATHLEEN SMITH | 281-253-4385 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | PSDTX1298 | 4911 |  |  | 06/22/2012 &nbsp;ACT | 11/12/2013 &nbsp;ACT | 2013-11-21 | 2017-11-17 | A |  | Combinec Cycle Electric Generating Plant | 103839 | combined cycle turbine | 15.21 | natural gas | 700 | MW | The generating equipment consists of two natural gas-fired combustion turbines (CTs), each exhausting to a fired heat recovery steam generator (HRSG) to produce steam to drive a shared steam turbine generator. The steam turbine is rated at 271 MW of electric output. Three models of combustion turbines are being considered for this site: the General Electric 7FA.05, the Siemens SGT6-5000F(4), and the Siemens SGT6-5000F(5). The final selection of the combustion turbine will not be made until after the permit is issued. Plant output will range between 637 and 735 MW, depending on the model turbine selected. Duct Burners are rated at 750 MMBtu/hr each. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | selective catalytic reduction | 2 | PPMVD | 24-HR ROLLING AVG, 15% OXYGEN | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Combustion Turbine | 15.21 | natural gas | 87 | MW | The exhaust heat from the turbine will be used to heat a heating medium which is used to regenerate rich amine from the acid gas removal system. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 2 | PPMVD | 15@ O2, 3 HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The turbine is fuelad by what is technically natural gas but contains enough nitrogen to affect the Wobbe Index of the turbine fuel gas compared to typical pipeline gas.
TX-0708 | LA PALOMA ENERGY CENTER | LA PALOMA ENERGY CENTER, LLC | CAMERON | TX |  | USA | GARY NEUS | (281) 682-8448 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 101542 PSDTX1288 | 4911 | 221112 | unknown | 03/15/2012 &nbsp;ACT | 02/07/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is a new electric power plant, fueled by pipeline quality natural gas. The design of the plant is standard combined cycle (CC) technology. |  | (2) combined cycle turbines | 15.21 | natural gas | 650 | MW | The specific equipment includes two combustion turbines (CTs) connected to electric generators, producing between 183 and 232 MW of electricity, depending on ambient temperature and the selected CT. The two HRSGs use duct burners rated at 750 MMBtu/hr each to supplement the heat energy from the CTs. The steam from the two HRSGs is combined and routed to a single steam turbine driving a third electric generator with an electricity output capacity of 271 MW. Depending on the selected CT, total plant output at 59Â°F is between 637 MW and 735 MW. The applicant is considering three models of CT; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) Siemens SGT6-5000F(4); or (3) Siemens SGT6-5000F(5). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 2 | PPMVD | @15% O2, 24-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0712 | TRINIDAD GENERATING FACILITY | SOUTHERN POWER COMPANY | HENDERSON | TX |  | USA | KELLI MCCULLOUGH | (205) 257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tzvi Shalem 512-239-1310 tzvi.shalem@tceq.texas.gov | 111393 PSDTX1368 | 4911 | 221112 | 110007199735 | 06/27/2013 &nbsp;ACT | 11/20/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | Southern Power Company (SPC) is proposing to construct an electric generating facility near Trinidad, Henderson County, Texas. The Trinidad Generating Facility (TGF) will include a natural gas-fired combined cycle combustion turbine generator (CTG) equipped with heat recovery steam generator (HRSG) and duct burners (DB). |  | combined cycle turbine | 15.21 | natural gas | 497 | MW | The facility will consist of a Mitsubishi Heavy Industries (MHI) J model gas fired combustion turbine nominally rated at 497 megawatts (MW) equipped with a HRSG and DB with a maximum design capacity of 402 million British thermal units per hour (MMBtu/hr). The gross nominal output of the CTG with HRSG and DB is 530 MW. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 2 | PPMVD | @15% O2, 24-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 7 ppm ammonia slip limit
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Combined Cycle Turbine/Duct Burner | 15.21 | Natural Gas | 2419.61 | mmBtu/Hr | This entry is for both of two identical units at the facility. Nominal 197 mW General Electric Frame 7FA.04 Turbine w/ Duct Burner - throughput denotes aggregate heat input of turbine and duct burner (HHV). | Nitrogen Oxides (NOx) | Other - CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR & Dry Low-NOx Burners | 15.2 | LB/H |  | BACT-PSD | NSPS | U | 80 | U | 0 |  |  | 2 | PPM | @ 15% O2 | 0 | 0 | N |  | NOx emissions are applicable with and without duct firing.
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Natural Gas Fired Combustion Turbines | 16.11 | Natural Gas | 37.6 | MMBTU/H | Five (5) Natural Gas-Fired Solar Combustion Turbines rated at 37.6 MMBtu/hr each. Installed in 1976. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 7 | PPMV | 3-HR AVG @ 15 % O2 | BACT-PSD |  | U | 80 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | TURBINE GENERATORS - UNITS CC007 AND CC008 AT CITY CENTER | 16.11 | NATURAL GAS | 4.6 | MMBTU/H | THE TWO UNITS ARE IDENTICAL SOLAR MERCURY COMBUSTION GAS TURBINES FOR ELECTRIC POWER GENERATION. EACH UNIT IS RATED AT 4.6 MMBTU/HR, AND IS ALLOWED TO OPERATE 24 HOURS/DAY AND 8,760 HOURS/YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LEAN PRE-MIX TECHNOLOGY AND LIMITING THE FUEL TO NATURAL GAS ONLY | 0.178 | LB/MMBTU |  | BACT-PSD | NSPS , SIP , OPERATING PERMIT |  | 0 | N | 5 | PPMVD | CORRECTED TO 15% OXYGEN | 0.178 | LB/MMBTU |  | 0 | 0 | N
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | Caterpillar 3215C Black Start Generator (1) | 17.11 | ULSD | 1500 | KW-e |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Turbocharger and Aftercooler | 6.4 | G/KW-H | INSTANTANEOUS | BACT-PSD |  | U | 35 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Cost analysis not conducted since cost was not a factor in BACT determination. BACT limit set to NSPS limit since limit proposed by Chugach Electric Association was higher than NSPS.
AK-0073 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION | ANCHORAGE | AK | 99518 | USA | GREGORY ARTHUR | 907 762 4492 |  | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Kwame Agyei, Permit Engineer, kwame.agyei@alaska.gov | AQ0164CPT01 | 4911 | 221112 | 110046491854 | 04/14/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2012-02-22 | 2014-01-08 | D |  | Power plant that contains four combustion turbines, four duct burners, a black start generator, and an auxiliary heater. |  | Fuel Combustion | 17.11 | Diesel | 1500 | kW-e | EU 13 Black Start Engine | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Black Start diesel fired engine EU 13 shall be equipped with turbo charging and after cooling. The turbo charger reduces NOx emissions by boosting the pressure and temperature of the air entering the engine allowing more fuel to be added to increase power output. This translates into higher combustion efficiency and reduced emissions. | 6.4 | G/KW-H |  | BACT-PSD | NSPS | U | 35 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.11 | DIESEL | 2683 | HP | UNIT IS 2000 KW. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 6.4 | G/KW-H | 3-HR AVG | BACT-PSD |  | U | 0 | U | 4.8 | G/HP-H | 3-HR AVG | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Emergency Generator | 17.11 | diesel fuel | 142 | GAL/H | rated @ 2,000 KW | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | good combustion practices | 6 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 6.61 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | 2 MW EMERGENCY GENERATOR, SRC25 | 17.11 | ASTM #1, 2, DIESEL | 2000 | KW | LIMITED TO 100 H/YR FOR ROUTINE TESTING AND MAINTENANCE | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N | GOOD COMBUSTION PRACTICES. EPA CERTIFIED PER NSPS IIII | 0 |  |  | BACT-PSD | NSPS | Y | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | 500 KW EMERGENCY GENERATOR, FIRE PUMP, SRC26 | 17.11 | ASTM #1, 2, DIESEL | 500 | KW | LIMITED TO 100 H/YR FOR ROUTINE TESTING AND MAINTENANCE | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N | GOOD COMBUSTION PRACTICES. EPA CERTIFICATION PER NSPS IIII. | 0 |  | SEE NOTE | BACT-PSD | NSPS | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Emergency Generator | 17.11 | distillate fuel oil | 3755 | HP |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 0.67 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY GENERATOR | 17.11 | NO. 2 FUEL OIL | 4690 | B-HP | ANNUAL HOURS OF OPERATION NOT TO EXCEED 200 HOURS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICES | 4.46 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | EMERGENCY GENERATORS (EU014A AND EU-014B) | 17.11 | DISTILLATE OIL | 3600 | HP EACH |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICES | 4.42 | G/HP-H EACH | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 500 | H/YR EACH |  | 0 |  |  | 0 | 0 | N | 2016
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Diesel Engines | 17.11 | Diesel | 0 |  | Water Pumps (2 units) = 355 hp Tank Deluge Pumps (2 units) = 800 hp Generator = 1340 hp | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | good combustion practices, Use ultra low sulfur diesel, and comply with 40 CFR 60 Subpart IIII | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUEMENGINE (Diesel fuel emergency engine) | 17.11 | Diesel Fuel | 22.68 | MMBTU/H | a 2,922 horsepower (HP) (2,179 kilowatts (kW)) diesel fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Restricted to 4 hours/day, except during emergency conditions and stack testing, and 500 hours/year on a 12-month rolling time period basis. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices and meeting NSPS IIII requirements. | 6.4 | G/KW-H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is actually in &lsquo;&lsquo;NMHC + NOx&lsquo;&lsquo; (nonmethane hydrocarbon plus NOx), which is what is required in the NSPS.
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | LARGE INTERNAL COMBUSTION ENGINES (&gt;600 HP) - UNIT HA13 | 17.11 | DIESEL OIL | 1232 | HP | UNIT HA13 IS A MARATHON DIESEL GENERATOR AT HARRAH'S LAS VEGAS. ALL THE SEVEN (7) DIESEL GENERATORS AT HARRAH'S LAS VEGAS ARE FOR EMERGENCY USE ONLY. EACH ONE OF THEM IS SUBJECT TO THE SAME LIMIT OF OPERATING TIME FOR 2 HOURS PER DAY AND 36 HOURS PER YEAR. THE EMISSION LIMITS ARE CALCULATED BASED ON THE EMISSION FACTORS TAKEN FROM AP-42. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | THE UNIT IS EQUIPPED WITH A TURBOCHARGER. | 0.024 | LB/HP-H |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 29.57 | LB/H |  | 0.024 | LB/HP-H |  | 0 | 0 | N
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Emergency Generator | 17.11 | Diesel | 2015.7 | HP | Nominal 1,500 kW. Limited to 100 hours/year. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 4.8 | G/HP-HR | NMHC + NOX | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Diesel Fired Well Pump | 17.21 | Diesel | 2.7 | MMBTU/H | 2.7 MMBtu/hr Diesel Fired Well Pump. Installed in 1966. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Limited Operation of 168 hr/yr. | 4.41 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.21 | DIESEL | 182 | HP | UNIT IS 135 KW. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 4 | G/KW-H | 3-HR AVG | BACT-PSD |  | U | 0 | U | 3 | G/HP-H | 3-HR AVG | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | good combustion practices | 3.75 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.49 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 3.5 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICES | 2.86 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel Firewater pump engines (6 units) | 17.21 | diesel | 425 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel emergency generator engine - EGEN | 17.21 | diesel | 350 | hp |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices and meeting NSPS Subpart IIII requirements. | 3 | G/BHP-H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The limit is actually in &lsquo;&lsquo;NMHC + NOx&lsquo;&lsquo; (nonmethane hydrocarbon plus NOx), which is what is required in the NSPS.
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Fire Pump Engine | 17.21 | Diesel | 251 | HP | Limited to 100 Hours/year. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 3 | G/HP-HR | NMHC + NOX | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Gasoline Fired Fire Pump Engine | 17.22 | Gasoline | 2.1 | MMBTU/H | 2.1 MMBtu/hr Gasoline-Fired Fire Pump Engine. Installed in 1978. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Limited Operation of 168 hr/yr. | 1.63 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | SMALL HEATERS AND DRYERS SN-05 THROUGH 19 | 17.23 | NATURAL GAS | 0 |  | RH VESSEL PREHEATER STATION, VESSEL TOP PART DRYER, RH VESSEL NOZZLE DRYER RH DEGASSER BURNER/LANCE LADLE PREHEATERS LADLE DRYOUT STATION VERTICAL LADLE HOLDING STATION TUNDISH PREHEATERS #1 THROUGH #4 | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.08 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0229 | SHINTECH PLAQUEMINE PLANT 2 | SHINTECH LOUISIANA LLC | IBERVILLE | LA | 70764 | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-731 | 2821 | 325211 | UNKNOWN | 11/19/2010 &nbsp;ACT | 07/10/2008 &nbsp;ACT | 2009-04-02 | 2009-04-20 | B |  | A PROPOSED 1.81 BILLION LBS/YR PVC PRODUCTION COMPLEX WHICH WILL CONSIST OF A CHLORALKALI PLANT, AN EDC/VCM PLANT, AND A PVC PLANT | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | EQT126, EQT127 - TWO THERMAL OXIDIZERS (2M-5, 2M-6) | 19.2 | NATURAL GAS | 72 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICES | 0.02 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OK-0126 | SUNOCO INC TULSA REFINERY | SUNOCO INC | TULSA | OK | 74107 | USA |  |  |  | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 98-014-C(M-14) PSD | 2911 | 324110 | 110000454981 | 12/04/2007 &nbsp;ACT | 05/27/2008 &nbsp;ACT | 2008-12-31 | 2009-04-20 | B |  | SUNOCO INCORPORATED (SUNOCO) OWNS AND OPERATES A PETROLEUM REFINERY (SIC 2911, NAICS 32411) IN TULSA, OKLAHOMA (THE TULSA REFINERY). | SUNOCO IS PROPOSING TO CONSTRUCT A DIESEL HYDROTREATING UNIT (DHT) FOR THE PRODUCTION OF ULTRA LOW SULFUR DIESEL (ULSD). | SRU COMBUSTION UNIT | 19.2 | NATURAL GAS | 7.2 | MMBTU/H | THE PROJECT WILL CONSTRUCT AN SRU WITH A DESIGN CAPACITY OF 20.1 LONG TONS PER DAY (LTPD) AND ASSOCIATED TAIL GAS TREATMENT UNIT (TGTU). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION | 0.14 | LB/MMBTU | 3 HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 1 | LB/H | 3 HOUR AVERAGE | 0 |  |  | 0 | 0 | N |  | THE SRU WILL USE STANDARD CLAUS CATALYST IN THE REACTORS. OFFGAS FROM THE SRU WILL BE ROUTED TO THE TGTU WHICH WILL USE STANDARD HYDROTREATING CATALYST FOR THE HYDROGENATION REACTION. THE REDUCED GASES FROM THE TGTU WILL BE CIRCULATED BACK TO THE SRU FOR ELEMENTAL SULFUR RECOVERY. THE TAIL-GAS TREATMENT AND RECIRCULATION BACK TO THE SRU WILL GUARANTEE SULFUR RECOVERY EFFICIENCY OF AT LEAST 99.8%. OFFGAS FROM THE TGTU WILL BE OXIDIZED TO SO2 IN AN INTEGRATED NATURAL GAS-FIRED INCINERATOR. THE SRU/TGTU EXHAUST WILL BE VENTED INTO THE ATMOSPHERE THROUGH A COMMON STACK.
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Three (3) Flares | 19.31 | Natural Gas | 1.25 | MMBTU/H | 1.25 MMBtu/hr Ammonia Tank Flare, 0.4 MMBtu/hr Emergency Flare, and 1.25 MMBtu/hr Small Flare | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Work Practice Requirements and Limited Use (limit venting to 168 hr/yr each during startup, shutdown, and maintenance events) | 0.068 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT AMMONIA VENT FLARE | 19.31 | NATURAL GAS | 0.26 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICE | 792.03 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 6.9 | T/YR | ROLLING 12 MONTH AVERAGE | 0.098 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT PROCESS SSM FLARE | 19.31 | NATURAL GAS | 0.05 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICE | 0.093 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.41 | T/YR | ROLLING 12 MONTH AVERAGE | 0.098 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA STORAGE FLARE | 19.31 | NATURAL GAS | 0.05 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD AND EFFICIENT OPERATING PRACTICES | 10.02 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 43.88 | T/YR | ROLLING 12 MONTH AVERAGE | 0.098 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Ammonia Flare | 19.31 | natural gas | 0.4 | MMBTU/H | There are four (4) natural gas pilots | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | work practice/good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | There is no numeric emission limit in the permit.
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | GASIFIER FLARE, SRC16 | 19.31 | SWEET SYNGAS | 900000 | LB/H | FLARING DURING STARUP AND UPSETS. SYNGAS CLEANUP PRIOR TO FLARING - GASIFIER QUENCH, SOUR WATER SCRUB, ACTIVATED CARBON BEDS (MIN 95% HG REMOVAL), AMINE SCRUB (MIN 95% S REMOVAL AS SO2). 1.5 MMBTU/HR NAT GAS PILOT. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N | GOOD COMBUSTION PRACTICES. MEET 40 CFR 60.18. | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | PROCESS FLARE, SRC21 | 19.31 | PROCESS & PURGE GASES |  |  | PROCESS & PURGE GASES FROM 2000 T/D AMMONIA PLANT AND 2400 T/D UREA PLANT (LIQUID SOLUTION). 1.5 MMBTU/HR NAT GAS PILOT. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N | GOOD COMBUSTION PRACTICES. MEET 40 CFR 60.18. | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | AMMONIA STORAGE FLARE, SRC27 | 19.31 | AMMONIA |  |  | 0.75 MMBTU/H NAT GAS PILOT. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N | GOOD COMBUSTION PRACTICES. MEET 40 CFR 60.18. | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | FRONT END PROCESS FLARE | 19.31 | NATURAL GAS PILOT | 0.25 | MMBTU/H | HEAT INPUT IS FOR NATURAL GAS PILOT ONLY. SSM EMISSIONS ARE CONTROLLED BY THE FLARE AND ARE LIMITED TO 336 HOURS OF VENTING PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.068 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 595.47 | LB/H, SSM VENTING | 3-HR AVERAGE | 0 |  |  | 0 | 0 | N |  | SSM VENTING HOURS LIMITED TO 336 PER YEAR.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | BACK END AMMONIA FLARE | 19.31 | NATURAL GAS | 0.25 | MMBTU/H | HEAT INPUT IS FOR PILOT ONLY. SSM EMISSIONS ARE CONTROLLED BY THE FLARE AND ARE LIMITED TO 336 HR/YR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.068 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 624.94 | LB/H, SSM EVENTS | 3-HR AVERAGE | 0 |  |  | 0 | 0 | N |  | SSM EVENTS LIMITED TO 336 HRS PER YEAR
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | AMMONIA STORAGE FLARE | 19.31 | NATURAL GAS | 0.13 | MMBTU/H | HEAT INPUT IS FOR PILOT ONLY. SSM EVENTS HAVE SEPARATE LIMITS. SSM VENTING IS LIMITED TO 168 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.068 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 125 | LB/H, SSM VENTING | 3-HR AVERAGE | 0 |  |  | 0 | 0 | N |  | SSM VENTING IS LIMITED TO 168 HR PER YEAR.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | UAN PLANT VENT FLARE | 19.31 |  | 0.19 | MMBTU/H | HEAT INPUT IS FOR NATUAL GAS PILOT. SSM EMISSIONS HAVE SEPARATE LIMITS. SSM VENTING LIMITED TO 336 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.068 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 332.08 | LB/H, SSM VENTING | 3-HR AVERAGE | 0 |  |  | 0 | 0 | N |  | SSM VENTING LIMITED TO 336 HR PER YEAR.
LA-0244 | LAKE CHARLES CHEMICAL COMPLEX - LAB UNIT | SASOL NORTH AMERICA, INC. | CALCASIEU | LA | 70669 | USA | MAGGIE PAGELS | 337-494-5769 | MARGARET.PAGELS@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225) 219-3395 | PSD-LA-291(M3) | 2869 | 325110 | 110017418061 | 09/17/2009 &nbsp;ACT | 11/29/2010 &nbsp;ACT | 2011-03-29 | 2011-07-06 | C |  | Chemical Production Unit for Linear Alkyl Benzene (LAB)production. | Modification to an existing PSD Permit (PSD-LA-291(M2), dated October 18, 1988) to increase operating time of the heater. Emissions will not be increased above the permitted limits. Existing BACT will not be revised. | EQT0026 - LAB Unit Flare LF-1 | 19.31 | Natural Gas | 0 |  |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Steam Assisted | 10.23 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT was determined in 1983
LA-0275 | LINEAR ALKYL BENZENE (LAB) UNIT | SASOL CHEMICALS (USA) LLC | CALCASIEU | LA | 70669 | USA | ERIC RODRIGUEZ | 281-588-3761 | ERIC.RODRIGUEZ@SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Dan Nguyen, (225) 219-3395 | PSD-LA-291(M4) | 2865 | 325110 | 110017418061 | 10/06/2015 &nbsp;ACT | 04/29/2016 &nbsp;ACT | 2016-06-23 | 2017-04-28 | C |  | LAB production unit, PSD-LA-291(M2) issued October 18, 1998 - PSD-LA-291(M3) issued November 29, 2010. Permit PSD-LA-291(M4) for emission limits revision, No BACT change. |  | LF-1 - LAB Unit Flare | 19.31 | Natural Gas | 0 |  |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Steam assisted | 10.15 | LBS/HR | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Flare No. 1 - 008 | 19.31 | natural gas | 85097 | MM BTU/yr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | complying with 40 CFR 60.18; good combustion practices (including establishment of flare minimization practices) | 0.068 | LB/MM BTU |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Pyrolysis Gasoline Tank Flare - 009 | 19.31 | natural gas | 0.66 | mm btu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | complying with 40 CFR 60.18 and 63.11; good combustion practices (including establishment of flare minimization practices) | 0.068 | LB/MM BTU |  | BACT-PSD | NESHAP , NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | vessel evacuation flare - 018 | 19.31 | natural gas | 3.04 | mm btu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | good combustion practices (including establishment of flare minimization practices) | 0.068 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NM-0052 | ZIA II GAS PLANT | DCP MIDSTREAM L.P. | LEA | NM | 88255 | USA | JENNIFER HANNA | 4326205460 | JHANNA@DCPMIDSTREAM.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Joseph Kimbrell, 505-476-4300, joseph.kimbrell@state.nm.us | PSD-5217 | 1311 | 211111 | 110056438083 | 11/13/2013 &nbsp;ACT | 04/25/2014 &nbsp;ACT | 2015-11-19 | 2016-07-07 | A | https://www.env.nm.gov/aqb/ | Natural Gas Processing plant using cryogenic process and designed to operate at 230 MMscf/day of natural gas. | The permittee submitted an application on 5/13/2015 to revise the permit. Most BACT determinations will not change. | Units FL1 &amp; FL2: Refinery Flares (Inlet Gas Flare &amp; Acid Gas Flare) | 19.33 | natural gas, acid gas | 2.3 | mmBtu/hr | Only for routine or predictable Startup, Shutdown, or Maintenance of units controlled by Flares (Blowdown/Venting, Amine Unit-Acid Gas Injection well maintenance) | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | NOx, CO, PM10, PM2.5, SO2 controlled through Good Combustion Practices (GCP), pipeline quality natural gas for pilot; limits on flaring events. VOC & CO2e controlled through GCP, limits on flaring and meet 40 CFR 60.18. | 695.2 | PPH |  | BACT-PSD | NSPS , SIP , OPERATING PERMIT | N | 98 | U | 101.6 | PPH |  | 0 |  |  | 0 | 0 | N |  | The 2 emissions limits represent limits for Units FL1 and FL2.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | AMMONIA STORAGE FLARE (EU-016) | 19.39 | NATURAL GAS | 1.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 125 | LB/H | WHILE VENTING 3 HOUR AVG. | BACT-PSD |  | N | 0 |  | 0.068 | LB/MMBTU | DURING NORMAL OP. 3 HR AVG. | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS USED SHALL BE NATURAL GAS LIMIT 4: 168 HOURS / 12 CONSECUTIVE MONTH PERIOD LIMIT 5: COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUT DOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUTDOWN. THIS ANALYSIS SHALL IDENTFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 6: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MINS DURING ANY 2 CONSEC. HRS.; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMACOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FRONT END FLARE EU-017 | 19.39 | NATURAL GAS | 1.12 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.068 | LB/MMBTU | NORMAL OPS. 3 HR AVG. | BACT-PSD |  | N | 0 |  | 595.49 | LB/H | VENTING OPS. 3 HR AVG. | 0 |  |  | 0 | 0 | N |  | LIMIT 3: PILOT AND PURGE GAS FUELS USED SHALL BE NATURAL GAS LIMIT 4: COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUTDOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ROOT CAUSE ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DUING ANY 2 CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMOCOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE. LIMIT 6: SHALL NOT EXCEED 336 HRS PER 12 CONSECUTIVE MONTH PERIOD WITH COMPLIANCE DETERMINED AT END OF EACH MONTH.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | BACK END FLARE (EU-018) | 19.39 | NATURAL GAS | 1.12 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.068 | LB/MMBTU | NORMAL OPS. 3 HR AVG. | BACT-PSD |  | N | 0 |  | 624.94 | LB/H | VENTING OPS. 3 HR AVG. | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS USED SHALL BE NATURAL GAS LIMIT 4: COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUTDOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ROOT CAUSE ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DUING ANY 2 CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMOCOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE. LIMIT 6: SHALL NOT EXCEED 336 HOURS PER 12 CONSECUTIVE MONTH PERIOD WITH COMPLIANCE DETERMINED AT END OF EACH MONTH.
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | flares | 19.39 | natural gas | 7.33 | kg/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | AUXILIARY HEATER | 19.6 | NATURAL GAS | 40 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 9 | PPMVD | @3% O2, 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | GASIFIER HEATERS (2), 25 MMBTU/H, SRC14 &amp; SRC15 | 19.6 | NAT GAS | 25 | MMBTU/H | BOTH HEATERS AT APPROX 25 MMBTU/H FOR STARTUP. NORMAL OPS ONE HEATER OFF, ONE ON STANDBY AT 9 MMBTU/H. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N | GOOD COMBUSTION PRACTICES. | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAIILABLE
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | ASU REGEN HEATER, 0.1 MMBTU/H, SRC13 | 19.6 | NAT GAS | 0.1 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N | GOOD COMBUSTION PRACTICES | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EMERGENCY GENERATOR SN-62 | 19.8 | DIESEL | 625 | HP |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD OPERATING PRACTICES, LIMITED HOURS OF OPERATION, COMPLIANCE WITH NSPS SUBPART IIII | 0.4 | G/KW-H |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Thermal oxidizers (2 units) | 50.008 | natural gas | 21 | mm btu/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low NOX Burners | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT PRIMARY REFORMER | 61.012 | NATURAL GAS | 1400 | T/D AMMONIA | 824 MMBTU/HR | Nitrogen Oxides (NOx) | Other - | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SELECTIVE CATALYTIC REDUCTION (SCR) | 0.0124 | LB/MMBTU | ROLLING 30 DAY AVERAGE | BACT-PSD | SIP , OTHER | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | CEMS TO VERIFY COMPLIANCE THIS LIMIT WAS ASSIGNED BY THE ADMINISTRATIVE LAW JUDGE AND LATER APPROVED BY THE ARKANSAS POLLUTION CONTROL AND ECOLOGY COMMISSION. THE ORIGINAL LIMIT AS PROPOSED BY THE FACILITY WAS 0.0124 LB/MMBTU (ROLLING 3 HOUR AVERAGE).
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Primary Reformer | 61.012 | natural gas | 1.13 | million cubic feet/h |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction (SCR) | 9 | PPMV | 30 DAY ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 56 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Ammonia Plant, Flares | 61.012 | natural gas | 2789 | tpd |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.07 | LB/MMBTU PILOT |  | BACT-PSD |  | U | 0 | U | 15.1 | TPY |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Reformer Furnace | 61.012 | natural gas | 955 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low-NOx burners, SCR | 0.0109 | LB/MMBTU | 30-DAY AVERAGE ROLLED DAILY | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Ammonia Pressure Tanks | 61.012 |  | 0 |  |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Flare; flare minimization; nitrogen as purge gas | 0.07 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 12.8 | TPY |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | PRIMARY REFORMER | 61.012 | NATURAL GAS | 1006.4 | MMBTU/H | NOX CEMS | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SELECTIVE CATALYTIC REDUCTION (SCR) AND GOOD COMBUSTION PRACTICES | 9 | PPMVD | 30 DAY ROLLING AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NOX CEMS
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | DM WEATHERLY NITRIC ACID PLANT # 2 | 62.014 |  | 1265 | T/D | 461,725 TON/YR OF 100% HNO3 | Nitrogen Oxides (NOx) | Other - | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SELECTIVE CATALYTIC REDUCTION (SCR) | 0.064 | LB/TON | 30 DAY ROLLING AVERAGE EXCLUDING SSM | BACT-PSD | NSPS , SIP , OTHER | N | 0 | N | 17.76 | T/YR | ROLLING 12 MONTH TOTAL INCLUDING SSM | 0 |  |  | 0 | 0 | N |  | CEMS TO VERIFY COMPLIANCE THIS SOURCE CONTAINS THE FOLLOWING INTERIM LIMITS DURING THE FIRST 12 MONTHS OF OPERATION AS ASSIGNED BY THE ADMINISTRATIVE LAW JUDGE AND APPROVED BY THE ARKANSAS POLLUTION CONTROL AND ECOLOGY COMMISSION: 0.32 LB/TON EXCLUDING SSM (30 DAY ROLLING AVERAGE) 25 PPMV
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Nitric Acid Plant | 62.014 |  | 1905 | metric tons/day |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | De-NOx system | 5 | PPMV | ROLLING 30 DAY AVERAGE | BACT-PSD |  | U | 0 | U | 30 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Nitric Acid Storage Tank | 62.014 |  | 0 |  | The maximum storage capacity of the tank is 1,935,773 gallons | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Acid/Water Vent Lock | 0.72 | TONS/YR | ROLLING 12 MONTH TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | NITRIC ACID PLANT TAILGAS, SRC20 | 62.014 |  | 575 | T/D |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR, AMMONIA SLIP MAX 10 PPMV (DRY) CONVERTED TO 15% O2. | 50 | PPMV |  | BACT-PSD | NSPS | Y | 98 | Y | 1.12 | LB/T |  | 10 | % |  | 0 | 0 | N |  | AT 575 T/D OF 57% ACID, PMT LIMIT IS 15.3 LB/H - (100% ACID/57% ACID) X 15.3 X 24 LB/DAY/ 575 TPD = 1.12 LB/TON OF 100% ACID.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | TWO (2) NITRIC ACID UNITS | 62.014 |  | 630 | TONS NITRIC ACID/DAY, EACH | COMBINED NITRIC ACID PRODUCTION FROM BOTH PLANTS IS LIMITED TO 459,900 TONS OF 100% NITRIC ACID PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SELECTIVE CATALYTIC REDUCTION (SCR) | 0.5 | LB/TON 100% ACID | 30 DAY AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | SELEXOL AGR CO2 VENT, SRC17 | 64.003 |  |  |  | CO2-RICH STREAM FROM ACID GAS REMOVAL (AGR) UNIT. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | GOOD COMBUSTION PRACTICES FOR THERMAL OXIDIZER (CAT-OX) USED TO CONTROL CO EMISSIONS. | 0.9 | LB/H |  | BACT-PSD |  | Y | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NOX EMISSIONS BASED ON 9 MMBTU/H NAT GAS BURNER ASSOCIATED WITH THE T.O/CAT-OX
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Modular Ethylene Cracking Furnaces - 001 | 64.003 | natural gas/fuel gas | 1028 | MM BTU/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | good combustion practices; fueled by natural gas or process fuel gas; LNB + SCR | 0.01 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Ethylene Cracking Furnace - 015 | 64.003 | natural gas/fuel gas | 168 | mm btu |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LNB, good combustion practices, fueled by natural gas and/or fuel gas | 0.098 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EAFS SN-01 AND SN-02 | 81.21 | NATURAL GAS | 0 |  |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.3 | LB/TON |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | LMFS SN-01 AND SN-02 | 81.29 | NATURAL GAS | 0 |  |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0 |  |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | RH DEGASSER | 81.29 | NATURAL GAS | 0 |  |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 1 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-39, ANNEALING | 81.29 | NATURAL GAS | 98.25 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.1 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | ANNEALING COATING LINE FURNACE SECTION | 81.29 | NATURAL GAS | 50 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.1 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACE, SN-53, ANNEALING COATING LINE DRYING | 81.29 | NATURAL GAS | 38 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.1 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | DRYERS, MGO COATING LINE | 81.29 | NATURAL GAS | 38 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.1 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-58 AND 60, FINAL ANNEALING AND COATING LINE | 81.29 | NATURAL GAS | 32 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW NOX BURNERS SCR COMBUSTION OF CLEAN FUEL GOOD COMBUSTION PRACTICES | 0.1 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | 245 MMBtu natural gas fired Auxiliary boiler | 12.31 | Natural Gas | 1052 | MMscf/yr | Total fuel usage of the auxiliary boiler shall not exceed 1052 MMsch/yr on a 12-month rolling basis | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good combustion practices and ULNOx burners | 0.011 | LB/MMBTU |  | LAER | NSPS | U | 0 | U | 9 | PPMDV @ 15% O2 |  | 0 |  |  | 0 | 0 | N
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Heating Medium Heaters | 12.31 | natural gas | 130 | MMBTU/H | There are (5) heaters each at 130 MMBtu/hr which operate when the turbine exhaust is not providing enough heat for the amine regenrating heating oil system | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | ultra-low NOx burners | 5 | PPMVD | @3% O2, 1 HOUR BASED ON STACK TEST | LAER |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0682 | GALENA PARK TERMINAL | KM LIQUIDS TERMINALS LLC | HARRIS | TX |  | USA | NEAL NYGAARD | 832-239-8018 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ozden Tamer Phone: 512-239-4577 e-mail: ozden.tamer@tceq.texas.gov | 101199 & N158 | 4226 | 325110 | 110037844376 | 02/23/2012 &nbsp;ACT | 06/12/2013 &nbsp;ACT | 2015-03-17 | 2016-05-09 | B |  | Tank Terminal | This project is for a new 100,000 barrel per day condensate splitter that takes condensate from a pipeline and separates it into light naphtha, heavy naphtha, kerosene/distillate, residual and Y-grade products which are stored in tanks and loaded in marine vessels at existing docks at this tank terminal. Natural gas used at the facility will be sampled for sulfur every 6 months. | Heaters | 12.31 | Natural gas | 129 | MMBTU/H | Maximum firing rate of 129 MMBtu/hr and heaters will be equipped with ultra low NOx burners and SCR. Natural gas fired at the heaters are sampled for sulfur every 6 months . Heaters will be sampled for NOx, CO, PM. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | low-NOx burners and SCR | 0.01 | LB/MMBTU | HOURLY | LAER | NSPS , MACT | N | 0 | U | 0.006 | LB/MMBTU | ANNUAL | 0 |  |  | 0 | 0 | N |  | Fuel flow must be monitored continuously. NOx emissions are calculated using the fuel flow rate.
TX-0811 | LINEAR ALPHA OLEFINS PLANT | INEOS OLIGOMERS USA LLC | BRAZORIA | TX |  | USA | JOHN WALTER | 281-535-4224 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, PhD, 512-239-1284, jesse.lovegren@tceq.texas.gov | 136130 AND N250 | 2869 | 325110 | Not Found | 09/20/2016 &nbsp;ACT | 11/03/2016 &nbsp;ACT | 2016-10-06 | 2017-11-16 | B |  | Manufactures linear alpha olefins (LAO) from ethylene |  | Industrial-Sized Furnaces, Natural Gas-fired | 12.31 | natural gas | 217 | MM BTU / H | Thermal Fluid (â€œhot oilâ€) Heater, throughput based on higher heating value basis | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | Low-NOX burners and Selective Catalytic Reduction (SCR). Ammonia slip limited to 10 ppmv (corrected to 3% O2) on a 1-hr block average. | 0.006 | LB / MM BTU | HHV BASIS, ANNUAL AVERAGE | LAER | MACT , SIP | N | 0 | U | 0.014 | LB/MMBTU | HHV BASIS, 1-HR AVERAGE | 0 |  |  | 0 | 0 | N |  | MACT DDDDD, SIP MECT
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | Large combustion turbine | 15.21 | Natural Gas | 0 |  | This process entry is for operations with the duct burner. Limits entered are for each turbine. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR, DLN, and good combustion practice | 2 | PPMVD@15% O2 |  | LAER | NSPS | U | 0 | U | 26.5 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | At no time may a unit exceed 340 lb/hr from each combined cycle combustion turbine to ensure compliance with 1 hr NO2 NAAQS.
TX-0682 | GALENA PARK TERMINAL | KM LIQUIDS TERMINALS LLC | HARRIS | TX |  | USA | NEAL NYGAARD | 832-239-8018 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ozden Tamer Phone: 512-239-4577 e-mail: ozden.tamer@tceq.texas.gov | 101199 & N158 | 4226 | 325110 | 110037844376 | 02/23/2012 &nbsp;ACT | 06/12/2013 &nbsp;ACT | 2015-03-17 | 2016-05-09 | B |  | Tank Terminal | This project is for a new 100,000 barrel per day condensate splitter that takes condensate from a pipeline and separates it into light naphtha, heavy naphtha, kerosene/distillate, residual and Y-grade products which are stored in tanks and loaded in marine vessels at existing docks at this tank terminal. Natural gas used at the facility will be sampled for sulfur every 6 months. | Vapor Combustion Units | 19.9 |  | 0 |  | VCUs are open flame units and will achieve 99.8% DRE (destruction removal efficiency) | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | VCU's will not have add-on control. VCUs are designed to minimize VOC emissions from tanks and marine loading. | 0 |  |  | LAER | NSPS | U | 99.8 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0811 | LINEAR ALPHA OLEFINS PLANT | INEOS OLIGOMERS USA LLC | BRAZORIA | TX |  | USA | JOHN WALTER | 281-535-4224 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, PhD, 512-239-1284, jesse.lovegren@tceq.texas.gov | 136130 AND N250 | 2869 | 325110 | Not Found | 09/20/2016 &nbsp;ACT | 11/03/2016 &nbsp;ACT | 2016-10-06 | 2017-11-16 | B |  | Manufactures linear alpha olefins (LAO) from ethylene |  | Other Combustion | 19.9 |  | 0 |  | Collateral emissions from control devices (thermal oxidizer and vapor combustor) for truck, railcar and barge loading activities | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNERS | 0.06 | LB/MMBTU | HHV BASIS, ANNUAL AVERAGE | LAER | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | MECT
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Thermal Oxidizer | 50.002 | natural gas | 0 |  | There are 3 LNG trains and each train has a thermal oxidizer. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | low NOx burners | 0.06 | LB/MMBTU |  | LAER |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This applies only to the burners
TX-0682 | GALENA PARK TERMINAL | KM LIQUIDS TERMINALS LLC | HARRIS | TX |  | USA | NEAL NYGAARD | 832-239-8018 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ozden Tamer Phone: 512-239-4577 e-mail: ozden.tamer@tceq.texas.gov | 101199 & N158 | 4226 | 325110 | 110037844376 | 02/23/2012 &nbsp;ACT | 06/12/2013 &nbsp;ACT | 2015-03-17 | 2016-05-09 | B |  | Tank Terminal | This project is for a new 100,000 barrel per day condensate splitter that takes condensate from a pipeline and separates it into light naphtha, heavy naphtha, kerosene/distillate, residual and Y-grade products which are stored in tanks and loaded in marine vessels at existing docks at this tank terminal. Natural gas used at the facility will be sampled for sulfur every 6 months. | MSS-Heaters | 99.999 |  | 0 |  | Heaters are used to abate MSS emissions directed to them. Nox emission factor from the heaters will be 0.025 lb/MMBtu, during 8 hours at startup and 4 hours of shutdown. CO emissions will be limited to 100 pppmv from heaters during 8 hours at startup and 4 hours of shutdown. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | NOx emission factor will be 0.025 lb/MMbtu, during 8 hours at startup and 4 hours of shutdown NOx anual emission factor from heaters when they are abating MSS emissions will be 0.006 lb/MMBtu, annually | 0.025 | LB/MMBTU | DURING 8 HRS AT STARTUP AND 4 HRS OF SHU | LAER | NSPS , MACT | U | 0 | U | 0.006 | LB/MMBTU | ANNUALLY | 0 |  |  | 0 | 0 | N
OH-0354 | KRATON POLYMERS U.S. LLC | KRATON POLYMERS U.S. LLC | WASHINGTON | OH | 45714-0235 | USA | DALE LOUDERMILK | 740-423-2299 | DALE.LOUDERMILK@KRATON.CC | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0108853 | 2822 | 325212 | 110030900997 | 08/29/2012 &nbsp;ACT | 01/15/2013 &nbsp;ACT | 2013-09-27 | 2016-05-04 | B |  | Thermoplastic elastomer manufacturing facility | Two new 249 MMBtu/hour natural gas, distillate oil, and belpre naphtha-fired boilers installed to replace 2 existing coal, distillate oil, and belpre naphtha-fired boilers. | Two 249 MMBtu/H boilers | 12.31 | Natural Gas | 249 | MMBtu/H | Two boilers, burning natural gas or distillate oil w/ less than 0.05% sulfur; and co-fired with maximum of 54.8 MMBtu/H Belpre naphtha. Fitted with low-NOx burners with flue gas recirculation, as needed. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Low-NOx burners | 0.12 | LB/MMBTU | BURNING DISTILLATE OIL | N/A | NSPS , SIP | U | 0 | U | 392.83 | T/YR |  | 0.1 | LB/MMBTU | BURNING NATURAL GAS | 0 | 0 | N |  | 0.40 LB NOx/MMBtu/H when burning Belpre Naphtha. Subject to NSPS Subparts A and Db. Netted out for NOx by replacing old coal/oil-fired boilers.
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | AUXILIARY BOILER (1) AND FUEL GAS HEATERS (6) | 12.31 | NATURAL GAS | 185 | MMBTU/HR | The auxiliary boiler will provide steam to the steam turbine at startup and at cold starts to warm up the ST rotor. The steam from the auxiliary boiler will not be used to augment the power generation of the combustion turbines or steam turbine. The boiler is proposed to operate 8760 hrs/yr but will be limited by an annual fuel throughput based on a capacity factor of 10%. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | ultra low-NOâ€ž burners | 0.011 | LB/MMBTU |  | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | COMBUSTION TURBINE GENERATOR WITH DUCT-FIRED HEAT RECOVERY STEAM GENERATORS (3) | 15.21 | natural gas | 3227 | MMBTU/HR | 3227 MMBTU/HR CT with 500 MMBTU/HR Duct Burner, 3 on 1 configuration. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 20 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 2 | PPMVD | 1 HR AVG | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Turbine: 2.0 ppmvd @ 15% O2 (1-hour average)
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | DIESEL-FIRED EMERGENCY GENERATOR 3000 kW (1) | 17.11 | DIESEL FUEL | 0 |  |  | Nitrogen Oxides (NOx) | Other - NA | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good Combustion Practices/Maintenance | 6.4 | G/KW | PER HR | N/A |  | U | 0 | U | 10.6 | T/YR | 12 MO ROLLING TOTAL | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | DIESEL-FIRED WATER PUMP 376 bph (1) | 17.21 | DIESEL FUEL | 0 |  | FWP-1: 104.0 tons/year (12-month rolling total) | Nitrogen Oxides (NOx) | Other - NA | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good Combustion Practices/Maintenance | 0 |  |  | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | EMISSION LIMIT: 1 3.0 g/hp-hr NOx + NMHC (4.0 g/kW-hr NOx + NMHC)
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | PROPANE-FIRED EMERGENCY GENERATORS 150 kW (2) | 17.23 | PROPANE | 0 |  |  | Nitrogen Oxides (NOx) | Other - NA | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Good Combustion Practices/Maintenance | 2 | G/HP-H | HR | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MN-0076 | BLANDIN PAPER/RAPIDS ENERGY CENTER | BLANDIN PAPER COMPANY/MINNESOTA POWER | ITASCA | MN | 55744 | USA | NATHAN WAECH | 2183276269 |  | 5 | MN001 | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | MR. RICHARD CORDES | (651)757-2291 | RICHARD.CORDES@STATE.MN.US |  | 06100001-011 | 2621 | 322110 | 110000426290 | 08/16/2007 &nbsp;ACT | 09/18/2008 &nbsp;ACT | 2008-12-01 | 2009-02-10 | B |  | BLANDIN PAPER PRODUCES PAPER FOR ADVERTISING SUPPLEMENTS, CATALOGS, AND MAGAZINES. |  | BOILER | 12.31 | NATURAL GAS | 280 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | FLUE GAS RECIRCULATION WITH LOW-NOX BURNERS | 0.035 | LB/MMBTU | 24 HOUR ROLLING AVG | Other Case-by-Case | NSPS | Y | 73 | U | 0.2 | LB/MMBTU | 30 DAY ROLLING AVG | 0 |  |  | 0 | 0 | N
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | BOILERS - UNITS CC026, CC027 AND CC028 AT CITY CENTER | 12.31 | NATURAL GAS | 44 | MMBTU/H | THE THREE UNITS ARE IDENTICAL CATERPILLAR BOILERS, EACH RATED AT 44 MMBTU/HR. EACH UNIT IS SUBJECT TO THE ANNUAL LIMIT OF OPERATING TIME TO 5,800 HOURS. THE EMISSION LIMITS ARE BASED ON THE ATC PERMIT FOR MODIFICATION #13 DATED NOVEMBER 30, 2009. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER AND GOOD COMBUSTION PRACTICES | 0.0109 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT | N | 0 | N | 9 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0109 | LB/MMBTU |  | 0 | 0 | N
OH-0336 | CAMPBELL SOUP COMPANY | CAMPBELL SOUP COMPANY | HENRY | OH |  | USA | ANN CURNOW | 763-278-5932 | ANN.CURNOW@HDRIC.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0106678 | 2032 | 311422 | 110041176679 | 07/28/2010 &nbsp;ACT | 12/14/2010 &nbsp;ACT | 2011-03-31 | 2011-10-13 | B |  | Canned food maufacturing facility. | Replacing 5 natural gas boilers with 3 new ones. Facility is a Major PSD facility for SO2, NOx, PE, and CO. This permit is PSD for CO. Five old natural gas steam boilers will be decommissioned upon the installation of the 3 new ones. The boilers will burn natural gas and use #2 fuel oil as backup. The facility took a restriction on the #2 fuel oil used to avoid PSD on all but the CO. The boilers are used for steam production for process lines and cogeneration for building heat. | Boilers (3) | 12.31 | Natural Gas | 0 |  | The natural gas throughput is unknown; the limits are based on the potential of 8760 hours of operation. Boilers used for cogeneration of heat to facility. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.04 | LB/MMBTU | BASED ON MFG. GUARANTEE | OTHER CASE-BY-CASE | OPERATING PERMIT | U | 0 | U | 63.08 | T/YR | ROLLING 12 MO. FROM 3 BOILERS TOGETHER | 0 |  |  | 0 | 0 | N
PA-0267 | CRAFTMASTER MFG INC | CRAFTMASTER MFG INC | BRADFORD | PA | 188480311 | USA | MICHAEL STEELE | 5702688737 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 08-00003F | 2493 | 321219 | 110037965057 | &nbsp; | 07/29/2008 &nbsp;ACT | 2009-07-15 | 2009-07-28 | B |  | FACILITY INSTALLED 2 RTO'S FOR THE LINE I &amp; II REFINERS AND DRYERS. THEY WERE SUBJECT TO THE MACT DDDD AND THOUGH VOC EMISSIONS DECREASED WITH THE RTO'S, THE ADDED COMBUSTION TRIPPED NSR FOR NOX. REQUIRED TO BUY ERC'S AT A RATIO OF 1.15:1. |  | RTO 2 | 12.31 | NG AND PROPANE | 12300 | CF/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 85 | PPMVD | @3% | Other Case-by-Case |  | U | 0 | U | 5.6 | T/YR |  | 0 |  |  | 0 | 0 | N |  | NSR
PA-0267 | CRAFTMASTER MFG INC | CRAFTMASTER MFG INC | BRADFORD | PA | 188480311 | USA | MICHAEL STEELE | 5702688737 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 08-00003F | 2493 | 321219 | 110037965057 | &nbsp; | 07/29/2008 &nbsp;ACT | 2009-07-15 | 2009-07-28 | B |  | FACILITY INSTALLED 2 RTO'S FOR THE LINE I &amp; II REFINERS AND DRYERS. THEY WERE SUBJECT TO THE MACT DDDD AND THOUGH VOC EMISSIONS DECREASED WITH THE RTO'S, THE ADDED COMBUSTION TRIPPED NSR FOR NOX. REQUIRED TO BUY ERC'S AT A RATIO OF 1.15:1. |  | RTO 1 | 12.31 | NG, PROPANE | 10.7 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N | IT IS A CONTROL DEVISE | 85 | PPMDV |  | Other Case-by-Case |  | U | 0 | U | 4.8 | T/YR |  | 0 |  |  | 0 | 0 | N |  | TRIPPED NSR ON AN ACCUMULLATION BASIS, OFFSETS
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | WATER HEATERS - UNITS NY037 AND NY038 AT NEW YORK - NEW YORK | 13.31 | NATURAL GAS | 2 | MMBTU/H | THE TWO UNITS ARE IDENTICAL RBI FUTURA III WATER HEATERS.THE EMISSION LIMITS REPORTED HEREIN ARE BASED ON THE ATC PERMIT FOR MODIFICATION #9 DATED SEPTEMBER 6, 2006. EACH UNIT IS ALLOWED TO OPERATE 24 HOURS/DAY AND 8,760 HOURS/YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOX BURNERS AND GOOD COMBUSTION PRACTICES | 0.025 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 20 | PPMVD | CORRECTED TO 3% OXYGEN | 0.025 | LB/MMBTU |  | 0 | 0 | N
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | EMERGENCY GENERATORS - UNITS LX024 AND LX025 AT LUXOR | 17.11 | DIESEL OIL | 2206 | HP | THE TWO UNITS ARE IDENTICAL CATERPILLAR GENERATORS MODEL 3512C. EACH UNIT HAS A FOUR-STROKE COMPRESSION-IGNITION ENGINE RATED AT 2,206 HORSE POWER (HP). THE EMISSION LIMITS REPORTED HEREIN ARE BASED ON THE ATC PERMIT FOR MODIFICATION #10 DATED SEPTEMBER 20, 2006. EACH UNIT IS ALLOWED TO OPERATE UP TO ONE HOUR PER DAY AND FIFTY TWO HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | TURBOCHARGING, AFTER-COOLING, AND LEAN-BURN TECHNOLOGY | 0.0131 | LB/HP-H |  | Other Case-by-Case | NSPS , SIP , OPERATING PERMIT |  | 0 | N | 28.98 | LB/H |  | 0.0131 | LB/HP-H |  | 0 | 0 | N |  | EMISSION LIMIT 2 APPLIES TO EACH UNIT.
OH-0310 | AMERICAN MUNICIPAL POWER GENERATING STATION | AMERICAN MUNICIPAL POWER | MEIGS | OH | 45771 | USA | RANDY MEYER | 6143376222 | RMEYER@AMP-OHIO.ORG | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104461 | 4911 | 221112 | 110000384325 | 05/15/2006 &nbsp;ACT | 10/08/2009 &nbsp;ACT | 2008-04-15 | 2009-11-06 | A |  | TWO 5191 MMBTU/HOUR PULVERIZED COAL-FIRED BOILERS; ONE 150 MMBTU/HOUR NATURAL GAS AUXILIARY BOILER, ONE FLY ASH AND GYPSUM LANDFILL, COAL STORAGE, CRUSHERS, FERTILIZER PLANT, LIMESTONE AND FLY ASH HANDLING EQUIPMENT, AND COOLING CELLS. ADMINISTRATIVE MODIFICATION 10/09 TO ADD CASE-BY-CASE MACT FOR BOILERS. 1ST ISSUED 2/7/08 AS PTI#06-08138; STILL INITIAL INSTALLATION | FUGITIVE EMISSIONS FROM STORAGE PILES (COAL,LIMESTONE, UREA), CONVEYING, HANDLING, ROADWAYS, BARGE OR TRUCK UNLOADING WERE NOT ENTERED INTO THE DATABASE DUE TO THE INSIGNIFICANT EMISSIONS (MOST < 1 TON FUGITIVE PM) AND LACK OF PROCESS CODES TO ENTER THEM. | FGD LANFILL | 29.9 |  | 807291 | T/ROLLING 12-MO | LANDFILL FOR COAL ASH DISPOSAL FOR FACILITY: GYPSUM, FLYASH AND BOTTOM ASH | Particulate Mater (PM), Fine Suspended | Unspecified | (Particulate Matter (PM)) | PM | P | BEST AVAILABLE MEASURES TO MINIMIZE FUGITIVE DUST: WATERING, COMPACTING, COVER | 1.84 | T/YR | PER ROLLING 12-MONTHS | BACT-PSD | SIP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | FUGITIVE PM10
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | 250 MMBTU/H STEAM SUPERHEATER BOILER, SRC31 | 12.3 | NAT GAS & PSA TAILGAS | 250 | MMBTU/H | OPERATED DURING STEADY-STATE PRODUCTION ON NATURAL GAS AND (HYDROGEN-RICH) PRESSURE SWING ADSORBER (PSA) TAILGAS. BALANCED WITH PACKAGE BOILER AT STARTUP/SHUTDOWN SO COMBINED HEAT INPUT <= 250 MMBTU/H. | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N | GOOD COMBUSTION PRACTICES | 0.0052 | LB/MMBTU |  | BACT-PSD | NSPS | Y | 0 |  | 1.3 | LB/H |  | 20 | % |  | 0 | 0 | N |  | LB/MMBTU AND LB/H LIMITS APPLY TO PACKAGE BOILER AND STEAM SUPERHEATER COMBINED EMISSIONS.
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | 250 MMBTU/H PACKAGE BOILER, SRC24 | 12.31 | NAT GAS | 250 | MMBTU/H | OPERATED ONLY DURING STARTUP AND SHUTDOWN, RAMPS DOWN/UP AS STEAM SUPERHEATER BOILER RAMPS UP/DOWN. COMBINED HEAT INPUT BALANCED <= 250 MMBTU/HR. | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.0052 | LB/MMBTU |  | BACT-PSD | NSPS | Y | 0 |  | 1.3 | LB/H |  | 20 | % |  | 0 | 0 | N |  | LB/MMBTU AND LB/H LIMITS APPLY TO PACKAGE BOILER AND STEAM SUPERHEATER COMBINED EMISSIONS.
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | 2 MW EMERGENCY GENERATOR, SRC25 | 17.11 | ASTM #1, 2, DIESEL | 2000 | KW | LIMITED TO 100 H/YR FOR ROUTINE TESTING AND MAINTENANCE | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | P | ULSD FUEL, GOOD COMBUSTION PRACTICES, EPA CERTIFIED PER NSPS IIII | 0 |  | SEE NOTE | BACT-PSD | NSPS , NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | VE PER NSPS SUBPART IIII. NO EMISSION LIMITS AVAILABLE
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | 500 KW EMERGENCY GENERATOR, FIRE PUMP, SRC26 | 17.11 | ASTM #1, 2, DIESEL | 500 | KW | LIMITED TO 100 H/YR FOR ROUTINE TESTING AND MAINTENANCE | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | P | ULSD FUEL, EPA CERTIFICATION PER NSPS IIII | 0 |  | SEE NOTE | BACT-PSD | NSPS | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | VE PER NSPS SUBPART IIII. NO EMISSION LIMITS AVAILABLE.
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | GASIFIER FLARE, SRC16 | 19.31 | SWEET SYNGAS | 900000 | LB/H | FLARING DURING STARUP AND UPSETS. SYNGAS CLEANUP PRIOR TO FLARING - GASIFIER QUENCH, SOUR WATER SCRUB, ACTIVATED CARBON BEDS (MIN 95% HG REMOVAL), AMINE SCRUB (MIN 95% S REMOVAL AS SO2). 1.5 MMBTU/HR NAT GAS PILOT. | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N | SMOKELESS FLARE. AIR OR STEAM-ASSIST ONLY IF UNASSISTED FLARE PRODUCES SMOKE. GOOD COMBUSTION PRACTICES. MEET 40 CFR 60.18. | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE. VE PER 40 CFR 60.18: NO VE AS DETERMINED BY METHOD 22, EXCEPT FOR TOTAL OF 5 MINS IN ANY 2-HR PERIOD. NO EMISSION LIMITS AVAILABLE
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | PROCESS FLARE, SRC21 | 19.31 | PROCESS & PURGE GASES |  |  | PROCESS & PURGE GASES FROM 2000 T/D AMMONIA PLANT AND 2400 T/D UREA PLANT (LIQUID SOLUTION). 1.5 MMBTU/HR NAT GAS PILOT. | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N | SMOKELESS FLARE. AIR OR STEAM-ASSIST ONLY IF UNASSISTED FLARE PRODUCES SMOKE. GOOD COMBUSTION PRACTICES. MEET 40 CFR 60.18. | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE. VE PER 40 CFR 60.18: NO VE AS DETERMINED BY METHOD 22, EXCEPT FOR TOTAL OF 5 MINS IN ANY 2-HR PERIOD. NO EMISSION LIMITS AVAILABLE
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | AMMONIA STORAGE FLARE, SRC27 | 19.31 | AMMONIA |  |  | 0.75 MMBTU/H NAT GAS PILOT. | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N | SMOKELESS FLARE. AIR OR STEAM-ASSIST ONLY IF UNASSISTED FLARE PRODUCES SMOKE. GOOD COMBUSTION PRACTICES. MEET 40 CFR 60.18. | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | VE PER 40 CFR 60.18: NO VE AS DETERMINED BY METHOD 22, EXCEPT FOR TOTAL OF 5 MINS IN ANY 2-HR PERIOD. NO EMISSION LIMITS AVAILABLE
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | GASIFIER HEATERS (2), 25 MMBTU/H, SRC14 &amp; SRC15 | 19.6 | NAT GAS | 25 | MMBTU/H | BOTH HEATERS AT APPROX 25 MMBTU/H FOR STARTUP. NORMAL OPS ONE HEATER OFF, ONE ON STANDBY AT 9 MMBTU/H. | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N | GOOD COMBUSTION PRACTICES | 20 | % |  | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | ASU REGEN HEATER, 0.1 MMBTU/H, SRC13 | 19.6 | NAT GAS | 0.1 | MMBTU/H |  | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N | GOOD COMBUSTION PRACTICES | 20 | % |  | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | UREA GRANULATION VENT, SRC19 | 61.012 |  | 1800 | T/D |  | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N | WET SCRUBBER IS INTEGRAL PART OF GRANULATION PROCESS, IS PROCESS EQUIPMENT. DESIGNED FOR MIN 98% CAPTURE AND RECYCLING OF PM/PM10. | 0.011 | LB/T |  | BACT-PSD |  | Y | 98 | N | 20.5 | LB/H |  | 20 | % |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | AMMONIUM NITRATE NEUTRALIZER VENT, SRC29 | 61.012 |  | 715 | T/D | AMMONIUM NITRATE/UAN PLANT PRODUCTION ~715 TPD AMMONIUM NITRATE AND ~1600 TPD UAN | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N | WET SCRUBBER IS INTEGRAL TO PROCESS. MUST BE DESIGNED TO CAPTURE AND RECYCLE 90% OF PM/PM10. | 1.5 | LB/H |  | BACT-PSD |  | Y | 0 | U | 20 | % |  | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | COAL/PETCOKE RAILCAR UNLOADING &amp; STORAGE, SRC01-SRC07 | 90.011 |  | 5000 | T/H | ENCLOSED RAILCAR UNLOADING AT NEGATIVE PRESSURE. COVERED CONVEYORS AND ENCLOSED TRANSFER POINTS. STORAGE IN EUROSILO OR EQUIVALENT. HIGH EFFICIENCY BAGHOUSES (RAILCAR UNLOADING, CONVEYORS, STORAGE SILO VENTS). | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | B | ENCLOSED RAILCAR UNLOADING AT NEGATIVE PRESSURE. COVERED CONVEYORS AND ENCLOSED TRANSFER POINTS. STORAGE IN EUROSILO OR EQUIVALENT. HIGH EFFICIENCY BAGHOUSES (RAILCAR UNLOADING, CONVEYORS, STORAGE SILO VENTS). | 0.09 | LB/H |  | BACT-PSD | NSPS | Y | 99 | N | 0.0009 | GR/DSCF |  | 5 | % |  | 0 | 0 | N |  | PMT LIMIT IS IN LB/H (APPROX. EQUIV TO GRAIN LOADING SHOWN AS EMISSION LIMIT 2). NSPS SUBPART Y: CURRENT OPACITY=20%, 2008 PROPOSED= 5%.
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | COAL/PETCOKE RECLAIM TO ROD MILL, SRC08-SRC12 | 90.011 |  | 105 | T/H | COVERED CONVEYORS WITH ENCLOSED TRANSFER POINTS. CAPACITY IS 105 T/H FOR EACH CONVEYOR. | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | B | COVERED CONVEYORS WITH ENCLOSED TRANSFER POINTS. HIGH EFFICIENCY BAGHOUSES. | 0.002 | LB/H |  | BACT-PSD | NSPS | Y | 99 | U | 0 | GR/DSCF | SEE NOTE | 5 | % |  | 0 | 0 | N |  | PMT LIMIT IS IN LB/H (APPROX EQUIV TO GRAIN LOADING SHOWN AS EMISSION LIMIT 2). NSPS SUBPART Y: CURRENT OPACITY=20%, 2008 PROPOSED= 5%.
OH-0310 | AMERICAN MUNICIPAL POWER GENERATING STATION | AMERICAN MUNICIPAL POWER | MEIGS | OH | 45771 | USA | RANDY MEYER | 6143376222 | RMEYER@AMP-OHIO.ORG | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104461 | 4911 | 221112 | 110000384325 | 05/15/2006 &nbsp;ACT | 10/08/2009 &nbsp;ACT | 2008-04-15 | 2009-11-06 | A |  | TWO 5191 MMBTU/HOUR PULVERIZED COAL-FIRED BOILERS; ONE 150 MMBTU/HOUR NATURAL GAS AUXILIARY BOILER, ONE FLY ASH AND GYPSUM LANDFILL, COAL STORAGE, CRUSHERS, FERTILIZER PLANT, LIMESTONE AND FLY ASH HANDLING EQUIPMENT, AND COOLING CELLS. ADMINISTRATIVE MODIFICATION 10/09 TO ADD CASE-BY-CASE MACT FOR BOILERS. 1ST ISSUED 2/7/08 AS PTI#06-08138; STILL INITIAL INSTALLATION | FUGITIVE EMISSIONS FROM STORAGE PILES (COAL,LIMESTONE, UREA), CONVEYING, HANDLING, ROADWAYS, BARGE OR TRUCK UNLOADING WERE NOT ENTERED INTO THE DATABASE DUE TO THE INSIGNIFICANT EMISSIONS (MOST < 1 TON FUGITIVE PM) AND LACK OF PROCESS CODES TO ENTER THEM. | COAL CONVEYING, HANDLING, AND CRUSHING | 90.011 |  | 5553840 | T/YR | CRUSHING TO PULVERIZE COAL, HANDLING, CONVEYING TO BOILERS | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 77.6 | LB/H | FROM BAGHOUSE EXHAUST | BACT-PSD | SIP | U | 0 | U | 9.8 | T/YR | PER ROLLING 12-MONTHS | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | FLUXANT TRUCK LDOUT &amp; CONVEYING, FUG | 90.019 |  | 250 | T/H | GASIFIER FLUXANT VARIES, BUT MAY INCLUDE LIMESTONE, IRON ORE OR SAND. | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N | COVERED CONVEYORS AND ENCLOSED TRANSFER POINTS. FUGITIVE DUST BMPS. | 20 | % |  | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | FLUXANT STORAGE, SRCXX | 90.019 |  | 250 | T/H | GASIFIER FLUXANT VARIES, BUT MAY INCLUDE LIMESTONE, IRON ORE, OR SAND. MAX FILL RATE PRESUMED TO BE 250 T/H. MAX USE RATE IN GASIFIER IS 250 T/D. | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | A | HIGH EFFICIENCY BAGHOUSE(S) ON STORAGE SILO VENT(S) | 0.002 | LB/H |  | BACT-PSD |  | Y | 99 | U | 0 | LB/T | SEE NOTE | 20 | % |  | 0 | 0 | N |  | PMT LIMIT IS LB/H (EQUIVALENT LB/T LIMIT IS SHOWN AS EMISSION LIMIT 2), BASED ON 250 T/H FILL RATE.
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | COOLING TOWER, SRC22 | 99.009 |  | 121000 | GAL/MIN | COOLING WATER FLOW RATE 121,000 GPM. TDS MAX 5000 MG/L. | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | A | DRIFT/MIST ELIMINATORS | 0.0005 | % OF TOTAL CIRC FLOW |  | BACT-PSD |  | Y | 0 |  | 1.5 | LB/H |  | 20 | % |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | ZLDS COOLING TOWER, SRC30 | 99.009 |  | 985 | GAL/MIN | ZERO LIQUID DISCHARGE SYSTEM - COOLING WATER FLOW RATE 985 GPM. TDS MAX 50,000 MG/L. | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | A | DRIFT/MIST ELIMINATORS | 0.001 | % OF TOTAL CIRC FLOW |  | BACT-PSD |  | Y | 0 |  | 0.3 | LB/H |  | 20 | % |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | SLAG HAND, FUG | 99.19 |  | 580 | T/D | GASIFIER SLAG IS WET WHEN CONVEYED TO STORAGE. | Particulate Matter (PM) | Unspecified | (Particulate Matter (PM)) | PM | N | STORAGE IN 3-SIDED BUNKER. FUGITIVE DUST BMPS. | 20 | % |  | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 | % |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | 250 MMBTU/H STEAM SUPERHEATER BOILER, SRC31 | 12.3 | NAT GAS & PSA TAILGAS | 250 | MMBTU/H | OPERATED DURING STEADY-STATE PRODUCTION ON NATURAL GAS AND (HYDROGEN-RICH) PRESSURE SWING ADSORBER (PSA) TAILGAS. BALANCED WITH PACKAGE BOILER AT STARTUP/SHUTDOWN SO COMBINED HEAT INPUT <= 250 MMBTU/H. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | GOOD COMBUSTION PRACTICES | 0.0052 | LB/MMBTU |  | BACT-PSD | NSPS | Y | 0 |  | 1.3 | LB/H |  | 0 |  |  | 0 | 0 | N |  | LB/MMBTU AND LB/H LIMITS APPLY TO PACKAGE BOILER AND STEAM SUPERHEATER COMBINED EMISSIONS.
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | 250 MMBTU/H PACKAGE BOILER, SRC24 | 12.31 | NAT GAS | 250 | MMBTU/H | OPERATED ONLY DURING STARTUP AND SHUTDOWN, RAMPS DOWN/UP AS STEAM SUPERHEATER BOILER RAMPS UP/DOWN. COMBINED HEAT INPUT BALANCED <= 250 MMBTU/HR. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.0052 | LB/MMBTU |  | BACT-PSD |  | Y | 0 |  | 1.3 | LB/H |  | 0 |  |  | 0 | 0 | N |  | LIMITS APPLY TO PACKAGE BOILER AND STEAM SUPERHEATER COMBINED EMISSIONS.
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT PA15 | 12.31 | NATURAL GAS | 21 | MMBTU/H | UNIT PA15 IS A BRYAN BOILER AT PARIS CASINO RESORT. UNIT PA15 IS IDENTICAL TO UNIT PA16. UNIT PA14 IS A BRYAN BOILER RATED AT 17.0 MMBTU/HR. EACH OF THE THREE BOILERS IS SUBJECT TO THE LIMIT OF ANNUAL OPERATING TIME FOR 4,380 HOURS PER YEAR. THEY SHARE THE SAME BACT DETERMINATIONS ON THE PER MMBTU BASIS. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | OPERATING IN ACCORDANCE WITH THE MANUFACTURER'S SPECIFICATION | 0.0076 | LB/MMBTU |  | BACT-PSD | NSPS , SIP , OPERATING PERMIT |  | 0 | Y | 0.16 | LB/H |  | 0.0076 | LB/MMBTU |  | 0 | 0 | N
OH-0310 | AMERICAN MUNICIPAL POWER GENERATING STATION | AMERICAN MUNICIPAL POWER | MEIGS | OH | 45771 | USA | RANDY MEYER | 6143376222 | RMEYER@AMP-OHIO.ORG | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104461 | 4911 | 221112 | 110000384325 | 05/15/2006 &nbsp;ACT | 10/08/2009 &nbsp;ACT | 2008-04-15 | 2009-11-06 | A |  | TWO 5191 MMBTU/HOUR PULVERIZED COAL-FIRED BOILERS; ONE 150 MMBTU/HOUR NATURAL GAS AUXILIARY BOILER, ONE FLY ASH AND GYPSUM LANDFILL, COAL STORAGE, CRUSHERS, FERTILIZER PLANT, LIMESTONE AND FLY ASH HANDLING EQUIPMENT, AND COOLING CELLS. ADMINISTRATIVE MODIFICATION 10/09 TO ADD CASE-BY-CASE MACT FOR BOILERS. 1ST ISSUED 2/7/08 AS PTI#06-08138; STILL INITIAL INSTALLATION | FUGITIVE EMISSIONS FROM STORAGE PILES (COAL,LIMESTONE, UREA), CONVEYING, HANDLING, ROADWAYS, BARGE OR TRUCK UNLOADING WERE NOT ENTERED INTO THE DATABASE DUE TO THE INSIGNIFICANT EMISSIONS (MOST < 1 TON FUGITIVE PM) AND LACK OF PROCESS CODES TO ENTER THEM. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 150 | MMBTU/H |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 1.14 | LB/H |  | BACT-PSD | SIP | U | 0 | U | 0.5 | T/YR | PER ROLLING 12-MONTHS | 7.6 | LB/MMCF |  | 0 | 0 | N
AK-0073 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION | ANCHORAGE | AK | 99518 | USA | GREGORY ARTHUR | 907 762 4492 |  | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Kwame Agyei, Permit Engineer, kwame.agyei@alaska.gov | AQ0164CPT01 | 4911 | 221112 | 110046491854 | 04/14/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2012-02-22 | 2014-01-08 | D |  | Power plant that contains four combustion turbines, four duct burners, a black start generator, and an auxiliary heater. |  | Fuel Combustion | 15.21 | Natural Gas | 59900 | HP | EU IDs 5-8 Combined Cycle Natural Gas-fired Combustion Turbines rated at 59,900 hp (44.7 MW) | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion Turbines EU IDs 5-8 use good combustion practices involve increasing the residence time and excess oxygen to ensure complete combustion which in turn minimize particulates without an add-on control technology. | 0.0066 | LB/MMBTU | 3-HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | 2 MW EMERGENCY GENERATOR, SRC25 | 17.11 | ASTM #1, 2, DIESEL | 2000 | KW | LIMITED TO 100 H/YR FOR ROUTINE TESTING AND MAINTENANCE | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | ULSD FUEL, GOOD COMBUSTION PRACTICES, EPA CERTIFIED PER NSPS IIII | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | 500 KW EMERGENCY GENERATOR, FIRE PUMP, SRC26 | 17.11 | ASTM #1, 2, DIESEL | 500 | KW | LIMITED TO 100 H/YR FOR ROUTINE TESTING AND MAINTENANCE | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | ULSD FUEL, EPA CERTIFICATION PER NSPS IIII | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITSAVAILABLE.
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | GASIFIER FLARE, SRC16 | 19.31 | SWEET SYNGAS | 900000 | LB/H | FLARING DURING STARUP AND UPSETS. SYNGAS CLEANUP PRIOR TO FLARING - GASIFIER QUENCH, SOUR WATER SCRUB, ACTIVATED CARBON BEDS (MIN 95% HG REMOVAL), AMINE SCRUB (MIN 95% S REMOVAL AS SO2). 1.5 MMBTU/HR NAT GAS PILOT. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | SMOKELESS FLARE. AIR OR STEAM-ASSIST ONLY IF UNASSISTED FLARE PRODUCES SMOKE. GOOD COMBUSTION PRACTICES. MEET 40 CFR 60.18. | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | PROCESS FLARE, SRC21 | 19.31 | PROCESS & PURGE GASES |  |  | PROCESS & PURGE GASES FROM 2000 T/D AMMONIA PLANT AND 2400 T/D UREA PLANT (LIQUID SOLUTION). 1.5 MMBTU/HR NAT GAS PILOT. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | SMOKELESS FLARE. AIR OR STEAM-ASSIST ONLY IF UNASSISTED FLARE PRODUCES SMOKE. GOOD COMBUSTION PRACTICES. MEET 40 CFR 60.18. | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | AMMONIA STORAGE FLARE, SRC27 | 19.31 | AMMONIA |  |  | 0.75 MMBTU/H NAT GAS PILOT. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | SMOKELESS FLARE. AIR OR STEAM-ASSIST ONLY IF UNASSISTED FLARE PRODUCES SMOKE. GOOD COMBUSTION PRACTICES. MEET 40 CFR 60.18. | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | GASIFIER HEATERS (2), 25 MMBTU/H, SRC14 &amp; SRC15 | 19.6 | NAT GAS | 25 | MMBTU/H | BOTH HEATERS AT APPROX 25 MMBTU/H FOR STARTUP. NORMAL OPS ONE HEATER OFF, ONE ON STANDBY AT 9 MMBTU/H. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | GOOD COMBUSTION PRACTICES | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | ASU REGEN HEATER, 0.1 MMBTU/H, SRC13 | 19.6 | NAT GAS | 0.1 | MMBTU/H |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | GOOD COMBUSTION PRACTICES | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | UREA GRANULATION VENT, SRC19 | 61.012 |  | 1800 | T/D |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | WET SCRUBBER IS INTEGRAL PART OF GRANULATION PROCESS, IS PROCESS EQUIPMENT. DESIGNED FOR MIN 98% CAPTURE AND RECYCLING OF PM/PM10. | 0.005 | LB/T |  | BACT-PSD |  | Y | 98 | N | 9 | LB/H |  | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | AMMONIUM NITRATE NEUTRALIZER VENT, SRC29 | 61.012 |  | 715 | T/D | AMMONIUM NITRATE/UAN PLANT PRODUCTION ~715 TPD AMMONIUM NITRATE AND ~1600 TPD UAN | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | WET SCRUBBER IS INTEGRAL TO PROCESS. MUST BE DESIGNED TO CAPTURE AND RECYCLE 90% OF PM/PM10. | 1.5 | LB/H |  | BACT-PSD |  | Y | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Handling of Urea Product | 61.012 |  | 0 |  |  | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | baghouse and enclosure; work practices to prevent visible emissions. | 0.005 | GR/DSCF | 3-HOUR AVERAGE | BACT-PSD |  | U | 99.99 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | COAL/PETCOKE RAILCAR UNLOADING &amp; STORAGE, SRC01-SRC07 | 90.011 |  | 5000 | T/H | ENCLOSED RAILCAR UNLOADING AT NEGATIVE PRESSURE. COVERED CONVEYORS AND ENCLOSED TRANSFER POINTS. STORAGE IN EUROSILO OR EQUIVALENT. HIGH EFFICIENCY BAGHOUSES (RAILCAR UNLOADING, CONVEYORS, STORAGE SILO VENTS). | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | ENCLOSED RAILCAR UNLOADING AT NEGATIVE PRESSURE. COVERED CONVEYORS AND ENCLOSED TRANSFER POINTS. STORAGE IN EUROSILO OR EQUIVALENT. HIGH EFFICIENCY BAGHOUSES (RAILCAR UNLOADING, CONVEYORS, STORAGE SILO VENTS). | 0.04 | LB/H |  | BACT-PSD |  | Y | 99 | N | 0.0004 | GR/DSCF |  | 0 |  |  | 0 | 0 | N |  | PMT LIMIT IS IN LB/H (APPROX. EQUIV TO GRAIN LOADING SHOWN AS EMISSION LIMIT 2).
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | COAL/PETCOKE RECLAIM TO ROD MILL, SRC08-SRC12 | 90.011 |  | 105 | T/H | COVERED CONVEYORS WITH ENCLOSED TRANSFER POINTS. CAPACITY IS 105 T/H FOR EACH CONVEYOR. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | COVERED CONVEYORS WITH ENCLOSED TRANSFER POINTS. HIGH EFFICIENCY BAGHOUSES. | 0.001 | LB/H |  | BACT-PSD |  | Y | 99 | U | 0 | GR/DSCF | SEE NOTE | 0 |  |  | 0 | 0 | N |  | PMT LIMIT IS IN LB/H (APPROX EQUIV TO GRAIN LOADING SHOWN AS EMISSION LIMIT 2).
OH-0310 | AMERICAN MUNICIPAL POWER GENERATING STATION | AMERICAN MUNICIPAL POWER | MEIGS | OH | 45771 | USA | RANDY MEYER | 6143376222 | RMEYER@AMP-OHIO.ORG | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104461 | 4911 | 221112 | 110000384325 | 05/15/2006 &nbsp;ACT | 10/08/2009 &nbsp;ACT | 2008-04-15 | 2009-11-06 | A |  | TWO 5191 MMBTU/HOUR PULVERIZED COAL-FIRED BOILERS; ONE 150 MMBTU/HOUR NATURAL GAS AUXILIARY BOILER, ONE FLY ASH AND GYPSUM LANDFILL, COAL STORAGE, CRUSHERS, FERTILIZER PLANT, LIMESTONE AND FLY ASH HANDLING EQUIPMENT, AND COOLING CELLS. ADMINISTRATIVE MODIFICATION 10/09 TO ADD CASE-BY-CASE MACT FOR BOILERS. 1ST ISSUED 2/7/08 AS PTI#06-08138; STILL INITIAL INSTALLATION | FUGITIVE EMISSIONS FROM STORAGE PILES (COAL,LIMESTONE, UREA), CONVEYING, HANDLING, ROADWAYS, BARGE OR TRUCK UNLOADING WERE NOT ENTERED INTO THE DATABASE DUE TO THE INSIGNIFICANT EMISSIONS (MOST < 1 TON FUGITIVE PM) AND LACK OF PROCESS CODES TO ENTER THEM. | COAL CONVEYING, HANDLING, AND CRUSHING | 90.011 |  | 5553840 | T/YR | CRUSHING TO PULVERIZE COAL, HANDLING, CONVEYING TO BOILERS | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | BAGHOUSE WITH OPTION OF ENCLOSURES, FOGGING, WET SUPPRESSION | 9 | T/YR | PER ROLLING 12-MONTHS | BACT-PSD | SIP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | FLUXANT TRUCK LDOUT &amp; CONVEYING, FUG | 90.019 |  | 250 | T/H | GASIFIER FLUXANT VARIES, BUT MAY INCLUDE LIMESTONE, IRON ORE OR SAND. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | COVERED CONVEYORS AND ENCLOSED TRANSFER POINTS. FUGITIVE DUST BMPS. | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | FLUXANT STORAGE, SRCXX | 90.019 |  | 250 | T/H | GASIFIER FLUXANT VARIES, BUT MAY INCLUDE LIMESTONE, IRON ORE, OR SAND. MAX FILL RATE PRESUMED TO BE 250 T/H. MAX USE RATE IN GASIFIER IS 250 T/D. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | HIGH EFFICIENCY BAGHOUSE(S) ON STORAGE SILO VENT(S) | 0.002 | LB/H |  | BACT-PSD |  | Y | 99 | U | 0 | LB/T | SEE NOTE | 0 |  |  | 0 | 0 | N |  | PMT LIMIT IS LB/H (EQUIVALENT LB/T LIMIT IS SHOWN AS EMISSION LIMIT 2), BASED ON 250 T/H FILL RATE.
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | COOLING TOWER, SRC22 | 99.009 |  | 121000 | GAL/MIN | COOLING WATER FLOW RATE 121,000 GPM. TDS MAX 5000 MG/L. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | DRIFT/MIST ELIMINATORS | 0.0005 | % OF TOTAL CIRC FLOW |  | BACT-PSD |  | N | 0 |  | 1.5 | LB/H |  | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | ZLDS COOLING TOWER, SRC30 | 99.009 |  | 985 | GAL/MIN | ZERO LIQUID DISCHARGE SYSTEM - COOLING WATER FLOW RATE 985 GPM. TDS MAX 50,000 MG/L. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | DRIFT/MIST ELIMINATORS | 0.001 | % OF TOTAL CIRC FLOW |  | BACT-PSD |  | Y | 0 |  | 0.3 | LB/H |  | 0 |  |  | 0 | 0 | N
ID-0017 | POWER COUNTY ADVANCED ENERGY CENTER | SOUTHEAST IDAHO ENERGY, LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 3039534297 | T.HORNYAK@REHINC.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV |  | P-2008.0066 | 2873 | 113210 | UNKNOWN | 04/29/2008 &nbsp;ACT | 02/10/2009 &nbsp;ACT | 2009-10-19 | 2010-02-05 | A |  | COAL/PETCOKE GASIFICATION PLANT PRODUCING AMMONIA, UREA, UAN, AND ELEMENTAL SULFUR. | FACILITY LOCATION: LAMB WESTON ROAD, AMERICAN FALLS, IDAHO. DESIGNATED FACILITY (FUEL CONVERSION PLANT AND CHEMICAL PLANT). PSD THRESHOLD IS 100 T/YR. BACT REQ'D FOR PM, PM10, CO, AND NOX. | SLAG HAND, FUG | 99.19 |  | 580 | T/D | GASIFIER SLAG IS WET WHEN CONVEYED TO STORAGE. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | STORAGE IN 3-SIDED BUNKER. FUGITIVE DUST BMPS. | 0 |  | SEE NOTE | BACT-PSD |  | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | BOILERS - UNITS CC026, CC027 AND CC028 AT CITY CENTER | 12.31 | NATURAL GAS | 44 | MMBTU/H | THE THREE UNITS ARE IDENTICAL CATERPILLAR BOILERS, EACH RATED AT 44 MMBTU/HR. EACH UNIT IS SUBJECT TO THE ANNUAL LIMIT OF OPERATING TIME TO 5,800 HOURS. THE EMISSION LIMITS ARE BASED ON THE ATC PERMIT FOR MODIFICATION #13 DATED NOVEMBER 30, 2009. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | LIMITING THE FUEL TO NATURAL GAS ONLY AND GOOD COMBUSTION PRACTICES | 0.0075 | LB/MMBTU |  | LAER | SIP , OPERATING PERMIT |  | 0 | N | 0.33 | LB/H |  | 0.0075 | LB/MMBTU |  | 0 | 0 | N |  | EMISSION LIMIT 2 APPLIES TO EACH UNIT.
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | COOLING TOWERS - UNITS CC026, CC027, AND CC028 AT CITY CENTER | 99.009 | N/A | 10890 | GAL/MIN | THE THREE UNITS ARE IDENTICAL COMPOSITE COOLING SYSTEM COOLING TOWERS. EACH UNIT HAS A CIRCULATION RATE OF 10,890 GPM, AND IS ALLOWED TO OPERATE 8,760 HOURS/YEAR. THE EMISSION LIMITS REPORTED HEREIN ARE BASED ON THE ATC PERMIT FOR MODIFICATION #13 DATED NOVEMBER 30, 2009. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | EACH UNIT IS EQUIPPED WITH A DRIFT ELIMINATOR LIMITING THE DRIFT RATE TO 0.001% AND THE TOTAL DISSOLVED SOLIDS IN THE CURCULATION WATER IS LIMITED TO 3,600 PPM. | 0.091 | LB/H |  | LAER | SIP , OPERATING PERMIT |  | 0 | N | 0.04 | T/YR |  | 0 |  |  | 0 | 0 | N |  | THE EMISSION LIMITS APPLY TO EACH UNIT.
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT FL01 | 13.31 | NATURAL GAS | 14.34 | MMBTU/H | UNIT FL01 IS A JOHNSTON BOILER AT FLAMINGO LAS VEGAS. THIS UNIT MAY OPERATE 8,760 HOURS PER YEAR. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | FLUE GAS RECIRCULATION AND OPERATING IN ACCORDANCE WITH THE MANUFACTURER'S SPECIFICATION | 0.0075 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 0.11 | LB/H |  | 0.0075 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | SMALL INTERNAL COMBUSTION ENGINE (&lt;600 HP) - UNIT FL12 | 13.31 | DIESEL OIL | 536 | HP | UNIT FL12 IS A DETROIT DIESEL GENERATOR AT FLAMINGO LAS VEGAS. LIKE ALL THE OTHER DIESEL GENERATORS, THE UNIT IS SUBJECT TO THE LIMIT OF MONTHLY AND ANNUAL OPERATING TIMES FOR 2 HOURS PER MONTH AND 36 HOURS PER YEAR RESPECTIVELY. EMISSION FACTORS LISTED IN AP-42 ARE USED TO CALCULATE THE EMISSION LIMITS FOR EACH AND EVERY DIESEL GENERATOR IN THIS MAJOR STATIONARY SOURCE, AND ARE NOT REPEATED FURTHER FOR REPORTING THE BACT DETERMINATIONS. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | THE UNIT IS EQUIPPED WITH A TURBOCHARGER. | 0.0022 | LB/HP-H |  | OTHER CASE-BY-CASE | SIP , OPERATING PERMIT | N | 0 | Y | 1.18 | LB/H |  | 0.0022 | LB/HP-H |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT BA01 | 13.31 | NATURAL GAS | 16.8 | MMBTU/H | UNIT BA01 IS A KEWANEE BOILER AT BALLY'S LAS VEGAS. UNIT BA01 IS IDENTICAL TO UNIT BA02. THE TWO BOILERS ARE SUBJECT TO THE ANNUAL LIMIT OF COMBINED TOTAL OPERATING TIME FOR 10,900 HOURS PER YEAR. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | OPERATING IN ACCORDANCE WITH THE MANUFACTURER'S SPECIFICATION | 0.0077 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 0.13 | LB/H |  | 0.0077 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT BA03 | 13.31 | NATURAL GAS | 31.38 | MMBTU/H | UNIT BA03 IS A KIWANEE BOLER AT BALLY'S LAS VEGAS. THE ANNUAL OPERATING TIME IS LIMITED TO 2,920 HOURS PER YEAR. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | OPERATING IN ACCORDANCE WITH THE MANUFACTURER'S SPECIFICATION | 0.0076 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT | N | 0 | Y | 0.24 | LB/H |  | 0.0076 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP01 | 13.31 | NATURAL GAS | 35.4 | MMBTU/H | UNIT CP01 IS A HURST BOILER AT CAESAR'S PALACE. UNIT CP01 IS IDENTICAL TO UNIT CP02. UNITS CP01 THROUGH CP05 (FIVE BOILERS) ARE SUBJECT TO THE ANNUAL LIMIT OF TOTAL OPERATING TIME FOR 33,520 HOURS PER YEAR. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | OPERATING IN ACCORDANCE WITH THE MANUFACTURER'S SPECIFICATION | 0.0076 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT | N | 0 | Y | 0.27 | LB/H |  | 0.0076 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP03 | 13.31 | NATURAL GAS | 33.48 | MMBTU/H | UNIT CP03 IS A BURNHAM BOILER AT CAESAR'S PALACE. UNITS CP01 THROUGH CP05 (FIVE BOILERS) ARE SUBJECT TO THE ANNUAL LIMIT OF TOTAL OPERATING TIME FOR 33,520 HOURS PER YEAR. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | OPERATING IN ACCORDANCE WITH THE MANUFACTURER'S SPECIFICATION | 0.0075 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 0.25 | LB/H |  | 0.0075 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP26 | 13.31 | NATURAL GAS | 24 | MMBTU/H | UNIT CP26 IS A UNILUX BOILER AT CAESAR'S PALACE. THE UNIT IS ALLOWED TO OPERATE UP TO 8,760 HOURS PER YEAR. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | OPERATING IN ACCORDANCE WITH THE MANUFACTURER'S SPECIFICATION | 0.0075 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT | N | 0 | Y | 0.18 | LB/H |  | 0.0075 | LB/MMBTU |  | 0 | 0 | N
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | WATER HEATERS - UNITS NY037 AND NY038 AT NEW YORK - NEW YORK | 13.31 | NATURAL GAS | 2 | MMBTU/H | THE TWO UNITS ARE IDENTICAL RBI FUTURA III WATER HEATERS.THE EMISSION LIMITS REPORTED HEREIN ARE BASED ON THE ATC PERMIT FOR MODIFICATION #9 DATED SEPTEMBER 6, 2006. EACH UNIT IS ALLOWED TO OPERATE 24 HOURS/DAY AND 8,760 HOURS/YEAR. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | LIMITING THE FUEL TO NATURAL GAS ONLY AND GOOD COMBUSTION PRACTICES | 0.0075 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT | N | 0 | Y | 0.015 | LB/H |  | 0.0075 | LB/MMBTU |  | 0 | 0 | N |  | EMISSION LIMIT 2 APPLIES TO EACH UNIT.
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | TURBINE GENERATORS - UNITS CC007 AND CC008 AT CITY CENTER | 16.11 | NATURAL GAS | 4.6 | MMBTU/H | THE TWO UNITS ARE IDENTICAL SOLAR MERCURY COMBUSTION GAS TURBINES FOR ELECTRIC POWER GENERATION. EACH UNIT IS RATED AT 4.6 MMBTU/HR, AND IS ALLOWED TO OPERATE 24 HOURS/DAY AND 8,760 HOURS/YEAR. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | GOOD COMBUSTION PRACTICES AND LIMITING THE FUEL TO NATURAL GAS ONLY | 0.202 | LB/MMBTU |  | OTHER CASE-BY-CASE | SIP , OPERATING PERMIT | N | 0 | N | 0.93 | LB/H |  | 0.202 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | LARGE INTERNAL COMBUSTION ENGINES (&gt;600 HP) - UNIT HA13 | 17.11 | DIESEL OIL | 1232 | HP | UNIT HA13 IS A MARATHON DIESEL GENERATOR AT HARRAH'S LAS VEGAS. ALL THE SEVEN (7) DIESEL GENERATORS AT HARRAH'S LAS VEGAS ARE FOR EMERGENCY USE ONLY. EACH ONE OF THEM IS SUBJECT TO THE SAME LIMIT OF OPERATING TIME FOR 2 HOURS PER DAY AND 36 HOURS PER YEAR. THE EMISSION LIMITS ARE CALCULATED BASED ON THE EMISSION FACTORS TAKEN FROM AP-42. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | THE UNIT IS EQUIPPED WITH A TURBOCHARGER. | 0.0007 | LB/HP-H |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 0.87 | LB/H |  | 0.0007 | LB/HP-H |  | 0 | 0 | N
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | EMERGENCY GENERATORS - UNITS LX024 AND LX025 AT LUXOR | 17.11 | DIESEL OIL | 2206 | HP | THE TWO UNITS ARE IDENTICAL CATERPILLAR GENERATORS MODEL 3512C. EACH UNIT HAS A FOUR-STROKE COMPRESSION-IGNITION ENGINE RATED AT 2,206 HORSE POWER (HP). THE EMISSION LIMITS REPORTED HEREIN ARE BASED ON THE ATC PERMIT FOR MODIFICATION #10 DATED SEPTEMBER 20, 2006. EACH UNIT IS ALLOWED TO OPERATE UP TO ONE HOUR PER DAY AND FIFTY TWO HOURS PER YEAR. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | TURBOCHARGER AND GOOD COMBUSTION PRACTICES | 0.0001 | LB/HP-H |  | Other Case-by-Case | SIP , OPERATING PERMIT | N | 0 | N | 0.2 | LB/H |  | 0.0001 | LB/HP-H |  | 0 | 0 | N |  | EMISSION LIMIT 2 APPLIES TO EACH UNIT.
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | COOLING TOWER - UNIT HA19 | 99.009 | N/A | 7200 | GAL/MIN | UNIT HA19 IS IDENTIFIED AS A BALTIMORE AIRCOIL CO. (BAC) SERIES 3000 COOLING TOWER AT HARRAH'S LAS VEGAS. UNIT HA19 IS IDENTICAL TO UNITS HA20 AND HA21. THE SAME EMISSION LIMIT APPLIES TO EACH OF THE THREE COOLING TOWERS. BACT FOR PM-10 FOR THE THREE UNITS INCLUDES: (1) EACH COOLING TOWER SHALL BE EQUIPPED WITH A DRIFT ELIMINATOR TO REDUCE DRIFT RATE TO BELOW 0.005%. (2) TOTAL DISSOLVED SOLIDS CONTENT IN THE COOLING WATER SHALL BE MAINTAINED BELOW 2,520 PPM. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | A DRIFT ELIMINATOR CONTROLS DRIFT RATE TO 0.005%, AND THE PERMITTEE IS REQUIRED TO MAINTAIN TSD CONTENT IN THE COOLING WATER TO A MAXIMUM OF 2,520 PPM. | 0.215 | LB/H |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 0.94 | T/YR |  | 0 |  |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | COOLING TOWER - UNIT FL17 | 99.009 | N/A | 6900 | GAL/MIN | UNIT FL17 IS A MARLEY COOLING TOWER AT FLAMINGO LAS VEGAS. UNIT FL17 IS IDENTICAL TO UNITS FL18, FL19, AND FL20. THE SAME EMISSION LIMIT APPLIES TO EACH OF THE FOUR COOLING TOWERS. BACT FOR PM-10 FOR THE FOUR COOLING TOWERS INCLUDES: (1) EACH COOLING TOWER SHALL BE EQUIPPED WITH A DRIFT ELIMINATOR TO REDUCE DRIFT RATE TO BELOW 0.005%. (2) TOTAL DISSOLVED SOLIDS CONTENT IN THE COOLING WATER SHALL BE MAINTAINED BELOW 3,000 PPM. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | DRIFT ELIMINATOR TO REDUCE DRIFT RATE TO LESS THAN 0.005% AND MAINTAINING TOTAL DISSOLVED SOLIDS CONTENT IN THE COOLING WATER TO BELOW 3,000 PPM. | 0.425 | LB/H |  | Other Case-by-Case | SIP , OPERATING PERMIT | N | 0 | Y | 1.86 | T/YR |  | 0 |  |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | COOLING TOWER - UNIT BA14 | 99.009 | N/A | 20400 | GAL/MIN | UNIT BA14 IS A BALTIMORE AIR COIL COOLING TOWER AT BALLY'S LAS VEGAS. BACT FOR PM-10 INCLUDES: (1) THE UNIT IS EQUIPPED WITH A DRIFT ELIMINATOR TO REDUCE DRIFT RATE TO BELOW 0.005%; (2) TOTAL DISSOLVED SOLIDS CONTENT IN THE COOLING WATER SHALL BE MAINTAINED BELOW 3,000 PPM. NO OTHER COOLING TOWERS AT BILL'S GAMBLIN' HALL & SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE HAVE AN ANNUAL POTENTIAL TO EMIT FOR PM-10 IN EXCESS OF ONE TON PER YEAR. THE BACT DETERMINATIONS ARE SIMILAR TO THAT OF UNIT BA14 AND ARE SKIPPED. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | BACT CONSISTS OF THE TWO REQUIREMENTS DESCRIBED IN THE PROCESS. | 0.744 | LB/H |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 3.26 | T/YR |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Gas Turbines (8 units) | 15.11 | natural gas | 333 | mm btu/hr |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and fueled by natural gas | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Emergency Generator | 17.11 | Diesel | 2015.7 | HP | Nominal 1,500 kW. Limited to 100 hours/year. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0.15 | G/HP-HR |  | 0 | 0 | N |  | Additionally, this engine is subject to the opacity requirements given under Â§80.113.
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Fire Pump Engine | 17.21 | Diesel | 251 | HP | Limited to 100 Hours/year. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0.15 | G/HP-HR |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | AMMONIA STORAGE FLARE (EU-016) | 19.39 | NATURAL GAS | 1.1 | MMBTU/H |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0075 | LB/MMBTU | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 168 | H/12 CONSEC MONTH | COMPLIANCE DETERMINED AT END OF MONTHS | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS SHALL BE NATURAL GAS LIMIT 4: SHALL COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUT DOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) SHALL TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP AND SHUT DOWN. THIS ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DURING TWO CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMOCOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE.
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | flares | 19.39 | natural gas | 7.33 | kg/hr |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Steam Methane Reformer | 50.002 | NATURAL GAS | 10 | MMSCFH | Steam Methane Reformer, equipped with low NOx burners, SCR, and CO oxidation catalyst | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Other - 5 or 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 1.75 | LB/H | 3-HR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Steam Methane Reformer, equipped with low NOx burners, SCR, and CO oxidation catalyst
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Handling of Urea Product | 61.012 |  | 0 |  |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | B | baghouse and enclosure; work practices to prevent visible emissions. | 0.005 | GR/DSCF | 3-HOUR AVERAGE | BACT-PSD |  | U | 99.99 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | EIGHTEEN CELL COOLING TOWER (EU-010) | 99.999 |  | 0 |  |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | HIGH EFFICIENCY DRIFT ELIMINATORS | 2000 | MG/L | AVG. ON A MONTHLY BASIS | BACT-PSD |  | N | 0 |  | 0.0005 | % | DRIFT | 0 |  |  | 0 | 0 | N | 2016
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | AUXILIARY BOILER (1) AND FUEL GAS HEATERS (6) | 12.31 | NATURAL GAS | 185 | MMBTU/HR | The auxiliary boiler will provide steam to the steam turbine at startup and at cold starts to warm up the ST rotor. The steam from the auxiliary boiler will not be used to augment the power generation of the combustion turbines or steam turbine. The boiler is proposed to operate 8760 hrs/yr but will be limited by an annual fuel throughput based on a capacity factor of 10%. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur /carbon fuel and good combustion practices | 0.007 | LB/MMBTU |  | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | COMBUSTION TURBINE GENERATOR WITH DUCT-FIRED HEAT RECOVERY STEAM GENERATORS (3) | 15.21 | natural gas | 3227 | MMBTU/HR | 3227 MMBTU/HR CT with 500 MMBTU/HR Duct Burner, 3 on 1 configuration. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Other - 201A | (Particulate Matter (PM)) | PM | P | Pipeline Quality Natural Gas | 0.0039 | LB/MMBTU | AVG OF 3 TEST RUNS | N/A |  | U | 0 | U | 14.1 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Turbine without DB: 9.2 lb/hr (0.0030 lb/MMBtu); with DB: 14.1 lbs/hr (0.0039 lb/MMBtu) (average of three test runs)
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | PROPANE-FIRED EMERGENCY GENERATORS 150 kW (2) | 17.23 | PROPANE | 0 |  |  | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur fuel and good combustion practices | 0.019 | G/HP-H | PER HR | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | TUNNEL FURNACES SN-20 AND 21 | 12.31 | NATURAL GAS | 234 | MMBTU/H | 2 TUNNEL FURNCE SECTIONS 234 MMBTU/HR AND 192 MMBTU/HR MADE UP OF A SERIES OF INDIVIDUAL 3 MMBTU BURNERS. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Startup Heater | 12.31 | natural gas | 104 | MMBTU/H |  | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0019 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | FOUR (4) NATURAL GAS-FIRED BOILERS | 12.31 | NATURAL GAS | 218 | MMBTU/HR, EACH | FUEL INPUT TO ALL FOUR BOILERS SHALL NOT EXCEED 2,802 MMCF/YEAR | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | PROPER DESIGN AND GOOD COMBUSTION PRACTICES | 1.9 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUAUXBOILER (Auxiliary Boiler) | 12.31 | natural gas | 182 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 182 MMBTU/H fuel heat input. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.005 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | At greater than $40,000 for the least expensive option, none of the control technologies are economically feasible. Control technologies evaluated were a scrubber and various types of fabric filters and ESPs.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUAUXBOILER (Auxiliary boiler) | 12.31 | Natural gas | 182 | MMBTU/H | A natural gas fired auxiliary boiler, rated at 182 MMBTU/H to provide auxiliary steam when the plant is off-line, used to maintain warm drums on the HRSG and maintain the steam turbine generator seals. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.005 | LB/MMBTU |  | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The low concentration of PM / PM10 / PM2.5 in the auxiliary boiler exhaust makes the cost of add-on control very high. Also, of the add-on control options evaluated (pulse jet fabric filter, dry and wet ESP, and venturi scrubber), only the venturi scrubber and wet ESP are expected to be able to effectively reduce condensable PM emissions. The following costs are estimated for the add-on control technologies: â€¢ Fabric Filter Control: over $47,000 per ton controlled (assuming 99.9 percent control of filterable PM/PM10/PM2.5) â€¢ Electrostatic Precipitator (ESP): over $34,000 per ton controlled (assuming 99.4 percent control of filterable PM/PM10/PM2.5) â€¢ Wet ESP: over $29,000 per ton controlled (assuming 99.2 percent control of filterable and condensable PM/PM10/PM2.5) â€¢ Venturi Scrubber: over $20,000 per ton controlled (assuming 99.0 percent control of filterable and condensable PM/PM10/PM2.5)
NY-0112 | WESTROCK-SOLVAY LLC | WESTROCK-SOLVAY LLC | ONONDAGA | NY | 13204-1035 | USA |  | 315-484-9050 |  | 2 | NY001 | NEW YORK DEPT. OF ENVIRONMENTAL CONSERVATION | MR. NICK ONDERDONK-MILNE | (518)402-8403 | nick.onderdonk-milne@dec.ny.gov | DEC Region 7 315-426-7400 | 7-3132-00055/00037 | 2631 | 322213 | 110009824547 | 11/02/2012 &nbsp;ACT | 11/02/2012 &nbsp;ACT | 2017-09-11 | 2017-09-28 | B | http://www.dec.ny.gov/chemical/32249.html | WestRock-Solvay LLC is a linerboard and corrugated medium facility utilizing three paper machines capable of producing a variety of linerboard and corrugated medium products. The facility also operates a wastewater treatment facility to treat the effluent from the paper making process and plans to add boilers for steam supply with this application. Up to three (3) permanent, large package boilers (&lt; 250 mmBtu/hr) capable of firing natural gas, No. 2 Fuel Oil (ULSD), or Biogas. In additionally, up to two (2) back-up medium size package boilers (&lt; 100 mmBtu/hr) capable of firing natural gas and No. 2 fuel Oil (ULSD) as a back-up. Total annual oil use for all boilers shall not exceed 164,640 mmBtu/yr (figure based on 336 hrs/yr x 490 mmBtu/hr). | State Facility Permit | Boilers - NG | 12.31 | natural gas | 0 |  |  | Particulate matter, filterable (FPM) | Other - EPA approved Method | (Particulate Matter (PM)) | PM | B | Good combustion practice and use of low NOx burners. | 0.007 | LB/MMBTU | 1 H | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | AMMONIA CATALYST STARTUP HEATER | 12.39 | NATURAL GAS | 106.3 | MMBTU/H | ANNUAL NATURAL GAS USAGE LIMITED TO 20.84 MMCF. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS COMBUSTION ONLY, PROPER DESIGN AND GOOD COMBUSTION PRACTICES | 1.9 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, VACUUM DEGASSER | 13.29 | NATURAL GAS | 51.2 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACE, ANNEALING PICKLING LINE | 13.29 | NATURAL GAS | 66 | MMBTU/H | ANNEALING PICKLING LINE FURNACE SN-47; ANNEALING COATING LINE FURNACE , SN 51; | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, PICKLE LINE | 13.31 | NATURAL GAS | 67 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILERS SN-26 AND 27, GALVANIZING LINE | 13.31 | NATURAL GAS | 24.5 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER EU-002 | 13.31 | NATURAL GAS | 70 | MMBTU/HR |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICE | 0.13 | LB/H | 3HR AVERAGE | BACT-PSD |  | N | 0 |  | 200 | H/YR |  | 0 |  |  | 0 | 0 | N | 2016 | SHALL COMBUST NATURAL GAS
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGFUELHTR (Two fuel pre-heaters identified as EUFUELHTR1 &amp; EUFUELHTR2) | 13.31 | Natural gas | 27 | MMBTU/H | Two natural gas fired dew point heaters for warming the natural gas fuel (EUFUELHTR1 & EUFUELHTR2 in flexible group FGFUELHTR). The total combined heat input during operation shall not exceed 27 MMBTU/H (each) as well. The CO2e limit is for both units combined; however the other limits are per unit. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.002 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME. | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above of 0.002 LB/MMBTU is for each fuel heater. At greater than $40,000 for the least expensive option, none of the control technologies are economically feasible. Control technologies evaluated were a scrubber and various types of fabric filters and ESPs.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 9.9 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit in the table above is for EACH CTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. Pulse jet fabric filter baghouse: minimum of $364,528 per ton. Mechanical shaker fabric filter baghouse: minimum of $404,724 per ton. Reverse-air fabric filter baghouse: minimum of $476,689 per ton. Dry ESP (Wire-plate type): minimum of $478,806 Dry ESP (Wire-pipe type): minimum of $303,809 per ton. Wet ESP (Wire-plate type): minimum of $576,763 per ton. Wet ESP (Wire-pipe type): minimum of $440,047 per ton. Venturi Scrubber: minimum of $1,445,564 per ton.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas, combustion inlet air filter. | 0.0025 | LB/MMBTU |  | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Fabric filter control: over $260,000 per ton controlled (assuming 99.9 percent control of filterable PM/PM10/PM2.5). Electrostatic Precipitator (ESP): over $188,000 per ton controlled (assuming 99.4 percent control of filterable PM/PM10/PM2.5). Wet ESP: over $165,000 per ton controlled (assuming 99.2 percent control of filterable and condensable PM/PM10/PM2.5). Venturi Scrubber: over $112,000 per ton controlled (assuming 99.0 percent control of filterable and condensable PM/PM10/PM2.5).
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EMERGENCY GENERATORS | 17.11 | DIESEL | 1500 | KW |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD OPERATING PRACTICES, LIMITED HOURS OF OPERATION, COMPLIANCE WITH NSPS SUBPART IIII | 0.02 | G/KW-H |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Emergency Generator | 17.11 | distillate fuel oil | 3755 | HP |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 0.1 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY GENERATOR | 17.11 | NO. 2 FUEL OIL | 4690 | B-HP | ANNUAL HOURS OF OPERATION NOT TO EXCEED 200 HOURS. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUEMENGINE (Diesel fuel emergency engine) | 17.11 | Diesel Fuel | 22.68 | MMBTU/H | a 2,922 horsepower (HP) (2,179 kilowatts (kW)) diesel fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Restricted to 4 hours/day, except during emergency conditions and stack testing, and 500 hours/year on a 12-month rolling time period basis. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and meeting NSPS Subpart IIII requirements. | 0.2 | G/KW-H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 0.1 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and meeting NSPS Subpart IIII requirements. | 0.15 | G/BHP-H | TEST PROTOCOL WILL SPECIFY AVG TIME. | BACT-PSD | NSPS | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | SMALL HEATERS AND DRYERS SN-05 THROUGH 19 | 17.23 | NATURAL GAS | 0 |  | RH VESSEL PREHEATER STATION, VESSEL TOP PART DRYER, RH VESSEL NOZZLE DRYER RH DEGASSER BURNER/LANCE LADLE PREHEATERS LADLE DRYOUT STATION VERTICAL LADLE HOLDING STATION TUNDISH PREHEATERS #1 THROUGH #4 | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | FRONT END PROCESS FLARE | 19.31 | NATURAL GAS PILOT | 0.25 | MMBTU/H | HEAT INPUT IS FOR NATURAL GAS PILOT ONLY. SSM EMISSIONS ARE CONTROLLED BY THE FLARE AND ARE LIMITED TO 336 HOURS OF VENTING PER YEAR. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS FOR PILOT FLARE, FLARE MINIMIZATION PRACTICES | 0.0019 | LB/MMBUT | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO ADDITIONAL PM EMISSIONS DURING VENTING EVENTS
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | BACK END AMMONIA FLARE | 19.31 | NATURAL GAS | 0.25 | MMBTU/H | HEAT INPUT IS FOR PILOT ONLY. SSM EMISSIONS ARE CONTROLLED BY THE FLARE AND ARE LIMITED TO 336 HR/YR. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.0019 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO ADDITIONAL PM IS ANTICIPATED DURING SSM VENTING.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | AMMONIA STORAGE FLARE | 19.31 | NATURAL GAS | 0.13 | MMBTU/H | HEAT INPUT IS FOR PILOT ONLY. SSM EVENTS HAVE SEPARATE LIMITS. SSM VENTING IS LIMITED TO 168 HOURS PER YEAR. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.0019 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | SSM VENTING LIMITED TO 168 HR PER YEAR.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | UAN PLANT VENT FLARE | 19.31 |  | 0.19 | MMBTU/H | HEAT INPUT IS FOR NATUAL GAS PILOT. SSM EMISSIONS HAVE SEPARATE LIMITS. SSM VENTING LIMITED TO 336 HOURS PER YEAR. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.0019 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | SSM VENTING IS LIMITED TO 336 HR PER YEAR.
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EMERGENCY GENERATOR SN-62 | 19.8 | DIESEL | 625 | HP |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD OPERATING PRACTICES, LIMITED HOURS OF OPERATION, COMPLIANCE WITH NSPS SUBPART IIII | 0.02 | G/KW-H |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Ammonia Plant, Flares | 61.012 | natural gas | 2789 | tpd |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Reformer Furnace | 61.012 | natural gas | 955 | MMBTU/H |  | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0019 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Ammonia Pressure Tanks | 61.012 |  | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | B | Flare; flare minimization | 0.1 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Urea Plant | 61.012 |  | 4880 | tpd | while the urea granulator in the urea plant is the principal emitter, there are other units that contribute. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | 2-stage scrubbing system with high efficiency venturi scrubber. | 0.005 | GR/DSCF |  | BACT-PSD |  | U | 0 | U | 0.14 | LB/TON UREA | 3-HOUR AVERAGE | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Cooling Tower | 61.012 |  | 0 |  |  | Particulate matter, filterable (FPM) | Other - sampling and analysis of cooling water | (Particulate Matter (PM)) | PM | B | drift eliminators; TDS of water not to exceed 2000 mg/l | 0.0005 | % LOSS FROM CIRC. |  | BACT-PSD |  | U | 0 | U | 1 | LB/H | 24-HOUR AVERAGE | 4.42 | TPY |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Handling of Urea Product | 61.012 |  | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | B | baghouse and enclosure; work practices to prevent visible emissions. | 0.0005 | GR/DSCF | 3-HOUR AVERAGE | BACT-PSD |  | U | 99.99 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | PRIMARY REFORMER | 61.012 | NATURAL GAS | 1006.4 | MMBTU/H | NOX CEMS | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 1.9 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | TWO (2) AMMONIUM NITRATE UNITS | 61.012 |  | 798 | TON AN PER DAY, EACH | UAN PRODUCTION IS LIMITED TO 1,314,000 TONS PER YEAR. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | WET SCRUBBER WITH HIGH EFFICIENCY DEMISTER | 0.0128 | LB/TON OF UAN | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Grain Dryer | 70.21 |  | 300 | ton/hr |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD | NSPS | U | 0 | U | 6.44 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Grain Receiving and Handling | 70.23 |  | 20000 | bu/hr | 6 units routed to 1 stack. Grain Truck Dump Pit #1, Grain Elevator #1, Grain Truck Dump Pit #2, Grain Elevator #2, Conveyor #1, and Scalper | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD | NSPS | N | 0 | U | 0.82 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Mill Feed Receiving | 70.23 |  | 12 | ton/hr |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.03 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Grain Receiving via Rail | 70.29 |  | 720 | ton/hr |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Millfeed | 70.29 |  | 106.25 | ton/hr |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.72 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Rotary Conditioner | 70.29 |  | 106.25 | ton/hr |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.1 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.26 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Flaker with Process Cyclone | 70.29 |  | 106.25 | ton/hr |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.008 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.96 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Meal Grinding | 70.29 |  | 106.25 | ton/hr |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.39 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Meal Bin #36 | 70.29 |  | 106.25 | ton/hr |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.08 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Pellet and Hull Storage Bins | 70.29 |  | 20 | ton/hr | 2 Pellet storage bins and 2 Hull storage bins | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.08 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Calcium Bin | 70.29 |  | 250 | ton/hr |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.04 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Grain Cleaning | 70.29 |  | 300 | ton/hr |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0.44 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Dryer/Cooler | 70.29 |  | 106.25 | ton/hr |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | Wet Venturi Scrubber | 0.0025 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 1.16 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | DDGS and Pellet Storage/loadout | 70.29 |  | 250 | ton/hr | 4 units routed to 1 stack. DDGS/Pellet Storage Building, Dump pit/conveyor, Bridge Conveyor, Loadout Conveyor | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.75 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Pellet Cooler | 70.29 |  | 22 | ton/hr |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.33 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EAFS SN-01 AND SN-02 | 81.21 | NATURAL GAS | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | BAGHOUSE | 0.0018 | GR/DSCF | 3 HR | BACT-PSD |  |  | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | ANNEALING COATING CLEANING SECTION, SN-52 | 81.23 |  | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | MIST ELIMINATOR | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | LMFS SN-01 AND SN-02 | 81.29 | NATURAL GAS | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | FABRIC FILTER | 0.0018 | GR/DSCF | 3 HR | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | RH DEGASSER | 81.29 | NATURAL GAS | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | SCALE EXHAUST, PICKLE LINE | 81.29 |  | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | FABRIC FILTER | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | DUST EXHAUST SN-23A, TENSION LEVELER | 81.29 |  | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | FABRIC FILTER | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | COLD MILL REVERSING COLD MILL AND SKIN PASS MILL SN-25, 38, 44, 45, AND 46 | 81.29 |  | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | MIST ELIMINATOR | 0.0025 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | GALVANIZING LINE CAUSTIC CLEANING AND POST TREATMENT SN-34 THROUGH 37 | 81.29 |  | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | MIST ELIMINATOR | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-39, ANNEALING | 81.29 | NATURAL GAS | 98.25 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | DECARBURIZING LINE CLEANING SECTIONS SN-41 AND 43 | 81.29 |  | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | MIST ELIMINATOR | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | ANNEALING PICKLING LINE SCALE DUST AND SHOTBLAST | 81.29 |  | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | FABRIC FILTER | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | ANNEALING COATING LINE FURNACE SECTION | 81.29 | NATURAL GAS | 50 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACE, SN-53, ANNEALING COATING LINE DRYING | 81.29 | NATURAL GAS | 38 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | DRYERS, MGO COATING LINE | 81.29 | NATURAL GAS | 38 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | MGO COATING CLEANING SECTIONS SN-55 AND 57 | 81.29 |  | 0 |  |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | MIST ELIMINATOR | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-58 AND 60, FINAL ANNEALING AND COATING LINE | 81.29 | NATURAL GAS | 32 | MMBTU/H |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | TWO (2) COOLING TOWERS | 99.009 |  | 179720 | GPM, COMBINED | ONE UNIT IS EIGHT CELL, THE OTHER IS SIX CELL. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | HIGH EFFICIENCY DRIFT ELIMINATORS | 0.0005 | % DRIFT | CONTINUOUS | BACT-PSD |  | Y | 0 |  | 2000 | MG/L TDS | CONTINUOUS | 0 |  |  | 4592 | 0 | N | 2012 | TOWERS USE ONSITE WELL WATER. IT IS HAS HIGHER THAN NORMAL TDS. COST EFFECTIVENESS BASED ON REDUCTION OF TDS FROM 2,000 MG/L TO 1,500 MG/L. ADVERSE ENVIRONMENTAL IMPACTS WERE CONSIDERED.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCOOLTWR (Cooling Tower--Wet Mechanical Drift) | 99.009 |  | 0 |  | A four-cell evaporative cooling tower in series with mechanical chilling to cool turbine inlet air. Particulate emissions will be controlled with high efficiency drift eliminators. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | A | Mist/Drift Eliminators | 0.0006 | % | VENDOR-CERTIFIED MAX. DRIFT RATE | BACT-PSD |  | N | 0 | N | 7700 | PPM | MAX. TDS IN COOLING WATER | 0 |  |  | 0 | 0 | N |  | NOTE: Emission limit 1 above is 0.0006%, vendor-certified maximum drift rate. Emission limit 2 above is 7700 ppmw, maximum total dissolved solids (TDS) in cooling water. The estimated efficiency is to reduce drift loss to 0.0006. There are no BACT emission limits in the permit, but there is a requirement for the permittee to equip and maintain EUCOOLTWR with mist/drift eliminators with a vendor-certified maximum drift rate of 0.0006 percent or less, and there is also a limit of 7700 ppmw maximum Total Dissolved Solids (TDS) in cooling water.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | PAVED ROADWAYS AND PARKING LOTS WITH PUBLIC ACCESS | 99.14 |  | 17160 | VEHICLE MILES TRAVELED |  | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | PAVE ALL PLANT HAUL ROADS, DAILY SWEEPING AND WET SUPPRESSION, PROMPT CLEANUP OF ANY SPILLED MATERIAL | 90 | % CONTROL | CONTINUOUS | BACT-PSD |  | N | 90 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0354 | KRATON POLYMERS U.S. LLC | KRATON POLYMERS U.S. LLC | WASHINGTON | OH | 45714-0235 | USA | DALE LOUDERMILK | 740-423-2299 | DALE.LOUDERMILK@KRATON.CC | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0108853 | 2822 | 325212 | 110030900997 | 08/29/2012 &nbsp;ACT | 01/15/2013 &nbsp;ACT | 2013-09-27 | 2016-05-04 | B |  | Thermoplastic elastomer manufacturing facility | Two new 249 MMBtu/hour natural gas, distillate oil, and belpre naphtha-fired boilers installed to replace 2 existing coal, distillate oil, and belpre naphtha-fired boilers. | Two 249 MMBtu/H boilers | 12.31 | Natural Gas | 249 | MMBtu/H | Two boilers, burning natural gas or distillate oil w/ less than 0.05% sulfur; and co-fired with maximum of 54.8 MMBtu/H Belpre naphtha. Fitted with low-NOx burners with flue gas recirculation, as needed. | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.03 | LB/MMBTU | BURING WITH NG OR OIL W/ BELPRE NAPHTHA | N/A | MACT , SIP | U | 0 | U | 32.76 | T/YR |  | 0.02 | LB/MMBTU | BURNING NATURAL GAS OR DISTILLATE OIL | 0 | 0 | N |  | Subject to Part 63 Subpart JJJJJJ Table 1. Netted out for PM by replacing old coal/oil-fired boilers.
OH-0310 | AMERICAN MUNICIPAL POWER GENERATING STATION | AMERICAN MUNICIPAL POWER | MEIGS | OH | 45771 | USA | RANDY MEYER | 6143376222 | RMEYER@AMP-OHIO.ORG | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104461 | 4911 | 221112 | 110000384325 | 05/15/2006 &nbsp;ACT | 10/08/2009 &nbsp;ACT | 2008-04-15 | 2009-11-06 | A |  | TWO 5191 MMBTU/HOUR PULVERIZED COAL-FIRED BOILERS; ONE 150 MMBTU/HOUR NATURAL GAS AUXILIARY BOILER, ONE FLY ASH AND GYPSUM LANDFILL, COAL STORAGE, CRUSHERS, FERTILIZER PLANT, LIMESTONE AND FLY ASH HANDLING EQUIPMENT, AND COOLING CELLS. ADMINISTRATIVE MODIFICATION 10/09 TO ADD CASE-BY-CASE MACT FOR BOILERS. 1ST ISSUED 2/7/08 AS PTI#06-08138; STILL INITIAL INSTALLATION | FUGITIVE EMISSIONS FROM STORAGE PILES (COAL,LIMESTONE, UREA), CONVEYING, HANDLING, ROADWAYS, BARGE OR TRUCK UNLOADING WERE NOT ENTERED INTO THE DATABASE DUE TO THE INSIGNIFICANT EMISSIONS (MOST < 1 TON FUGITIVE PM) AND LACK OF PROCESS CODES TO ENTER THEM. | FGD LANFILL | 29.9 |  | 807291 | T/ROLLING 12-MO | LANDFILL FOR COAL ASH DISPOSAL FOR FACILITY: GYPSUM, FLYASH AND BOTTOM ASH | Particulate matter, fugitive | Unspecified |  | PM | P | BEST AVAILABLE MEASURES TO MINIMIZE FUGITIVE DUST: WATERING, COMPACTING, COVER | 3.9 | T/YR | PER ROLLING 12-MONTHS | BACT-PSD | SIP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | SYNTHETIC MINOR LIMIT TO AVOID BAT
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | 2 Cell Cross-Flow Cooling Tower | 99.11 |  | 15000 | gallons per minute | 2 Cell Cross-Flow Cooling Tower | Particulate matter, fugitive | Unspecified |  | PM | A | High Efficiency Drift Eliminators | 0.002 | % DRIFT |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Urea Ship Loading | 99.11 |  | 1000 | tons urea/hour | The Urea Ship Loading Operations are conveyor systems used to load products from the Urea Plant into ships. | Particulate matter, fugitive | Unspecified |  | PM | B | Use of UF-85 (Hardening Agent), Product Coolers on Granulation Urea Process Lines, Loading into Partial Enclosure, and use of a Telescoping Chute | 0.0013 | LB/TON OF UREA |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Urea Handling Units | 99.11 |  | 1000 | tons urea/hour |  | Particulate matter, fugitive | Unspecified |  | PM | A | Fully Enclosed Conveyors and Fabric Filters | 0.005 | GRAINS/DSCF | 3 STACK TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | MAINTENANCE VEHICLES | 99.19 |  | 0 |  | MAINTENANCE VEHICLES GENERATING FUGITIVE ROAD DUST WHEN TRAVELING ON PAVED AND UNPAVED ROADWAYS IN THE SOLAR FIELD FOR THE PROJECT | Particulate matter, fugitive | Unspecified |  | PM | P | FUGITIVE DUST CONTROL PLAN | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | Duct Burners (4) | 12.31 | Natural Gas | 140 | MMBTU/H | Each duct burner-turbine pair exhaust through a common stack | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 7.6 | LB/MMSCF | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Cost analysis not conducted since cost was not a factor in BACT determination.
AK-0073 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION | ANCHORAGE | AK | 99518 | USA | GREGORY ARTHUR | 907 762 4492 |  | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Kwame Agyei, Permit Engineer, kwame.agyei@alaska.gov | AQ0164CPT01 | 4911 | 221112 | 110046491854 | 04/14/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2012-02-22 | 2014-01-08 | D |  | Power plant that contains four combustion turbines, four duct burners, a black start generator, and an auxiliary heater. |  | Fuel Combustion | 12.31 | Natural Gas | 140 | MMBTU/H | EU IDs 9-12 Duct Burners | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion Turbines EU IDs 9-12 use good combustion practices involve increasing the residence time and excess oxygen to ensure complete combustion which in turn minimize particulates without an add-on control technology. | 7.6 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0073 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION | ANCHORAGE | AK | 99518 | USA | GREGORY ARTHUR | 907 762 4492 |  | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Kwame Agyei, Permit Engineer, kwame.agyei@alaska.gov | AQ0164CPT01 | 4911 | 221112 | 110046491854 | 04/14/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2012-02-22 | 2014-01-08 | D |  | Power plant that contains four combustion turbines, four duct burners, a black start generator, and an auxiliary heater. |  | Fuel Combustion | 12.31 | Diesel | 12.5 | MMBTU/H | Auxiliary Heater | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Combustion Turbines EU ID# 15 uses good combustion practices involve increasing the residence time and excess oxygen to ensure complete combustion which in turn minimize particulates without an add-on control technology. | 7.6 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Three (3) Package Boilers | 12.31 | Natural Gas | 243 | MMBTU/H | Three (3) New Natural Gas-Fired 243 MMBtu/hr Package Boilers | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0074 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Startup Heater | 12.31 | Natural Gas | 101 | MMBTU/H | Natural Gas-Fired 101 MMBtu/hr Startup Heater. Installed in 1976. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0074 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 110 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA METHODS 5 & 202, OR METHODS 201A & 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 0.8 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Startup Heater | 12.31 | Natural gas | 110.12 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0024 | LB/MMBTU | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.01 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Startup Heater | 12.31 | natural gas | 104 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0075 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | FOUR (4) NATURAL GAS-FIRED BOILERS | 12.31 | NATURAL GAS | 218 | MMBTU/HR, EACH | FUEL INPUT TO ALL FOUR BOILERS SHALL NOT EXCEED 2,802 MMCF/YEAR | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | PROPER DESIGN AND GOOD COMBUSTION PRACTICES | 7.6 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | NATURAL GAS AUXILIARY BOILERS (EU-012A, EU-012B, EU-012C) | 12.31 | NATURAL GAS | 218.6 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | PROPER DESIGN AND GOOD COMBUSTION PRACTICES AT ALL TIMES THE BOILERS ARE IN OPERATION. | 7.6 | LB/MMCF EACH | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 2:SHALL COMBUST NATURAL GAS LIMIT 3: EACH SHALL NOT EXCEED 1877.39 MMCF/ 12 MONTH CONSECUTIVE PERIOD
*IN-0287 | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING STATION | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING | KNOX | IN | 47528 | USA | PATRICK COUGHLIN | 317-838-2108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Mehul Sura 317-233-6868 msura@IDEM.IN.gov Section Chief - Tripurari P. Sinha Ph. D. 317-234-4907 | 083-38023-00003 | 4911 | 22 | Not Entered | 12/22/2016 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2018-07-25 | 2018-07-25 | C | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | stationary electric utility generating station |  | Auxiliary Boiler | 12.31 | natural gas | 213 | MMBtu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0075 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This BACT is for Startup and Shutdown emissions only
LA-0229 | SHINTECH PLAQUEMINE PLANT 2 | SHINTECH LOUISIANA LLC | IBERVILLE | LA | 70764 | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-731 | 2821 | 325211 | UNKNOWN | 11/19/2010 &nbsp;ACT | 07/10/2008 &nbsp;ACT | 2009-04-02 | 2009-04-20 | B |  | A PROPOSED 1.81 BILLION LBS/YR PVC PRODUCTION COMPLEX WHICH WILL CONSIST OF A CHLORALKALI PLANT, AN EDC/VCM PLANT, AND A PVC PLANT | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | EQT112, EQT113 - TWO UTIL. BOILERS (2U-1, 2U-2) | 12.31 | NATURAL GAS | 250 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND CLEAN BURNING FUELS | 0.005 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0244 | LAKE CHARLES CHEMICAL COMPLEX - LAB UNIT | SASOL NORTH AMERICA, INC. | CALCASIEU | LA | 70669 | USA | MAGGIE PAGELS | 337-494-5769 | MARGARET.PAGELS@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225) 219-3395 | PSD-LA-291(M3) | 2869 | 325110 | 110017418061 | 09/17/2009 &nbsp;ACT | 11/29/2010 &nbsp;ACT | 2011-03-29 | 2011-07-06 | C |  | Chemical Production Unit for Linear Alkyl Benzene (LAB)production. | Modification to an existing PSD Permit (PSD-LA-291(M2), dated October 18, 1988) to increase operating time of the heater. Emissions will not be increased above the permitted limits. Existing BACT will not be revised. | EQT0029 - Hot Oil Heater H-601 | 12.31 | natural gas | 170 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | No additional control | 1.71 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 | % OPACITY |  | 0 |  |  | 0 | 0 | N |  | BACT was determined in 1983
LA-0275 | LINEAR ALKYL BENZENE (LAB) UNIT | SASOL CHEMICALS (USA) LLC | CALCASIEU | LA | 70669 | USA | ERIC RODRIGUEZ | 281-588-3761 | ERIC.RODRIGUEZ@SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Dan Nguyen, (225) 219-3395 | PSD-LA-291(M4) | 2865 | 325110 | 110017418061 | 10/06/2015 &nbsp;ACT | 04/29/2016 &nbsp;ACT | 2016-06-23 | 2017-04-28 | C |  | LAB production unit, PSD-LA-291(M2) issued October 18, 1998 - PSD-LA-291(M3) issued November 29, 2010. Permit PSD-LA-291(M4) for emission limits revision, No BACT change. |  | Heaters (3 units) | 12.31 | Natural Gas and Ethane | 0 |  | LH-1(H-201): 87.3 MM BTU/hr - fires CH4 & Ethane LH-2(H-202): 21.0 MM BTU/hr - fires CH4 & Ethane LH-3(H-601): 220.5 MM BTU/hr - fires CH4, Ethane, and hydrogen waste gas | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LH-1: 0.86 lbs/hr LH-2: 0.21 lbs/hr LH-3: 1.67 lbs/hr
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Auxiliary boilers | 12.31 | natural gas | 171 | mm btu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | boiler A and B (010 and 011) | 12.31 | natural gas/fuel gas | 248 | mm btu/hr (each) |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices; fueled by natural gas or process fuel gas | 0.007 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | boiler B-201 | 12.31 | natural gas/fuel gas | 229 | mm btu |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices; fueled by natural gas or process fuel gas | 0.007 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MA-0037 | CENTRAL HEATING PLANT: AMHERST CAMPUS | UNIVERSITY OF MASSACHUSETTS BUILDING AUTHORITY | HAMPSHIRE | MA | 1003 | USA |  |  |  | 1 | OT002 | EPA REGION I | MR. BRENDAN MCCAHILL | (617) 918-1652 | MCCAHILL.BRENDAN@EPA.GOV |  | 050-026-MA11 | 361 | 221112 | UNKNOWN | 10/29/2008 &nbsp;ACT | 10/29/2008 &nbsp;ACT | 2009-10-21 | 2010-06-17 | D |  | COMBUSTION TURBINE WITH HEAT RECOVERY STEAM GENERATOR 2 LOW PRESSURE BOILERS 1 HIGH PRESSURE BOILER |  | BOILERS | 12.31 | NATURAL GAS | 162 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.02 | LB/MMBTU | 1-HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | DISTILLATE OIL RATE: 0.030 LBS/MMBTU
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUAUXBOILER (Auxiliary Boiler) | 12.31 | natural gas | 182 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 182 MMBTU/H fuel heat input. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 1.36 | LB/H | HOURLY, TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | At greater than $40,000 for the least expensive option, none of the control technologies are economically feasible. Control technologies evaluated were a scrubber and various types of fabric filters.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUAUXBOILER (Auxiliary boiler) | 12.31 | Natural gas | 182 | MMBTU/H | A natural gas fired auxiliary boiler, rated at 182 MMBTU/H to provide auxiliary steam when the plant is off-line, used to maintain warm drums on the HRSG and maintain the steam turbine generator seals. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0075 | LB/MMBTU |  | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The low concentration of PM / PM10 / PM2.5 in the auxiliary boiler exhaust makes the cost of add-on control very high. Also, of the add-on control options evaluated (pulse jet fabric filter, dry and wet ESP, and venturi scrubber), only the venturi scrubber and wet ESP are expected to be able to effectively reduce condensable PM emissions. The following costs are estimated for the add-on control technologies: â€¢ Fabric Filter Control: over $47,000 per ton controlled (assuming 99.9 percent control of filterable PM/PM10/PM2.5) â€¢ Electrostatic Precipitator (ESP): over $34,000 per ton controlled (assuming 99.4 percent control of filterable PM/PM10/PM2.5) â€¢ Wet ESP: over $29,000 per ton controlled (assuming 99.2 percent control of filterable and condensable PM/PM10/PM2.5) â€¢ Venturi Scrubber: over $20,000 per ton controlled (assuming 99.0 percent control of filterable and condensable PM/PM10/PM2.5)
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Boiler, Nat Gas Fired | 12.31 | NATURAL GAS | 261 | MMBTU/H | 261 MMBTU/H natrual gas-fired boiler, equipped with low-NOx burners, SCR, and CO catalytic oxidation | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 1.31 | LB/H | 3-HR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 261 MMBtU/H natural gas-fired boiler, equipped with natural gas-fired boiler, equipped with low-NOx burners, SCR, and CO catalytic oxidation
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Boiler #1 | 12.31 | natural gas | 200 | MMBTU/H | The boiler is capable of combusting natural gas and Fuel Oil | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0074 | LB/MMBTU | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD | NESHAP | U | 0 | U | 0.024 | LB/MMBTU | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N |  | 0.0074 lb/MMBtu limit applies only when combusting natural gas. 0.024 lb/MMBtu limit applies only when combusting fuel oil
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Boiler #2 | 12.31 | natural gas | 200 | MMBTU/H | The boiler is capable of combusting natural gas and Fuel Oil | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0074 | LB/MMBTU | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD | NESHAP | U | 0 | U | 0.024 | LB/MMBTU | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N |  | 0.0074 lb/MMBtu limit applies only when combusting natural gas. 0.024 lb/MMBtu limit applies only when combusting fuel oil
NM-0052 | ZIA II GAS PLANT | DCP MIDSTREAM L.P. | LEA | NM | 88255 | USA | JENNIFER HANNA | 4326205460 | JHANNA@DCPMIDSTREAM.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Joseph Kimbrell, 505-476-4300, joseph.kimbrell@state.nm.us | PSD-5217 | 1311 | 211111 | 110056438083 | 11/13/2013 &nbsp;ACT | 04/25/2014 &nbsp;ACT | 2015-11-19 | 2016-07-07 | A | https://www.env.nm.gov/aqb/ | Natural Gas Processing plant using cryogenic process and designed to operate at 230 MMscf/day of natural gas. | The permittee submitted an application on 5/13/2015 to revise the permit. Most BACT determinations will not change. | Industrial Sized Boilers/Furnaces &gt;100 mmBtu/hr | 12.31 | Natural gas | 114 | mmBtu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD | SIP , OPERATING PERMIT , NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | AMMONIA CATALYST STARTUP HEATER | 12.39 | NATURAL GAS | 106.3 | MMBTU/H | ANNUAL NATURAL GAS USAGE LIMITED TO 20.84 MMCF. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS COMBUSTION ONLY, PROPER DESIGN AND GOOD COMBUSTION PRACTICES | 7.6 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, VACUUM DEGASSER | 13.29 | NATURAL GAS | 51.2 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACE, ANNEALING PICKLING LINE | 13.29 | NATURAL GAS | 66 | MMBTU/H | ANNEALING PICKLING LINE FURNACE SN-47; ANNEALING COATING LINE FURNACE , SN 51; | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | Sigma Thermal Auxiliary Heater (1) | 13.31 | Natural Gas | 12.5 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 7.6 | LB/MMSCF | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Cost analysis not conducted since cost was not a factor in BACT determination.
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Waste Heat Boilers | 13.31 | Natural Gas | 50 | MMBTU/H | Five (5) Natural Gas-Fired 50 MMBtu/hr Waste Heat Boilers. Installed in 1986. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Limited Use (200 hr/yr) | 0.0074 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, PICKLE LINE | 13.31 | NATURAL GAS | 67 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILERS SN-26 AND 27, GALVANIZING LINE | 13.31 | NATURAL GAS | 24.5 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER EU-002 | 13.31 | NATURAL GAS | 70 | MMBTU/HR |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.522 | LB/H | 3HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 200 | H/YR |  | 0 |  |  | 0 | 0 | N | 2016 | SHALL COMBUST NATURAL GAS
LA-0229 | SHINTECH PLAQUEMINE PLANT 2 | SHINTECH LOUISIANA LLC | IBERVILLE | LA | 70764 | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-731 | 2821 | 325211 | UNKNOWN | 11/19/2010 &nbsp;ACT | 07/10/2008 &nbsp;ACT | 2009-04-02 | 2009-04-20 | B |  | A PROPOSED 1.81 BILLION LBS/YR PVC PRODUCTION COMPLEX WHICH WILL CONSIST OF A CHLORALKALI PLANT, AN EDC/VCM PLANT, AND A PVC PLANT | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | EQT122-EQT125 - FOUR VCM CRACKING FURNACES | 13.31 | NATURAL GAS | 90 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND CLEAN BURNING FUELS | 0.007 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0244 | LAKE CHARLES CHEMICAL COMPLEX - LAB UNIT | SASOL NORTH AMERICA, INC. | CALCASIEU | LA | 70669 | USA | MAGGIE PAGELS | 337-494-5769 | MARGARET.PAGELS@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225) 219-3395 | PSD-LA-291(M3) | 2869 | 325110 | 110017418061 | 09/17/2009 &nbsp;ACT | 11/29/2010 &nbsp;ACT | 2011-03-29 | 2011-07-06 | C |  | Chemical Production Unit for Linear Alkyl Benzene (LAB)production. | Modification to an existing PSD Permit (PSD-LA-291(M2), dated October 18, 1988) to increase operating time of the heater. Emissions will not be increased above the permitted limits. Existing BACT will not be revised. | EQT0027 - PACOL CHARGE HEATER H-201 | 13.31 | Natural Gas | 87.3 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.86 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 | % OPACITY |  | 0 |  |  | 0 | 0 | N |  | BACT was determined in 1983
LA-0244 | LAKE CHARLES CHEMICAL COMPLEX - LAB UNIT | SASOL NORTH AMERICA, INC. | CALCASIEU | LA | 70669 | USA | MAGGIE PAGELS | 337-494-5769 | MARGARET.PAGELS@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225) 219-3395 | PSD-LA-291(M3) | 2869 | 325110 | 110017418061 | 09/17/2009 &nbsp;ACT | 11/29/2010 &nbsp;ACT | 2011-03-29 | 2011-07-06 | C |  | Chemical Production Unit for Linear Alkyl Benzene (LAB)production. | Modification to an existing PSD Permit (PSD-LA-291(M2), dated October 18, 1988) to increase operating time of the heater. Emissions will not be increased above the permitted limits. Existing BACT will not be revised. | EQT0028 - PACOL STARTUP HEATER H-202 | 13.31 | natural gas | 21 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N | No additional Control | 0.21 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 | % OPACITY |  | 0 |  |  | 0 | 0 | N |  | BACT was determined in 1983
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Regenerative Heaters | 13.31 | natural gas | 7.37 | mm btu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGFUELHTR (Two fuel pre-heaters identified as EUFUELHTR1 &amp; EUFUELHTR2) | 13.31 | Natural gas | 27 | MMBTU/H | Two natural gas fired dew point heaters for warming the natural gas fuel (EUFUELHTR1 & EUFUELHTR2 in flexible group FGFUELHTR). The total combined heat input during operation shall not exceed 27 MMBTU/H (each) as well. The CO2e limit is for both units combined; however the other limits are per unit. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.2 | LB/H | HOURLY; EACH FUEL HEATER | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | At greater than $40,000 for the least expensive option, none of the control technologies are economically feasible. Control technologies evaluated were a scrubber and various types of fabric filters and ESPs.
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Regeneration Heater, methanol to gasoline | 13.31 | NATURAL GAS | 13 | MMBTU/H | 13 MMBTU/H methanol-to-gasoline regeneration heater, equipped with low-NOx burner | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | good combustion practices (continuous oxygen trim or annual tune-ups) 13 MMBTU/H methanol-to-gasoline regeneration heater, equipped with low-NOx burner
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Reactor Heater, 5 | 13.31 | NATURAL GAS | 12 | MMBTU/H | Five 12 MMBTU/H reactor heaters, equipped with low-NOx burners | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | good combustion practices (continuous oxygen trim or annual tune-ups) Five 12 MMBTU/H reactor heaters, equipped with low-NOx burners
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Dryer Regenerator Heater - 005 | 13.39 | process fuel gas | 29 | mm btu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices; fueled by process fuel gas | 0.007 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Gas Turbines (8 units) | 15.11 | natural gas | 333 | mm btu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices and fueled by natural gas | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | GE LM6000PF-25 Turbines (4) | 15.21 | Natural Gas | 59900 | hp ISO | Turbine-duct burner pairs exhaust through common stack | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 0.0066 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Cost analysis not conducted since cost was not a factor in BACT determination.
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA METHODS 5 & 202, OR METHODS 201A & 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 0.0048 | LB/MMBTU | 9-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0.0049 | LB/MMBTU | 9-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices, inlet air conditioning, and the use of pipeline quality natural gas. | 19.8 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit in the table above applies to EACH CTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10 which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. Pulse Jet Fabric Filter Baghouse: minimum of $364,528 per ton Mechanical Shaker Fabric Filter Baghouse: minimum of $404,724 per ton Reverse-Air Fabric Filter Baghouse: minimum of $476,689 per ton Dry ESP (Wire-Plate Type): minimum of $478,806 per ton Dry ESP (Wire-Pipe Type): minimum of $303,809 per ton Wet ESP (Wire-Plate Type): minimum of $576,763 per ton Wet ESP (Wire-Pipe Type): minimum of $440,047 per ton Venturi Scrubber: minimum of $1,445,564 per ton
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas, combustion inlet air filter. | 0.0066 | LB/MMBTU |  | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Fabric Filter Control: over $260,000 per ton controlled (assuming 99.9 percent control of filterable PM/PM10/PM2.5). Electrostatic Precipitator (ESP): over $188,000 per ton controlled (assuming 99.4 percent control of filterable PM/PM10/PM2.5). Wet ESP: over $165,000 per ton controlled (assuming 99.2 percent control of filterable and condensable PM/PM10/PM2.5). Venturi Scrubber: over $112,000 per ton controlled (assuming 99.0 percent control of filterable and condensable PM/PM10/PM2.5).
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | Large combustion turbine | 15.21 | Natural Gas | 0 |  | This process entry is for operations with the duct burner. Limits entered are for each turbine. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices with the use of low ash/sulfer fuels | 0.0039 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 11.8 | LB/HR |  | 0 |  |  | 0 | 0 | N
*IN-0287 | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING STATION | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING | KNOX | IN | 47528 | USA | PATRICK COUGHLIN | 317-838-2108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Mehul Sura 317-233-6868 msura@IDEM.IN.gov Section Chief - Tripurari P. Sinha Ph. D. 317-234-4907 | 083-38023-00003 | 4911 | 22 | Not Entered | 12/22/2016 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2018-07-25 | 2018-07-25 | C | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | stationary electric utility generating station |  | combined cycle combustion turbines | 15.25 | natural gas and syn gas | 2129 | MMBtu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 14.3 | TONS/YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This BACT is for Startup and Shutdown emissions only
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Natural Gas Fired Combustion Turbines | 16.11 | Natural Gas | 37.6 | MMBTU/H | Five (5) Natural Gas-Fired Solar Combustion Turbines rated at 37.6 MMBtu/hr each. Installed in 1976. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0074 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MA-0037 | CENTRAL HEATING PLANT: AMHERST CAMPUS | UNIVERSITY OF MASSACHUSETTS BUILDING AUTHORITY | HAMPSHIRE | MA | 1003 | USA |  |  |  | 1 | OT002 | EPA REGION I | MR. BRENDAN MCCAHILL | (617) 918-1652 | MCCAHILL.BRENDAN@EPA.GOV |  | 050-026-MA11 | 361 | 221112 | UNKNOWN | 10/29/2008 &nbsp;ACT | 10/29/2008 &nbsp;ACT | 2009-10-21 | 2010-06-17 | D |  | COMBUSTION TURBINE WITH HEAT RECOVERY STEAM GENERATOR 2 LOW PRESSURE BOILERS 1 HIGH PRESSURE BOILER |  | COMBUSTION TURBINE | 16.2 | NATURAL GAS | 137 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P |  | 0.03 | LB/MMBTU | 1-HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | DISTILLATE OIL EMISSION RATE 0.036 LBS/MMBTU
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | Caterpillar 3215C Black Start Generator (1) | 17.11 | ULSD | 1500 | KW-e |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 0.03 | G/HP-H | INSTANTANEOUS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Cost analysis not conducted since cost was not a factor in BACT determination.
AK-0073 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION | ANCHORAGE | AK | 99518 | USA | GREGORY ARTHUR | 907 762 4492 |  | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Kwame Agyei, Permit Engineer, kwame.agyei@alaska.gov | AQ0164CPT01 | 4911 | 221112 | 110046491854 | 04/14/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2012-02-22 | 2014-01-08 | D |  | Power plant that contains four combustion turbines, four duct burners, a black start generator, and an auxiliary heater. |  | Fuel Combustion | 17.11 | Diesel | 1500 | kW-e | EU 13 Black Start Engine | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Black Start diesel fired engine EU 13 shall be equipped with turbo charging and after cooling. The turbo charger reduces NOx emissions by boosting the pressure and temperature of the air entering the engine allowing more fuel to be added to increase power output. This translates into higher combustion efficiency and reduced emissions. | 0.03 | G/HP-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EMERGENCY GENERATORS | 17.11 | DIESEL | 1500 | KW |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD OPERATING PRACTICES, LIMITED HOURS OF OPERATION, COMPLIANCE WITH NSPS SUBPART IIII | 0.04 | G/KW-H |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.11 | DIESEL | 2683 | HP | UNIT IS 2000 KW. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA METHODS 5 & 202, OR 201A & 202 | (Particulate Matter (PM)) | PM | P | USE ULTRA LOW SULFUR FUEL | 0.2 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Emergency Generator | 17.11 | diesel fuel | 142 | GAL/H | rated @ 2,000 KW | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.2 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.22 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Emergency Generator | 17.11 | distillate fuel oil | 3755 | HP |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 0.1 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY GENERATOR | 17.11 | NO. 2 FUEL OIL | 4690 | B-HP | ANNUAL HOURS OF OPERATION NOT TO EXCEED 200 HOURS. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | EMERGENCY GENERATORS (EU014A AND EU-014B) | 17.11 | DISTILLATE OIL | 3600 | HP EACH |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-H EACH | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 500 | H/YR EACH |  | 0 |  |  | 0 | 0 | N | 2016
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Diesel Engines | 17.11 | Diesel | 0 |  | Water Pumps (2 units) = 355 hp Tank Deluge Pumps (2 units) = 800 hp Generator = 1340 hp | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices, Use ultra low sulfur diesel, and comply with 40 CFR 60 Subpart IIII | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0389 | KARN WEADOCK GENERATING COMPLEX | CONSUMERS ENERGY | BAY | MI | 48732-9601 | USA | JAMES M. WALKER | 5177880428 | JMWALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | FOR TECHNICAL QUESTIONS ABOUT THIS PERMIT, PLEASE CONTACT THE PERMIT ENGINEER - DAVID K. RIDDLE RIDDLED@MICHIGAN.GOV (517-373-7081) | 341-07 | 4911 | 221112 | 26-01700033 | 10/15/2007 &nbsp;ACT | 12/29/2009 &nbsp;ACT | 2010-03-08 | 2010-12-16 | U |  | ELECTRICITY GENERATING FACILITY, EXISTING CAPACITY GREATER THAN 2,000 MW. | AFTER CONSTRUCTION CONSUMERS WILL RETIRE 5 TO 7 COAL-FIRED BOILERS (638 - 958 MW) STATEWIDE. FINAL CONDITIONS WILL BE AT WWW.DEQ.STATE.MI.US/APS/FINALCONDITIONS.SHTML. MATERIAL HANDLING - CONTACT PERMIT ENGINEER FOR TECHNICAL INFORMATION (DAVID RIDDLE, 517-373-7081). INCLUDES 9 EMISSION UNITS. COAL, LIMESTONE, SORBENT AND ASH HANDLING PROCESSES. VARIOUS BACT LIMITS FOR OPACITY, PM AND PM10. BACT FOR THE MATERIAL HANDLING EQUIPMENT CONSISTED OF A COMBINATION OF PASSIVE CONTROL EQUIPMENT SUCH AS WET/CHEMICAL SUPPRESSION SYSTEMS AND ENCLOSED CONVEYORS; AND ACTIVE CONTROL SUCH AS FABRIC FILTERS. ACTIVE CONTROL IS LIMITED TO 0.004 GR/DSCF. | FIRE PUMP | 17.11 | ULTRA LOW SULFUR DIESEL | 525 | HP | OPERATIONAL LIMITS: 1 HOUR/DAY AND 500 HRS/YEAR FOR PM2.5 NAAQS. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | ENGINE DESIGN AND OPERATION. 15 PPM SULFUR FUEL. | 0.31 | LB/MMBTU | TEST METHOD | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0389 | KARN WEADOCK GENERATING COMPLEX | CONSUMERS ENERGY | BAY | MI | 48732-9601 | USA | JAMES M. WALKER | 5177880428 | JMWALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | FOR TECHNICAL QUESTIONS ABOUT THIS PERMIT, PLEASE CONTACT THE PERMIT ENGINEER - DAVID K. RIDDLE RIDDLED@MICHIGAN.GOV (517-373-7081) | 341-07 | 4911 | 221112 | 26-01700033 | 10/15/2007 &nbsp;ACT | 12/29/2009 &nbsp;ACT | 2010-03-08 | 2010-12-16 | U |  | ELECTRICITY GENERATING FACILITY, EXISTING CAPACITY GREATER THAN 2,000 MW. | AFTER CONSTRUCTION CONSUMERS WILL RETIRE 5 TO 7 COAL-FIRED BOILERS (638 - 958 MW) STATEWIDE. FINAL CONDITIONS WILL BE AT WWW.DEQ.STATE.MI.US/APS/FINALCONDITIONS.SHTML. MATERIAL HANDLING - CONTACT PERMIT ENGINEER FOR TECHNICAL INFORMATION (DAVID RIDDLE, 517-373-7081). INCLUDES 9 EMISSION UNITS. COAL, LIMESTONE, SORBENT AND ASH HANDLING PROCESSES. VARIOUS BACT LIMITS FOR OPACITY, PM AND PM10. BACT FOR THE MATERIAL HANDLING EQUIPMENT CONSISTED OF A COMBINATION OF PASSIVE CONTROL EQUIPMENT SUCH AS WET/CHEMICAL SUPPRESSION SYSTEMS AND ENCLOSED CONVEYORS; AND ACTIVE CONTROL SUCH AS FABRIC FILTERS. ACTIVE CONTROL IS LIMITED TO 0.004 GR/DSCF. | EMERGENCY GENERATOR | 17.11 | ULTRA LOW SULFUR DIESEL | 2000 | KW | 2980 HP. OPERATIONAL LIMITS: 1 HR/DAY, 500 HRS/YR FOR PM2.5 NAAQS. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | ENGINE DESIGN AND OPERATION. 15 PPM SULFUR FUEL. | 0.0573 | LB/MMBTU | TEST METHOD | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUEMENGINE (Diesel fuel emergency engine) | 17.11 | Diesel Fuel | 22.68 | MMBTU/H | a 2,922 horsepower (HP) (2,179 kilowatts (kW)) diesel fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Restricted to 4 hours/day, except during emergency conditions and stack testing, and 500 hours/year on a 12-month rolling time period basis. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 1.58 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Diesel Fired Well Pump | 17.21 | Diesel | 2.7 | MMBTU/H | 2.7 MMBtu/hr Diesel Fired Well Pump. Installed in 1966. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Limited Operation of 168 hr/yr. | 0.31 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.21 | DIESEL | 182 | HP | UNIT IS 135 KW. | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA METHODS 5 & 202, OR 201A & 202 | (Particulate Matter (PM)) | PM | P | USE ULTRA LOW SULFUR FUEL | 0.2 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.2 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.03 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 0.1 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel Firewater pump engines (6 units) | 17.21 | diesel | 425 | hp |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel emergency generator engine - EGEN | 17.21 | diesel | 350 | hp |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0389 | KARN WEADOCK GENERATING COMPLEX | CONSUMERS ENERGY | BAY | MI | 48732-9601 | USA | JAMES M. WALKER | 5177880428 | JMWALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | FOR TECHNICAL QUESTIONS ABOUT THIS PERMIT, PLEASE CONTACT THE PERMIT ENGINEER - DAVID K. RIDDLE RIDDLED@MICHIGAN.GOV (517-373-7081) | 341-07 | 4911 | 221112 | 26-01700033 | 10/15/2007 &nbsp;ACT | 12/29/2009 &nbsp;ACT | 2010-03-08 | 2010-12-16 | U |  | ELECTRICITY GENERATING FACILITY, EXISTING CAPACITY GREATER THAN 2,000 MW. | AFTER CONSTRUCTION CONSUMERS WILL RETIRE 5 TO 7 COAL-FIRED BOILERS (638 - 958 MW) STATEWIDE. FINAL CONDITIONS WILL BE AT WWW.DEQ.STATE.MI.US/APS/FINALCONDITIONS.SHTML. MATERIAL HANDLING - CONTACT PERMIT ENGINEER FOR TECHNICAL INFORMATION (DAVID RIDDLE, 517-373-7081). INCLUDES 9 EMISSION UNITS. COAL, LIMESTONE, SORBENT AND ASH HANDLING PROCESSES. VARIOUS BACT LIMITS FOR OPACITY, PM AND PM10. BACT FOR THE MATERIAL HANDLING EQUIPMENT CONSISTED OF A COMBINATION OF PASSIVE CONTROL EQUIPMENT SUCH AS WET/CHEMICAL SUPPRESSION SYSTEMS AND ENCLOSED CONVEYORS; AND ACTIVE CONTROL SUCH AS FABRIC FILTERS. ACTIVE CONTROL IS LIMITED TO 0.004 GR/DSCF. | FIRE BOOSTER PUMP | 17.21 | ULTRA LOW SULFUR DIESEL | 40 | KW | OPERATIONAL LIMITS 1 HR/DAY AND 500 HRS/YR FOR PM2.5 NAAQS. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | ENGINE DESIGN AND OPERATION. 15 PPM SULFUR FUEL. | 0.31 | LB/MMBTU | TEST METHOD | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.57 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | firewater pumps, diesel | 17.21 | diesel | 325 | HP, EACH | Eight 325 hp diesel firewater pumps | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | comply with NSPS IIII, 52 hr/yr non-emergency operation
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Gasoline Fired Fire Pump Engine | 17.22 | Gasoline | 2.1 | MMBTU/H | 2.1 MMBtu/hr Gasoline-Fired Fire Pump Engine. Installed in 1978. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Limited Operation of 168 hr/yr. | 0.1 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | SMALL HEATERS AND DRYERS SN-05 THROUGH 19 | 17.23 | NATURAL GAS | 0 |  | RH VESSEL PREHEATER STATION, VESSEL TOP PART DRYER, RH VESSEL NOZZLE DRYER RH DEGASSER BURNER/LANCE LADLE PREHEATERS LADLE DRYOUT STATION VERTICAL LADLE HOLDING STATION TUNDISH PREHEATERS #1 THROUGH #4 | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0389 | KARN WEADOCK GENERATING COMPLEX | CONSUMERS ENERGY | BAY | MI | 48732-9601 | USA | JAMES M. WALKER | 5177880428 | JMWALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | FOR TECHNICAL QUESTIONS ABOUT THIS PERMIT, PLEASE CONTACT THE PERMIT ENGINEER - DAVID K. RIDDLE RIDDLED@MICHIGAN.GOV (517-373-7081) | 341-07 | 4911 | 221112 | 26-01700033 | 10/15/2007 &nbsp;ACT | 12/29/2009 &nbsp;ACT | 2010-03-08 | 2010-12-16 | U |  | ELECTRICITY GENERATING FACILITY, EXISTING CAPACITY GREATER THAN 2,000 MW. | AFTER CONSTRUCTION CONSUMERS WILL RETIRE 5 TO 7 COAL-FIRED BOILERS (638 - 958 MW) STATEWIDE. FINAL CONDITIONS WILL BE AT WWW.DEQ.STATE.MI.US/APS/FINALCONDITIONS.SHTML. MATERIAL HANDLING - CONTACT PERMIT ENGINEER FOR TECHNICAL INFORMATION (DAVID RIDDLE, 517-373-7081). INCLUDES 9 EMISSION UNITS. COAL, LIMESTONE, SORBENT AND ASH HANDLING PROCESSES. VARIOUS BACT LIMITS FOR OPACITY, PM AND PM10. BACT FOR THE MATERIAL HANDLING EQUIPMENT CONSISTED OF A COMBINATION OF PASSIVE CONTROL EQUIPMENT SUCH AS WET/CHEMICAL SUPPRESSION SYSTEMS AND ENCLOSED CONVEYORS; AND ACTIVE CONTROL SUCH AS FABRIC FILTERS. ACTIVE CONTROL IS LIMITED TO 0.004 GR/DSCF. | FLUE GAS DESULFURIZATION QUENCH PUMP | 17.23 | ULTRA LOW SULFUR DIESEL | 305 | KW | 455 HP. OPERATIONAL LIMITS: 1 HR/DAY, 500 HRS/YR FOR PM2.5 NAAQS. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | ENGINE DESIGN AND OPERATION. 15 PPM SULFUR FUEL. | 0.31 | LB/MMBTU | TEST METHOD | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0229 | SHINTECH PLAQUEMINE PLANT 2 | SHINTECH LOUISIANA LLC | IBERVILLE | LA | 70764 | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-731 | 2821 | 325211 | UNKNOWN | 11/19/2010 &nbsp;ACT | 07/10/2008 &nbsp;ACT | 2009-04-02 | 2009-04-20 | B |  | A PROPOSED 1.81 BILLION LBS/YR PVC PRODUCTION COMPLEX WHICH WILL CONSIST OF A CHLORALKALI PLANT, AN EDC/VCM PLANT, AND A PVC PLANT | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | EQT126, EQT127 - TWO THERMAL OXIDIZERS (2M-5, 2M-6) | 19.2 | NATURAL GAS | 72 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICE AND CLEAN BURNING FUELS | 0.0077 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Three (3) Flares | 19.31 | Natural Gas | 1.25 | MMBTU/H | 1.25 MMBtu/hr Ammonia Tank Flare, 0.4 MMBtu/hr Emergency Flare, and 1.25 MMBtu/hr Small Flare | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Work Practice Requirements and Limited Use (limit venting to 168 hr/yr each during startup, shutdown, and maintenance events) | 0.0074 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Ammonia Flare | 19.31 | natural gas | 0.4 | MMBTU/H | There are four (4) natural gas pilots | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | work practice/good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | There is no numeric emission limit in the permit.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | FRONT END PROCESS FLARE | 19.31 | NATURAL GAS PILOT | 0.25 | MMBTU/H | HEAT INPUT IS FOR NATURAL GAS PILOT ONLY. SSM EMISSIONS ARE CONTROLLED BY THE FLARE AND ARE LIMITED TO 336 HOURS OF VENTING PER YEAR. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS FOR PILOT, AND FLARE MINIMIZATION PRACTICES | 0.0075 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO ADDITIONAL PM10 EMISSIONS DURING VENTING EVENTS
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | BACK END AMMONIA FLARE | 19.31 | NATURAL GAS | 0.25 | MMBTU/H | HEAT INPUT IS FOR PILOT ONLY. SSM EMISSIONS ARE CONTROLLED BY THE FLARE AND ARE LIMITED TO 336 HR/YR. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.0075 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO ADDITIONAL EMISSIONS FOR SSM EVENTS.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | AMMONIA STORAGE FLARE | 19.31 | NATURAL GAS | 0.13 | MMBTU/H | HEAT INPUT IS FOR PILOT ONLY. SSM EVENTS HAVE SEPARATE LIMITS. SSM VENTING IS LIMITED TO 168 HOURS PER YEAR. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.0075 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | SSM EVENTS ARE LIMITED TO 168 HR PER YEAR.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | UAN PLANT VENT FLARE | 19.31 |  | 0.19 | MMBTU/H | HEAT INPUT IS FOR NATUAL GAS PILOT. SSM EMISSIONS HAVE SEPARATE LIMITS. SSM VENTING LIMITED TO 336 HOURS PER YEAR. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.0075 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0244 | LAKE CHARLES CHEMICAL COMPLEX - LAB UNIT | SASOL NORTH AMERICA, INC. | CALCASIEU | LA | 70669 | USA | MAGGIE PAGELS | 337-494-5769 | MARGARET.PAGELS@US.SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225) 219-3395 | PSD-LA-291(M3) | 2869 | 325110 | 110017418061 | 09/17/2009 &nbsp;ACT | 11/29/2010 &nbsp;ACT | 2011-03-29 | 2011-07-06 | C |  | Chemical Production Unit for Linear Alkyl Benzene (LAB)production. | Modification to an existing PSD Permit (PSD-LA-291(M2), dated October 18, 1988) to increase operating time of the heater. Emissions will not be increased above the permitted limits. Existing BACT will not be revised. | EQT0026 - LAB Unit Flare LF-1 | 19.31 | Natural Gas | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Steam assisted | 0.37 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 | % OPACITY |  | 0 |  |  | 0 | 0 | N |  | BACT was determined in 1983
LA-0275 | LINEAR ALKYL BENZENE (LAB) UNIT | SASOL CHEMICALS (USA) LLC | CALCASIEU | LA | 70669 | USA | ERIC RODRIGUEZ | 281-588-3761 | ERIC.RODRIGUEZ@SASOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Dan Nguyen, (225) 219-3395 | PSD-LA-291(M4) | 2865 | 325110 | 110017418061 | 10/06/2015 &nbsp;ACT | 04/29/2016 &nbsp;ACT | 2016-06-23 | 2017-04-28 | C |  | LAB production unit, PSD-LA-291(M2) issued October 18, 1998 - PSD-LA-291(M3) issued November 29, 2010. Permit PSD-LA-291(M4) for emission limits revision, No BACT change. |  | LF-1 - LAB Unit Flare | 19.31 | Natural Gas | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | steam assisted | 0.4 | LBS/HR | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Flare No. 1 - 008 | 19.31 | natural gas | 85097 | MM BTU/yr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | complying with 40 CFR 60.18; good combustion practices (including establishment of flare minimization practices); steam assisted | 0.007 | LB/MM BTU |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Pyrolysis Gasoline Tank Flare - 009 | 19.31 | natural gas | 0.66 | mm btu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | complying with 40 CFR 60.18 and 63.11; good combustion practices (including establishment of flare minimization practices); steam assisted | 0.007 | LB/MM BTU |  | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | vessel evacuation flare - 018 | 19.31 | natural gas | 3.04 | mm btu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices (including establishment of flare minimization practices) | 0.007 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | AMMONIA STORAGE FLARE (EU-016) | 19.39 | NATURAL GAS | 1.1 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0075 | LB/MMBTU | 3 HR AVG. | BACT-PSD |  |  | 0 |  | 168 | H/12 CONSEC. MONTH | COMPLIANCE DETERMINED AT END OF EA MONTH | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS SHALL BE NATURAL GAS LIMIT 4: SHALL COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUT DOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT THE PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) SHALL TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND TEH SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DURING ANY 2 CONSEC. HRS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMACOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FRONT END FLARE EU-017 | 19.39 | NATURAL GAS | 1.12 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 7.6 | LB/MMCF | 3 HR AVG | BACT-PSD |  | N | 0 |  | 336 | H/12 CONSEC. MONTH | VENTING | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS USED SHALL BE NATURAL GAS LIMIT 4: COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUTDOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ROOT CAUSE ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DUING ANY 2 CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMOCOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | BACK END FLARE (EU-018) | 19.39 | NATURAL GAS | 1.12 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0075 | LB/MMBTU | 3 HR AVG. | BACT-PSD |  | N | 0 |  | 336 | HR/12 CONSEC. MONTH |  | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS USED SHALL BE NATURAL GAS LIMIT 4: COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUTDOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ROOT CAUSE ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DUING ANY 2 CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMOCOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE.
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | flares | 19.39 | natural gas | 7.33 | kg/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | AUXILIARY HEATER | 19.6 | NATURAL GAS | 40 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - EPA METHODS 5 & 202, OR 201A & 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY PIPELINE NATURAL GAS | 0.3 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EMERGENCY GENERATOR SN-62 | 19.8 | DIESEL | 625 | HP |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD OPERATING PRACTICES, LIMITED HOURS OF OPERATION, COMPLIANCE WITH NSPS SUBPART IIII | 0.02 | G/KW-H |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0229 | SHINTECH PLAQUEMINE PLANT 2 | SHINTECH LOUISIANA LLC | IBERVILLE | LA | 70764 | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-731 | 2821 | 325211 | UNKNOWN | 11/19/2010 &nbsp;ACT | 07/10/2008 &nbsp;ACT | 2009-04-02 | 2009-04-20 | B |  | A PROPOSED 1.81 BILLION LBS/YR PVC PRODUCTION COMPLEX WHICH WILL CONSIST OF A CHLORALKALI PLANT, AN EDC/VCM PLANT, AND A PVC PLANT | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | EQT115, 116, 121, 129 - EMERGENCY IC ENGINES | 19.8 |  |  |  | SIZES AND FUELS: TO BE DETERMINED | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | MAINTAIN WRITTEN OPERATING AND MAINTENANCE PROCEDURES; PROPERLY TRAINED OPERATING PERSONNEL; MAINTAINING APPROPRIATE FUEL-TO AIR RATIO; AND PROPER DESIGN, FUEL HANDLING, SIZING, AND COMBUSTION AIR AND FUEL DISTRIBUTION | 0.0022 | LB/HP-H | FOR ENGINES < 600 HP | BACT-PSD |  | U | 0 | U | 0.0007 | LB/HP-H | FOR ENGINES > 600 HP | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Steam Methane Reformer | 50.002 | NATURAL GAS | 10 | MMSCFH | Steam Methane Reformer, equipped with low NOx burners, SCR, and CO oxidation catalyst | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 1.88 | LB/H | 3-HR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Steam Methane Reformer, equipped with low NOx burners, SCR, and CO oxidation catalyst
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Thermal oxidizers (2 units) | 50.008 | natural gas | 21 | mm btu/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Two (2) Urea Granulation Units | 61.012 |  | 1200 | T/D | Two (2) Urea Granulation Units rated at 1200 tons per day (each). | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | Wet Scrubber | 0.2 | LB/TON OF UREA |  | BACT-PSD |  | U | 90 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Primary Reformer | 61.012 | natural gas | 1.13 | million cubic feet/h |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0024 | LB/MMTU | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 11.9 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Urea Granulator | 61.012 |  | 1500 | metric tons/day |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | A | Wet Scrubber | 0.1 | KG/METRIC TON | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 60.4 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Ammonia Plant, Flares | 61.012 | natural gas | 2789 | tpd |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Reformer Furnace | 61.012 | natural gas | 955 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0024 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Ammonia Pressure Tanks | 61.012 |  | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | Flare; flare minimization | 0.25 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Urea Plant | 61.012 |  | 4880 | tpd | while the urea granulator in the urea plant is the principal emitter, there are other units that contribute. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | 2-stage scrubbing system with high efficiency venturi scrubber | 0.121 | LB/TON UREA | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Cooling Tower | 61.012 |  | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | drift eliminators; TDS of water not to exceed 2000 mg/l | 0.0005 | % LOSS FROM CIRC. |  | BACT-PSD |  | U | 0 | U | 0.6 | LB/H | 24-HOUR AVERAGE | 2.47 | TPY |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | PRIMARY REFORMER | 61.012 | NATURAL GAS | 1006.4 | MMBTU/H | NOX CEMS | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 7.6 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | TWO (2) AMMONIUM NITRATE UNITS | 61.012 |  | 798 | TON AN PER DAY, EACH | UAN PRODUCTION IS LIMITED TO 1,314,000 TONS PER YEAR. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | WET SCRUBBER WITH HIGH EFFICIENCY DEMISTER | 0.0128 | LB/TON UAN | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | UREA GRANULATION UNIT (EU-008) | 61.012 |  | 1320 | METRIC TON/DAY |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | WET SCRUBBER | 0.163 | LB/TON | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 368040 | TON/12 CONSEC. MONTH |  | 0 |  |  | 0 | 0 | N | 2016
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | TRUCK AND RAIL LOADING OPERATION (EU-021A) | 61.012 |  | 4800 | METRIC TON/DAY |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | BAGHOUSE | 0.15 | LB/H | 3 HR AVG. | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N | 2016
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Cooling Tower | 61.999 |  | 0 |  | There are 2 cooling towers. One has 6 cells with a total flowrate of 74,040 gal/min and the other has 9 cells with a total flowrate of 111,060 gal/min | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | A | drift eliminator | 0.0005 | % |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | There is no numerical emission limit. The drift eliminator is required to have a control efficiency of 0.0005%.
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Granulated Urea Transfer | 61.999 |  | 1500 | metric tons/day | There are six (6) different emission points. The transfer points are for the warehouse, train loading, and truck loading. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | A | bin vent filter | 0.005 | GR/DSCF | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The ton/yr limit varies for each of the 6 emission points depending on the flowrate.
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Modular Ethylene Cracking Furnaces - 001 | 64.003 | natural gas/fuel gas | 1028 | MM BTU/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices; fueled by natural gas or process fuel gas | 0.007 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Ethylene Cracking Furnace - 015 | 64.003 | natural gas/fuel gas | 168 | mm btu |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices, fueled by natural gas and/or fuel gas | 0.007 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Grain Dryer | 70.21 |  | 300 | ton/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD | NSPS | U | 0 | U | 6.44 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Grain Receiving and Handling | 70.23 |  | 20000 | bu/hr | 6 units routed to 1 stack. Grain Truck Dump Pit #1, Grain Elevator #1, Grain Truck Dump Pit #2, Grain Elevator #2, Conveyor #1, and Scalper | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0.82 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Mill Feed Receiving | 70.23 |  | 12 | ton/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.03 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Grain Receiving via Rail | 70.29 |  | 720 | ton/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Millfeed | 70.29 |  | 106.25 | ton/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.03 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.72 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Rotary Conditioner | 70.29 |  | 106.25 | ton/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.061 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.16 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Flaker with Process Cyclone | 70.29 |  | 106.25 | ton/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.008 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.59 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Meal Grinding | 70.29 |  | 106.25 | ton/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.39 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Meal Bin #36 | 70.29 |  | 106.25 | ton/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.08 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Pellet and Hull Storage Bins | 70.29 |  | 20 | ton/hr | 2 Pellet storage bins and 2 Hull storage bins | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.08 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Grain Cleaning | 70.29 |  | 300 | ton/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD | NSPS | U | 0 | U | 0.44 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Dryer/Cooler | 70.29 |  | 106.25 | ton/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | Wet Venturi Scrubber | 0.0025 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.71 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | DDGS and Pellet Storage/loadout | 70.29 |  | 250 | ton/hr | 4 units routed to 1 stack. DDGS/Pellet Storage Building, Dump pit/conveyor, Bridge Conveyor, Loadout Conveyor | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.75 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Pellet Cooler | 70.29 |  | 22 | ton/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD |  | U | 0 | U | 0.2 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EAFS SN-01 AND SN-02 | 81.21 | NATURAL GAS | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | BAGHOUSE FOR FILTERABLE | 0.0024 | GR/DSCF | 3 HR | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | ANNEALING COATING CLEANING SECTION, SN-52 | 81.23 |  | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | MIST ELIMINATOR | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | LMFS SN-01 AND SN-02 | 81.29 | NATURAL GAS | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | FABRIC FILTER | 0.0024 | GR/DSCF | 3 HR | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | RH DEGASSER | 81.29 | NATURAL GAS | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | SCALE EXHAUST, PICKLE LINE | 81.29 |  | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | FABRIC FILTER | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | DUST EXHAUST SN-23A, TENSION LEVELER | 81.29 |  | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | FABRIC FILTER | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | COLD MILL REVERSING COLD MILL AND SKIN PASS MILL SN-25, 38, 44, 45, AND 46 | 81.29 |  | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | MIST ELIMINATOR | 0.0066 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | GALVANIZING LINE CAUSTIC CLEANING AND POST TREATMENT SN-34 THROUGH 37 | 81.29 |  | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | MIST ELIMINATOR | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-39, ANNEALING | 81.29 | NATURAL GAS | 98.25 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | DECARBURIZING LINE CLEANING SECTIONS SN-41 AND 43 | 81.29 |  | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | MIST ELIMINATOR | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | ANNEALING PICKLING LINE SCALE DUST AND SHOTBLAST | 81.29 |  | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | FABRIC FILTER | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | ANNEALING COATING LINE FURNACE SECTION | 81.29 | NATURAL GAS | 50 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACE, SN-53, ANNEALING COATING LINE DRYING | 81.29 | NATURAL GAS | 38 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | DRYERS, MGO COATING LINE | 81.29 | NATURAL GAS | 38 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | MGO COATING CLEANING SECTIONS SN-55 AND 57 | 81.29 |  | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | MIST ELIMINATOR | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-58 AND 60, FINAL ANNEALING AND COATING LINE | 81.29 | NATURAL GAS | 32 | MMBTU/H |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | TWO (2) COOLING TOWERS | 99.009 |  | 179720 | GPM, COMBINED | ONE UNIT IS EIGHT CELL, THE OTHER IS SIX CELL. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | HIGH EFFICIENCY DRIFT ELIMINATORS | 0.005 | % DRIFT | CONTINUOUS | BACT-PSD |  | Y | 0 |  | 2000 | MG/L TDS | CONTINUOUS | 0 |  |  | 4592 | 0 | N | 2012 | TOWERS USE ONSITE WELL WATER. IT IS HAS HIGHER THAN NORMAL TDS. COST EFFECTIVENESS BASED ON REDUCTION OF TDS FROM 2,000 MG/L TO 1,500 MG/L. ADVERSE ENVIRONMENTAL IMPACTS WERE CONSIDERED.
LA-0229 | SHINTECH PLAQUEMINE PLANT 2 | SHINTECH LOUISIANA LLC | IBERVILLE | LA | 70764 | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-731 | 2821 | 325211 | UNKNOWN | 11/19/2010 &nbsp;ACT | 07/10/2008 &nbsp;ACT | 2009-04-02 | 2009-04-20 | B |  | A PROPOSED 1.81 BILLION LBS/YR PVC PRODUCTION COMPLEX WHICH WILL CONSIST OF A CHLORALKALI PLANT, AN EDC/VCM PLANT, AND A PVC PLANT | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | EQT120 COOLING TOWER (2C-4) | 99.009 |  | 38750 | GAL/MIN |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD DESIGNS, GOOD MAINTENANCE, AND MIST ELIMINATORS | 0.08 | LB/MMGAL |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0229 | SHINTECH PLAQUEMINE PLANT 2 | SHINTECH LOUISIANA LLC | IBERVILLE | LA | 70764 | USA | DAVID WISE | 2256851113 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-731 | 2821 | 325211 | UNKNOWN | 11/19/2010 &nbsp;ACT | 07/10/2008 &nbsp;ACT | 2009-04-02 | 2009-04-20 | B |  | A PROPOSED 1.81 BILLION LBS/YR PVC PRODUCTION COMPLEX WHICH WILL CONSIST OF A CHLORALKALI PLANT, AN EDC/VCM PLANT, AND A PVC PLANT | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS | EQT128 - COOLING TOWER (2M-7) | 99.009 |  | 106000 | GAL/MIN |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD DESIGN, GOOD MAINTENANCE, AND MIST ELIMINATORS | 0.06 | LB/MMGAL |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | cooling towers - 007 | 99.009 |  | 86500 | gpm |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | drift eliminators | 0.0005 | % | DRIFT RATE | BACT-PSD |  | U | 0 | U | 1400 | PPM | TDS | 0 |  |  | 0 | 0 | N
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCOOLTWR (Cooling Tower--Wet Mechanical Drift) | 99.009 |  | 0 |  | A four-cell evaporative cooling tower in series with mechanical chilling to cool turbine inlet air. Particulate emissions will be controlled with high efficiency drift eliminators. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | Mist/Drift Eliminators | 0.0006 | % | VENDOR-CERTIF. MAX DRIFT RATE | BACT-PSD | SIP | N | 0 | N | 7700 | PPM | MAX TDS IN COOLING WATER | 0 |  |  | 0 | 0 | N |  | Emission limit 1 above is 0.0006 percent with vendor-certified maximum drift rate. Emission limit 2 above is 7700 ppmw, maximum Total Dissolved Solids (TDS) in cooling water. The estimated efficiency is to reduce drift loss to 0.0006. There are no BACT emission limits in the permit, but there is a requirement for the permittee to equip and maintain EUCOOLTWR with mist/drift eliminators with a vendor-certified maximum drift rate of 0.0006 percent or less, and there is also a limit of 7700 ppmw maximum Total Dissolved Solids (TDS) in cooling water.
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Cooling tower, Induced draft | 99.009 |  | 1420 | GAL/MIN |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | high efficiency drift eliminators | 0.001 | % | DRIFT RATE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Cooling Tower | 99.009 |  | 159000 | gpm |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.5 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | 2 Cell Cross-Flow Cooling Tower | 99.11 |  | 15000 | gallons per minute | 2 Cell Cross-Flow Cooling Tower | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | High Efficiency Drift Eliminators | 0.002 | % DRIFT |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Urea Ship Loading | 99.11 |  | 1000 | tons urea/hour | The Urea Ship Loading Operations are conveyor systems used to load products from the Urea Plant into ships. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of UF-85 (Hardening Agent), Product Coolers on Granulation Urea Process Lines, Loading into Partial Enclosure, and use of a Telescoping Chute. | 0.0011 | LB/TON OF UREA |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Urea Handling Units | 99.11 |  | 1000 | tons urea/hour |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | Fully Enclosed Conveyors and Fabric Filters | 0.005 | GRAINS/DSCF | 3 STACK TEST AVERAGE | BACT-PSD |  | U | 99 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Haul Roads | 99.14 |  | 0 |  | There are two (2) paved haul roads. The length of one is 0.97 miles and the other is 1.07 miles long. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | paved road, water flushing, and sweeping | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | There is no numeric emission limit in the permits.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | PAVED ROADWAYS AND PARKING LOTS WITH PUBLIC ACCESS | 99.14 |  | 17160 | VEHICLE MILES TRAVELED |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | PAVE ALL PLANT HAUL ROADS, DAILY SWEEPING AND WET SUPPRESSION, PROMPT CLEANUP OF ANY SPILLED MATERIAL | 90 | % CONTROL | CONTINUOUS | BACT-PSD |  | N | 90 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | PAVED ROADS AND PARKING LOTS | 99.19 |  | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | PAVING ALL PLANT HAUL ROADS, WET SUPPRESSION, PROMPT CLEANUP OF ANY SPILLED MATERIALS. | 0 |  |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N | 2016
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COOLING TOWER | 99.999 |  | 130000 | GAL/MIN CIRCULATION RATE |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Other - MODIFIED METHOD 306 OR COOLING TOWER INSTITUTE TEST METHOD | (Particulate Matter (PM)) | PM | N |  | 1.6 | LB/H |  | BACT-PSD |  | U | 0 | U | 0.0005 | % DRIFT |  | 5000 | 5000 PPM TDS |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | EIGHTEEN CELL COOLING TOWER (EU-010) | 99.999 |  | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | HIGH EFFICIENCY DRIFT ELIMINATORS | 2000 | MG/L | AVG. ON A MONTHLY BASIS | BACT-PSD |  | N | 0 |  | 0.0005 | % | DRIFT | 0 |  |  | 0 | 0 | N | 2016
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | 245 MMBtu natural gas fired Auxiliary boiler | 12.31 | Natural Gas | 1052 | MMscf/yr | Total fuel usage of the auxiliary boiler shall not exceed 1052 MMsch/yr on a 12-month rolling basis | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practice | 0.0075 | LB/MMBTU | 3 HR AVG | LAER | NSPS | U | 0 | U | 4 | TPY |  | 0 |  |  | 0 | 0 | N
OH-0354 | KRATON POLYMERS U.S. LLC | KRATON POLYMERS U.S. LLC | WASHINGTON | OH | 45714-0235 | USA | DALE LOUDERMILK | 740-423-2299 | DALE.LOUDERMILK@KRATON.CC | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0108853 | 2822 | 325212 | 110030900997 | 08/29/2012 &nbsp;ACT | 01/15/2013 &nbsp;ACT | 2013-09-27 | 2016-05-04 | B |  | Thermoplastic elastomer manufacturing facility | Two new 249 MMBtu/hour natural gas, distillate oil, and belpre naphtha-fired boilers installed to replace 2 existing coal, distillate oil, and belpre naphtha-fired boilers. | Two 249 MMBtu/H boilers | 12.31 | Natural Gas | 249 | MMBtu/H | Two boilers, burning natural gas or distillate oil w/ less than 0.05% sulfur; and co-fired with maximum of 54.8 MMBtu/H Belpre naphtha. Fitted with low-NOx burners with flue gas recirculation, as needed. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 15.96 | T/YR |  | N/A | SIP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Netted out for PM10 by replacing old coal/oil-fired boilers.
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | AUXILIARY BOILER (1) AND FUEL GAS HEATERS (6) | 12.31 | NATURAL GAS | 185 | MMBTU/HR | The auxiliary boiler will provide steam to the steam turbine at startup and at cold starts to warm up the ST rotor. The steam from the auxiliary boiler will not be used to augment the power generation of the combustion turbines or steam turbine. The boiler is proposed to operate 8760 hrs/yr but will be limited by an annual fuel throughput based on a capacity factor of 10%. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Low sulfur/carbon fuel and good combustion practices | 0.007 | LB/MMBTU |  | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | COMBUSTION TURBINE GENERATOR WITH DUCT-FIRED HEAT RECOVERY STEAM GENERATORS (3) | 15.21 | natural gas | 3227 | MMBTU/HR | 3227 MMBTU/HR CT with 500 MMBTU/HR Duct Burner, 3 on 1 configuration. | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201A and OTM 28 | (Particulate Matter (PM)) | PM | P | Low sulfur/carbon fuel and good combustion pratices | 0.0039 | LB/MMBTU | AVG OF 3 TEST RUNS | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Turbines without DB: 9.2 lbs/hr (0.0030 lb/MMBtu)
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | DIESEL-FIRED EMERGENCY GENERATOR 3000 kW (1) | 17.11 | DIESEL FUEL | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | Ultra Low Sulfur Diesel/Fuel (15 ppm max) | 0.4 | G/KW | PER HR | N/A |  | U | 0 | U | 1 | T/YR | 12 MO ROLLING TOTAL | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | DIESEL-FIRED WATER PUMP 376 bph (1) | 17.21 | DIESEL FUEL | 0 |  | FWP-1: 104.0 tons/year (12-month rolling total) | Particulate matter, total &lt; 10 Âµ (TPM10) | EPA/OAR Mthd 201 and 202 | (Particulate Matter (PM)) | PM | P | Ultra Low Sulfur Diesel/Fuel (15 ppm max) | 0.3 | G/HP-H | PER HR | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | PROPANE-FIRED EMERGENCY GENERATORS 150 kW (2) | 17.23 | PROPANE | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.19 | G/HP-H | PER HR | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | AUXILIARY COOLER | 99.19 |  | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Low total dissolved solids | 0.01 | % | DRIFT RATE | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | INLET CHILLERS (4) | 99.999 |  | 0 |  |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | Low total dissolved solids and drift eliminators | 1500 | MG/L |  | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0336 | CAMPBELL SOUP COMPANY | CAMPBELL SOUP COMPANY | HENRY | OH |  | USA | ANN CURNOW | 763-278-5932 | ANN.CURNOW@HDRIC.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0106678 | 2032 | 311422 | 110041176679 | 07/28/2010 &nbsp;ACT | 12/14/2010 &nbsp;ACT | 2011-03-31 | 2011-10-13 | B |  | Canned food maufacturing facility. | Replacing 5 natural gas boilers with 3 new ones. Facility is a Major PSD facility for SO2, NOx, PE, and CO. This permit is PSD for CO. Five old natural gas steam boilers will be decommissioned upon the installation of the 3 new ones. The boilers will burn natural gas and use #2 fuel oil as backup. The facility took a restriction on the #2 fuel oil used to avoid PSD on all but the CO. The boilers are used for steam production for process lines and cogeneration for building heat. | Boilers (3) | 12.31 | Natural Gas | 0 |  | The natural gas throughput is unknown; the limits are based on the potential of 8760 hours of operation. Boilers used for cogeneration of heat to facility. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.01 | LB/MMBTU | BASED ON MFG. GUARANTEE | OTHER CASE-BY-CASE | OPERATING PERMIT | U | 0 | U | 19.71 | T/YR | ROLLING 12 MO. FROM 3 BOILERS TOGETHER | 0 |  |  | 0 | 0 | N |  | One boiler was submitted before the other 2 and it is permitted for an emission rate of 0.015 LB/MMBtu, while the other two are permitted at 0.01 LB/MMBtu.
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Calcium Bin | 70.29 |  | 250 | ton/hr |  | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | A | Baghouse | 0.003 | GR/DSCF | 3-HOUR OR TEST METHOD AVERAGE |  |  | U | 0 | U | 0.04 | LB/HR | 3-HOUR OR TEST METHOD AVERAGE | 0 |  |  | 0 | 0 | N
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | Duct Burners (4) | 12.31 | Natural Gas | 140 | MMBTU/H | Each duct burner-turbine pair exhaust through a common stack | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 7.6 | LB/MMSCF | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Cost analysis not conducted since cost was not a factor in BACT determination.
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Three (3) Package Boilers | 12.31 | Natural Gas | 243 | MMBTU/H | Three (3) New Natural Gas-Fired 243 MMBtu/hr Package Boilers | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0074 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Startup Heater | 12.31 | Natural Gas | 101 | MMBTU/H | Natural Gas-Fired 101 MMBtu/hr Startup Heater. Installed in 1976. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Limited Use (200 hr/yr) | 0.0074 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | TUNNEL FURNACES SN-20 AND 21 | 12.31 | NATURAL GAS | 234 | MMBTU/H | 2 TUNNEL FURNCE SECTIONS 234 MMBTU/HR AND 192 MMBTU/HR MADE UP OF A SERIES OF INDIVIDUAL 3 MMBTU BURNERS. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 110 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA METHODS 5 & 202, OR METHODS 201A & 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 0.8 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Startup Heater | 12.31 | Natural gas | 110.12 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and 28 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0024 | LB/MMBTU | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.01 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Startup Heater | 12.31 | natural gas | 104 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0075 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | FOUR (4) NATURAL GAS-FIRED BOILERS | 12.31 | NATURAL GAS | 218 | MMBTU/HR, EACH | FUEL INPUT TO ALL FOUR BOILERS SHALL NOT EXCEED 2,802 MMCF/YEAR | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | PROPER DESIGN AND GOOD COMBUSTION | 7.6 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | NATURAL GAS AUXILIARY BOILERS (EU-012A, EU-012B, EU-012C) | 12.31 | NATURAL GAS | 218.6 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | PROPER DESIGN AND GOOD COMBUSTION PRACTICES AT ALL TIMES THE BOILERS ARE IN OPERATION. | 7.6 | LB/MMCF EACH | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 2: SHALL COMBUST NATURAL GAS LIMIT 3: EACH SHALL NOT EXCEED 1877.39 MMCF/ 12 CONSECUTIVE MONTH PERIOD
*IN-0287 | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING STATION | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING | KNOX | IN | 47528 | USA | PATRICK COUGHLIN | 317-838-2108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Mehul Sura 317-233-6868 msura@IDEM.IN.gov Section Chief - Tripurari P. Sinha Ph. D. 317-234-4907 | 083-38023-00003 | 4911 | 22 | Not Entered | 12/22/2016 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2018-07-25 | 2018-07-25 | C | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | stationary electric utility generating station |  | Auxiliary Boiler | 12.31 | natural gas | 213 | MMBtu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0075 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This BACT is for Startup and Shutdown emissions only
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Auxiliary boilers | 12.31 | natural gas | 171 | mm btu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | boiler A and B (010 and 011) | 12.31 | natural gas/fuel gas | 248 | mm btu/hr (each) |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices; fueled by natural gas or process fuel gas | 0.007 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | boiler B-201 | 12.31 | natural gas/fuel gas | 229 | mm btu |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices; fueled by natural gas or process fuel gas | 0.007 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUAUXBOILER (Auxiliary Boiler) | 12.31 | natural gas | 182 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 182 MMBTU/H fuel heat input. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 1.36 | LB/H | HOURLY, TEST PROTOCOL | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | At greater than $40,000 for the least expensive option, none of the control technologies are economically feasible. Control technologies evaluated were a scrubber and various types of fabric filters and ESPs.
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUAUXBOILER (Auxiliary boiler) | 12.31 | Natural gas | 182 | MMBTU/H | A natural gas fired auxiliary boiler, rated at 182 MMBTU/H to provide auxiliary steam when the plant is off-line, used to maintain warm drums on the HRSG and maintain the steam turbine generator seals. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0075 | LB/MMBTU |  | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The low concentration of PM / PM10 / PM2.5 in the auxiliary boiler exhaust makes the cost of add-on control very high. Also, of the add-on control options evaluated (pulse jet fabric filter, dry and wet ESP, and venturi scrubber), only the venturi scrubber and wet ESP are expected to be able to effectively reduce condensable PM emissions. The following costs are estimated for the add-on control technologies: â€¢ Fabric Filter Control: over $47,000 per ton controlled (assuming 99.9 percent control of filterable PM/PM10/PM2.5) â€¢ Electrostatic Precipitator (ESP): over $34,000 per ton controlled (assuming 99.4 percent control of filterable PM/PM10/PM2.5) â€¢ Wet ESP: over $29,000 per ton controlled (assuming 99.2 percent control of filterable and condensable PM/PM10/PM2.5) â€¢ Venturi Scrubber: over $20,000 per ton controlled (assuming 99.0 percent control of filterable and condensable PM/PM10/PM2.5)
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Boiler, Nat Gas Fired | 12.31 | NATURAL GAS | 261 | MMBTU/H | 261 MMBTU/H natrual gas-fired boiler, equipped with low-NOx burners, SCR, and CO catalytic oxidation | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - 5 or 201A and 202 | (Particulate Matter (PM)) | PM | N |  | 1.31 | LB/H | 3-HR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 261 MMBtU/H natural gas-fired boiler, equipped with natural gas-fired boiler, equipped with low-NOx burners, SCR, and CO catalytic oxidation
NM-0052 | ZIA II GAS PLANT | DCP MIDSTREAM L.P. | LEA | NM | 88255 | USA | JENNIFER HANNA | 4326205460 | JHANNA@DCPMIDSTREAM.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Joseph Kimbrell, 505-476-4300, joseph.kimbrell@state.nm.us | PSD-5217 | 1311 | 211111 | 110056438083 | 11/13/2013 &nbsp;ACT | 04/25/2014 &nbsp;ACT | 2015-11-19 | 2016-07-07 | A | https://www.env.nm.gov/aqb/ | Natural Gas Processing plant using cryogenic process and designed to operate at 230 MMscf/day of natural gas. | The permittee submitted an application on 5/13/2015 to revise the permit. Most BACT determinations will not change. | Industrial Sized Boilers/Furnaces &gt;100 mmBtu/hr | 12.31 | Natural gas | 114 | mmBtu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD | NSPS , SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0641 | PINECREST ENERGY CENTER | PINECREST ENERGY CENTER LLC | ANGELINA | TX |  | USA | KATHLEEN SMITH | 281-253-4385 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | PSDTX1298 | 4911 |  |  | 06/22/2012 &nbsp;ACT | 11/12/2013 &nbsp;ACT | 2013-11-21 | 2017-11-17 | A |  | Combinec Cycle Electric Generating Plant | 103839 | Auxiliary boiler | 12.31 | natural gas | 150 | MMBTU/H | limited to 876 hours per year of operation | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | pipeline quality natural gas and good combustion practices | 1.14 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Heating Medium Heaters | 12.31 | natural gas | 130 | MMBTU/H | There are (5) heaters each at 130 MMBtu/hr which operate when the turbine exhaust is not providing enough heat for the amine regenrating heating oil system | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.91 | LB/H | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Natural gas is the fuel
TX-0708 | LA PALOMA ENERGY CENTER | LA PALOMA ENERGY CENTER, LLC | CAMERON | TX |  | USA | GARY NEUS | (281) 682-8448 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 101542 PSDTX1288 | 4911 | 221112 | unknown | 03/15/2012 &nbsp;ACT | 02/07/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is a new electric power plant, fueled by pipeline quality natural gas. The design of the plant is standard combined cycle (CC) technology. |  | boiler | 12.31 | natural gas | 150 | MMBTU/H | annual usage limitation to 876 hours per year | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | natural gas as fuel, includes PM and PM10
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Auxiliary Boiler | 12.31 | Natural Gas | 100 | mmBtu/hr | Limited to 2,000 hours of operation per year. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of Natural Gas & Good Combustion Practices | 0.5 | LB/H |  | BACT-PSD | SIP | U | 0 | U | 0 |  |  | 0.005 | LB/MMBTU |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | AMMONIA CATALYST STARTUP HEATER | 12.39 | NATURAL GAS | 106.3 | MMBTU/H | ANNUAL NATURAL GAS USAGE LIMITED TO 20.84 MMCF. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS COMBUSTION ONLY, PROPER DESIGN AND GOOD COMBUSTION PRACTICES | 7.6 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, VACUUM DEGASSER | 13.29 | NATURAL GAS | 51.2 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACE, ANNEALING PICKLING LINE | 13.29 | NATURAL GAS | 66 | MMBTU/H | ANNEALING PICKLING LINE FURNACE SN-47; ANNEALING COATING LINE FURNACE , SN 51; | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | Sigma Thermal Auxiliary Heater (1) | 13.31 | Natural Gas | 12.5 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 7.6 | LB/MMSCF | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Cost analysis not conducted since cost was not a factor in BACT determination.
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Waste Heat Boilers | 13.31 | Natural Gas | 50 | MMBTU/H | Five (5) Natural Gas-Fired 50 MMBtu/hr Waste Heat Boilers. Installed in 1986. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0074 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, PICKLE LINE | 13.31 | NATURAL GAS | 67 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILERS SN-26 AND 27, GALVANIZING LINE | 13.31 | NATURAL GAS | 24.5 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER EU-002 | 13.31 | NATURAL GAS | 70 | MMBTU/HR |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.522 | LB/H | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 200 | H/YR |  | 0 |  |  | 0 | 0 | N | 2016 | SHALL COMBUST NATURAL GAS
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Regenerative Heaters | 13.31 | natural gas | 7.37 | mm btu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGFUELHTR (Two fuel pre-heaters identified as EUFUELHTR1 &amp; EUFUELHTR2) | 13.31 | Natural gas | 27 | MMBTU/H | Two natural gas fired dew point heaters for warming the natural gas fuel (EUFUELHTR1 & EUFUELHTR2 in flexible group FGFUELHTR). The total combined heat input during operation shall not exceed 27 MMBTU/H (each) as well. The CO2e limit is for both units combined; however the other limits are per unit. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.2 | LB/H | HOURLY; EACH FUEL HEATER | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | At greater than $40,000 for the least expensive option, none of the control technologies are economically feasible. Control technologies evaluated were a scrubber and various types of fabric filters and ESPs.
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Regeneration Heater, methanol to gasoline | 13.31 | NATURAL GAS | 13 | MMBTU/H | 13 MMBTU/H methanol-to-gasoline regeneration heater, equipped with low-NOx burner | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | good combustion practices (continuous oxygen trim or annual tune-ups) 13 MMBTU/H methanol-to-gasoline regeneration heater, equipped with low-NOx burner
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Reactor Heater, 5 | 13.31 | NATURAL GAS | 12 | MMBTU/H | Five 12 MMBTU/H reactor heaters, equipped with low-NOx burners | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | good combustion practices (continuous oxygen trim or annual tune-ups) Five 12 MMBTU/H reactor heaters, equipped with low-NOx burners
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Dryer Regenerator Heater - 005 | 13.39 | process fuel gas | 29 | mm btu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices; fueled by process fuel gas | 0.007 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | GE LM6000PF-25 Turbines (4) | 15.21 | Natural Gas | 59900 | hp ISO | Turbine-duct burner pairs exhaust through common stack | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 0.0066 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Cost analysis not conducted since cost was not a factor in BACT determination.
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA METHODS 5 & 202, OR METHODS 201A & 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 0.0048 | LB/MMBTU | 9-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0.0049 | LB/MMBTU | 9-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices, inlet air conditioning, and the use of pipeline quality natural gas. | 19.8 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit in the table above is for EACH CTGHRSG. The cost analysis was for the best scenario: 100 percent capture of PM2.5/PM10, which are higher emitting than PM. PM cost effectiveness would be worse than the numbers provided. The dollar value year used was 2014. Pulse Jet Fabric Filter Baghouse: minimum of $364,528 per ton Mechanical Shaker Fabric Filter Baghouse: minimum of $404,724 per ton Reverse-Air Fabric Filter Baghouse: minimum of $476,689 per ton Dry ESP (Wire-Plate Type): minimum of $478,806 per ton Dry ESP (Wire-Pipe Type): minimum of $303,809 per ton Wet ESP (Wire-Plate Type): minimum of $576,763 per ton Wet ESP (Wire-Pipe Type): minimum of $440,047 per ton Venturi Scrubber: minimum of $1,445,564 per ton
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCCT (Combined cycle CTG with unfired HRSG) | 15.21 | Natural gas | 1934.7 | MMBTU/H | A 1,934.7 MMBTU/H natural gas fired heavy frame industrial combustion turbine. The turbine operates in combined-cycle with an unfired heat recovery steam generator (HRSG). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices and the use of pipeline quality natural gas, combustion inlet air filter. | 0.0066 | LB/MMBTU |  | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Fabric filter control: over $260,000 per ton controlled (assuming 99.9 percent control of filterable PM/PM10/PM2.5). Electrostatic precipitator (ESP): OVER $188,000 per ton controlled (assuming 99.4 percent control of filterable PM/PM10/PM2.5). Wet ESP: over $165,000 per ton controlled (assuming 99.2 percent control of filterable and condensable PM/PM10/PM2.5). Venturi Scrubber: over $112,000 per ton controlled (assuming 99.0 percent control of filterable and condensable PM/PM10/PM2.5).
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | Large combustion turbine | 15.21 | Natural Gas | 0 |  | This process entry is for operations with the duct burner. Limits entered are for each turbine. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0039 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 11.8 | LB/HR |  | 0 |  |  | 0 | 0 | N
*TX-0641 | PINECREST ENERGY CENTER | PINECREST ENERGY CENTER LLC | ANGELINA | TX |  | USA | KATHLEEN SMITH | 281-253-4385 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | PSDTX1298 | 4911 |  |  | 06/22/2012 &nbsp;ACT | 11/12/2013 &nbsp;ACT | 2013-11-21 | 2017-11-17 | A |  | Combinec Cycle Electric Generating Plant | 103839 | combined cycle turbine | 15.21 | natural gas | 700 | MW | The generating equipment consists of two natural gas-fired combustion turbines (CTs), each exhausting to a fired heat recovery steam generator (HRSG) to produce steam to drive a shared steam turbine generator. The steam turbine is rated at 271 MW of electric output. Three models of combustion turbines are being considered for this site: the General Electric 7FA.05, the Siemens SGT6-5000F(4), and the Siemens SGT6-5000F(5). The final selection of the combustion turbine will not be made until after the permit is issued. Plant output will range between 637 and 735 MW, depending on the model turbine selected. Duct Burners are rated at 750 MMBtu/hr each. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | pipeline quality natural gas and good combustion practices | 26.2 | LB/H |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Turbine models ranged from 25.5-26.2 lb/hr
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Combustion Turbine | 15.21 | natural gas | 87 | MW | The exhaust heat from the turbine will be used to heat a heating medium which is used to regenerate rich amine from the acid gas removal system. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 15.22 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0708 | LA PALOMA ENERGY CENTER | LA PALOMA ENERGY CENTER, LLC | CAMERON | TX |  | USA | GARY NEUS | (281) 682-8448 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 101542 PSDTX1288 | 4911 | 221112 | unknown | 03/15/2012 &nbsp;ACT | 02/07/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is a new electric power plant, fueled by pipeline quality natural gas. The design of the plant is standard combined cycle (CC) technology. |  | (2) combined cycle turbines | 15.21 | natural gas | 650 | MW | The specific equipment includes two combustion turbines (CTs) connected to electric generators, producing between 183 and 232 MW of electricity, depending on ambient temperature and the selected CT. The two HRSGs use duct burners rated at 750 MMBtu/hr each to supplement the heat energy from the CTs. The steam from the two HRSGs is combined and routed to a single steam turbine driving a third electric generator with an electricity output capacity of 271 MW. Depending on the selected CT, total plant output at 59Â°F is between 637 MW and 735 MW. The applicant is considering three models of CT; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) Siemens SGT6-5000F(4); or (3) Siemens SGT6-5000F(5). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | natural gas as fuel, includes PM and PM10
TX-0712 | TRINIDAD GENERATING FACILITY | SOUTHERN POWER COMPANY | HENDERSON | TX |  | USA | KELLI MCCULLOUGH | (205) 257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tzvi Shalem 512-239-1310 tzvi.shalem@tceq.texas.gov | 111393 PSDTX1368 | 4911 | 221112 | 110007199735 | 06/27/2013 &nbsp;ACT | 11/20/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | Southern Power Company (SPC) is proposing to construct an electric generating facility near Trinidad, Henderson County, Texas. The Trinidad Generating Facility (TGF) will include a natural gas-fired combined cycle combustion turbine generator (CTG) equipped with heat recovery steam generator (HRSG) and duct burners (DB). |  | combined cycle turbine | 15.21 | natural gas | 497 | MW | The facility will consist of a Mitsubishi Heavy Industries (MHI) J model gas fired combustion turbine nominally rated at 497 megawatts (MW) equipped with a HRSG and DB with a maximum design capacity of 402 million British thermal units per hour (MMBtu/hr). The gross nominal output of the CTG with HRSG and DB is 530 MW. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | natural gas as fuel
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Combined Cycle Turbine/Duct Burner | 15.21 | Natural Gas | 2419.61 | mmBtu/Hr | This entry is for both of two identical units at the facility. Nominal 197 mW General Electric Frame 7FA.04 Turbine w/ Duct Burner - throughput denotes aggregate heat input of turbine and duct burner (HHV). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | Good Combustion Practices, Inlet Air Filtration, & use of Natural Gas | 8.9 | LB/H |  | BACT-PSD |  | U | 0 | U | 0.0037 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N |  | Assume all PM is PM2.5 or less. PM2.5 limit is applicable with and without duct firing.
*IN-0287 | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING STATION | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING | KNOX | IN | 47528 | USA | PATRICK COUGHLIN | 317-838-2108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Mehul Sura 317-233-6868 msura@IDEM.IN.gov Section Chief - Tripurari P. Sinha Ph. D. 317-234-4907 | 083-38023-00003 | 4911 | 22 | Not Entered | 12/22/2016 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2018-07-25 | 2018-07-25 | C | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | stationary electric utility generating station |  | combined cycle combustion turbines | 15.25 | natural gas and syn gas | 2129 | MMBtu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 14.3 | TONS/YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This BACT is for Startup and Shutdown emissions only
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Natural Gas Fired Combustion Turbines | 16.11 | Natural Gas | 37.6 | MMBTU/H | Five (5) Natural Gas-Fired Solar Combustion Turbines rated at 37.6 MMBtu/hr each. Installed in 1976. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0074 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | Caterpillar 3215C Black Start Generator (1) | 17.11 | ULSD | 1500 | KW-e |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 0.03 | G/HP-H | INSTANTANEOUS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Cost analysis not conducted since cost was not a factor in BACT determination.
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EMERGENCY GENERATORS | 17.11 | DIESEL | 1500 | KW |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD OPERATING PRACTICES, LIMITED HOURS OF OPERATION, COMPLIANCE WITH NSPS SUBPART IIII | 0.04 | G/KW-H |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.11 | DIESEL | 2683 | HP | UNIT IS 2000 KW. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA METHODS 5 & 202, OR 201A & 202 | (Particulate Matter (PM)) | PM | P | USE ULTRA LOW SULFUR FUEL | 0.2 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Emergency Generator | 17.11 | diesel fuel | 142 | GAL/H | rated @ 2,000 KW | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and 28 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.2 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.22 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Emergency Generator | 17.11 | distillate fuel oil | 3755 | HP |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 0.1 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY GENERATOR | 17.11 | NO. 2 FUEL OIL | 4690 | B-HP | ANNUAL HOURS OF OPERATION NOT TO EXCEED 200 HOURS. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | LB/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | EMERGENCY GENERATORS (EU014A AND EU-014B) | 17.11 | DISTILLATE OIL | 3600 | HP EACH |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-H EACH | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 500 | H/YR EACH |  | 0 |  |  | 0 | 0 | N | 2016
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Diesel Engines | 17.11 | Diesel | 0 |  | Water Pumps (2 units) = 355 hp Tank Deluge Pumps (2 units) = 800 hp Generator = 1340 hp | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices, Use ultra low sulfur diesel, and comply with 40 CFR 60 Subpart IIII | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUEMENGINE (Diesel fuel emergency engine) | 17.11 | Diesel Fuel | 22.68 | MMBTU/H | a 2,922 horsepower (HP) (2,179 kilowatts (kW)) diesel fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Restricted to 4 hours/day, except during emergency conditions and stack testing, and 500 hours/year on a 12-month rolling time period basis. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 1.58 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Diesel Fired Well Pump | 17.21 | Diesel | 2.7 | MMBTU/H | 2.7 MMBtu/hr Diesel Fired Well Pump. Installed in 1966. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Limited Operation of 168 hr/yr. | 0.31 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.21 | DIESEL | 182 | HP | UNIT IS 135 KW. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA METHODS 5 & 202, OR 201A & 202 | (Particulate Matter (PM)) | PM | P | USE ULTRA LOW SULFUR FUEL | 0.2 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and 28 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.2 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.03 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 0.1 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel Firewater pump engines (6 units) | 17.21 | diesel | 425 | hp |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel emergency generator engine - EGEN | 17.21 | diesel | 350 | hp |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.57 | LB/H | HOURLY | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | firewater pumps, diesel | 17.21 | diesel | 325 | HP, EACH | Eight 325 hp diesel firewater pumps | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | comply with NSPS IIII, 52 hr/yr non-emergency operation
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Gasoline Fired Fire Pump Engine | 17.22 | Gasoline | 2.1 | MMBTU/H | 2.1 MMBtu/hr Gasoline-Fired Fire Pump Engine. Installed in 1978. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Limited Operation of 168 hr/yr. | 0.1 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | SMALL HEATERS AND DRYERS SN-05 THROUGH 19 | 17.23 | NATURAL GAS | 0 |  | RH VESSEL PREHEATER STATION, VESSEL TOP PART DRYER, RH VESSEL NOZZLE DRYER RH DEGASSER BURNER/LANCE LADLE PREHEATERS LADLE DRYOUT STATION VERTICAL LADLE HOLDING STATION TUNDISH PREHEATERS #1 THROUGH #4 | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Three (3) Flares | 19.31 | Natural Gas | 1.25 | MMBTU/H | 1.25 MMBtu/hr Ammonia Tank Flare, 0.4 MMBtu/hr Emergency Flare, and 1.25 MMBtu/hr Small Flare | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Work Practice Requirements and Limited Use (limit venting to 168 hr/yr each during startup, shutdown, and maintenance events) | 0.0074 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Ammonia Flare | 19.31 | natural gas | 0.4 | MMBTU/H | There are four (4) natural gas pilots | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and 28 | (Particulate Matter (PM)) | PM | P | work practice/good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | There is no numeric emission limit in the permit.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | FRONT END PROCESS FLARE | 19.31 | NATURAL GAS PILOT | 0.25 | MMBTU/H | HEAT INPUT IS FOR NATURAL GAS PILOT ONLY. SSM EMISSIONS ARE CONTROLLED BY THE FLARE AND ARE LIMITED TO 336 HOURS OF VENTING PER YEAR. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS FOR PILOT, USE FLARE MINIMIZATION PRACTICES | 0.0075 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | BACK END AMMONIA FLARE | 19.31 | NATURAL GAS | 0.25 | MMBTU/H | HEAT INPUT IS FOR PILOT ONLY. SSM EMISSIONS ARE CONTROLLED BY THE FLARE AND ARE LIMITED TO 336 HR/YR. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.0075 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | AMMONIA STORAGE FLARE | 19.31 | NATURAL GAS | 0.13 | MMBTU/H | HEAT INPUT IS FOR PILOT ONLY. SSM EVENTS HAVE SEPARATE LIMITS. SSM VENTING IS LIMITED TO 168 HOURS PER YEAR. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.0075 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | SSM VENTING LIMITED TO 168 HR PER YEAR.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | UAN PLANT VENT FLARE | 19.31 |  | 0.19 | MMBTU/H | HEAT INPUT IS FOR NATUAL GAS PILOT. SSM EMISSIONS HAVE SEPARATE LIMITS. SSM VENTING LIMITED TO 336 HOURS PER YEAR. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.0075 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Flare No. 1 - 008 | 19.31 | natural gas | 85097 | MM BTU/yr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | complying with 40 CFR 60.18; good combustion practices (including establishment of flare minimization practices); steam assisted | 0.007 | LB/MM BTU |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Pyrolysis Gasoline Tank Flare - 009 | 19.31 | natural gas | 0.66 | mm btu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | complying with 40 CFR 60.18 and 63.11; good combustion practices (including establishment of flare minimization practices); steam assisted | 0.007 | LBS/MM BTU |  | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | vessel evacuation flare - 018 | 19.31 | natural gas | 3.04 | mm btu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices (including establishment of flare minimization practices) | 0.007 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FRONT END FLARE EU-017 | 19.39 | NATURAL GAS | 1.12 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 7.6 | LB/MMCF | 3 HR AVG | BACT-PSD |  | N | 0 |  | 336 | H/12 CONSEC. MONTH | VENTING | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS USED SHALL BE NATURAL GAS LIMIT 4: COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUTDOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ROOT CAUSE ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DUING ANY 2 CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMOCOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | BACK END FLARE (EU-018) | 19.39 | NATURAL GAS | 1.12 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0075 | LB/MMBTU | 3 HR AVG. | BACT-PSD |  | N | 0 |  | 336 | HR/12 CONSEC. MONTHS |  | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS USED SHALL BE NATURAL GAS LIMIT 4: COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUTDOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ROOT CAUSE ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DUING ANY 2 CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMOCOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE.
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | AUXILIARY HEATER | 19.6 | NATURAL GAS | 40 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - EPA METHODS 5 & 202, OR 201A & 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY PIPELINE NATURAL GAS | 0.3 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EMERGENCY GENERATOR SN-62 | 19.8 | DIESEL | 625 | HP |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD OPERATING PRACTICES, LIMITED HOURS OF OPERATION, COMPLIANCE WITH NSPS SUBPART IIII | 0.02 | GR/KW-H |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Thermal oxidizers (2 units) | 50.008 | natural gas | 21 | mm btu/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Two (2) Urea Granulation Units | 61.012 |  | 1200 | T/D | Two (2) Urea Granulation Units rated at 1200 tons per day (each). | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | Wet Scrubber | 0.2 | LB/TON OF UREA |  | BACT-PSD |  | U | 90 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Primary Reformer | 61.012 | natural gas | 1.13 | million cubic feet/h |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and Mthd 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0024 | LB/MMBTU | AVERAGE OF 3 TEST RUNS | BACT-PSD |  | U | 0 | U | 11.9 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Urea Granulator | 61.012 |  | 1500 | metric tons/day |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and 28 | (Particulate Matter (PM)) | PM | A | Wet Scrubber | 0.025 | KG/METRIC TON | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 15.1 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Ammonia Plant, Flares | 61.012 | natural gas | 2789 | tpd |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.15 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Reformer Furnace | 61.012 | natural gas | 955 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - Method 5I or 201A and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0024 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Ammonia Pressure Tanks | 61.012 |  | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | B | Flare; flare minimization | 0.25 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Urea Plant | 61.012 |  | 4880 | tpd | while the urea granulator in the urea plant is the principal emitter, there are other units that contribute. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | 2-stage scrubbing system with high efficiency venturi scrubber | 0.121 | LB/TON UREA | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Cooling Tower | 61.012 |  | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | B | drift eliminators; TDS of water not to exceed 2000 mg/l | 0.0005 | % LOSS FROM CIRC. |  | BACT-PSD |  | U | 0 | U | 0.6 | LB/H | 24-HOUR AVERAGE | 2.47 | TPY |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | PRIMARY REFORMER | 61.012 | NATURAL GAS | 1006.4 | MMBTU/H | NOX CEMS | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 7.6 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | TWO (2) AMMONIUM NITRATE UNITS | 61.012 |  | 798 | TON AN PER DAY, EACH | UAN PRODUCTION IS LIMITED TO 1,314,000 TONS PER YEAR. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | WET SCRUBBER WITH HIGH EFFICIENCY DEMISTER | 0.0128 | LB/TON UAN | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | UREA GRANULATION UNIT (EU-008) | 61.012 |  | 1320 | METRIC TON/DAY |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | WET SCRUBBER | 0.163 | LB/TON | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 368040 | TON/12 CONSEC. MONTH |  | 0 |  |  | 0 | 0 | N | 2016
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | TRUCK AND RAIL LOADING OPERATION (EU-021A) | 61.012 |  | 4800 | METRIC TON/DAY |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | BAGHOUSE | 0.15 | LB/H | 3 HR AVG. | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N | 2016
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Cooling Tower | 61.999 |  | 0 |  | There are 2 cooling towers. One has 6 cells with a total flowrate of 74,040 gal/min and the other has 9 cells with a total flowrate of 111,060 gal/min | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and 28 | (Particulate Matter (PM)) | PM | A | drift eliminator | 0.0005 | % |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | There is no numerical emission limit. The drift eliminator is required to have a control efficiency of 0.0005%.
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Granulated Urea Transfer | 61.999 |  | 1500 | metric tons/day | There are six (6) different emission points. The transfer points are for the warehouse, train loading, and truck loading. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and 28 | (Particulate Matter (PM)) | PM | A | bin vent filter | 0.0013 | GR/DSCF | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The ton/yr limit varies for each of the 6 emission points depending on the flowrate.
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Modular Ethylene Cracking Furnaces - 001 | 64.003 | natural gas/fuel gas | 1028 | MM BTU/hr |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices; fueled by natural gas or process fuel gas | 0.007 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Ethylene Cracking Furnace - 015 | 64.003 | natural gas/fuel gas | 168 | mm btu |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices, fueled by natural gas and/or fuel gas | 0.007 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EAFS SN-01 AND SN-02 | 81.21 | NATURAL GAS | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | FABRIC FILTER | 0.0024 | GR/SDCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | ANNEALING COATING CLEANING SECTION, SN-52 | 81.23 |  | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | MIST ELIMINATOR | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | LMFS SN-01 AND SN-02 | 81.29 | NATURAL GAS | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | FABRIC FILTER | 0.0024 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | RH DEGASSER | 81.29 | NATURAL GAS | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | SCALE EXHAUST, PICKLE LINE | 81.29 |  | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | FABRIC FILTER | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | DUST EXHAUST SN-23A, TENSION LEVELER | 81.29 |  | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | FABRIC FILTER | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | COLD MILL REVERSING COLD MILL AND SKIN PASS MILL SN-25, 38, 44, 45, AND 46 | 81.29 |  | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | MIST ELIMINATOR | 0.0066 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | GALVANIZING LINE CAUSTIC CLEANING AND POST TREATMENT SN-34 THROUGH 37 | 81.29 |  | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | MIST ELIMINATOR | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-39, ANNEALING | 81.29 | NATURAL GAS | 98.25 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | DECARBURIZING LINE CLEANING SECTIONS SN-41 AND 43 | 81.29 |  | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | MIST ELIMINATOR | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | ANNEALING PICKLING LINE SCALE DUST AND SHOTBLAST | 81.29 |  | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | FABRIC FILTER | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | ANNEALING COATING LINE FURNACE SECTION | 81.29 | NATURAL GAS | 50 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACE, SN-53, ANNEALING COATING LINE DRYING | 81.29 | NATURAL GAS | 38 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | DRYERS, MGO COATING LINE | 81.29 | NATURAL GAS | 38 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | MGO COATING CLEANING SECTIONS SN-55 AND 57 | 81.29 |  | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | MIST ELIMINATOR | 0.003 | GR/DSCF |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-58 AND 60, FINAL ANNEALING AND COATING LINE | 81.29 | NATURAL GAS | 32 | MMBTU/H |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.2 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | TWO (2) COOLING TOWERS | 99.009 |  | 179720 | GPM, COMBINED | ONE UNIT IS EIGHT CELL, THE OTHER IS SIX CELL. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | HIGH EFFICIENCY DRIFT ELIMINATORS | 0.0005 | % DRIFT | CONTINUOUS | BACT-PSD |  | Y | 0 |  | 2000 | MG/L | CONTINUOUS | 0 |  |  | 4592 | 0 | N | 2012 | TOWERS USE ONSITE WELL WATER. IT IS HAS HIGHER THAN NORMAL TDS. COST EFFECTIVENESS BASED ON REDUCTION OF TDS FROM 2,000 MG/L TO 1,500 MG/L. ADVERSE ENVIRONMENTAL IMPACTS WERE CONSIDERED.
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | cooling towers - 007 | 99.009 |  | 86500 | gpm |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | drift eliminators | 0.0005 | % | DRIFT RATE | BACT-PSD |  | U | 0 | U | 1400 | PPM | TDS | 0 |  |  | 0 | 0 | N
MI-0427 | FILER CITY STATION | FILER CITY STATION LIMITED PARTNERSHIP | MANISTEE | MI | 49634 | USA | ALLEN ADKINS | 313-336-7189 | ALLEN.ADKINS@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Michelle Rogers, for any technical questions regarding this permit application. She may be reached at 517-284-6799 or at rogersm13@michigan.gov. Thank you. | 66-17 | 4931 | 221112 | Not Found | 07/17/2017 &nbsp;ACT | 11/17/2017 &nbsp;ACT | 2018-01-26 | 2018-03-08 | B |  | New natural gas combined heat and power plant proposed at existing cogenerating power plant permitted to burn wood, coal and tire derived fuel. |  | EUCOOLTWR (Cooling Tower--Wet Mechanical Drift) | 99.009 |  | 0 |  | A four-cell evaporative cooling tower in series with mechanical chilling to cool turbine inlet air. Particulate emissions will be controlled with high efficiency drift eliminators. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | Mist/Drift Eliminators | 0.0006 | % | VENDOR-CERTIF. MAX. DRIFT RATE | BACT-PSD | SIP | N | 0 | N | 7700 | PPM | MAX TDS IN COOLING WATER | 0 |  |  | 0 | 0 | N |  | Emission Limit 1 above is 0.0006%, vendor-certified maximum drift rate. Emission Limit 2 above is 7700 ppmw, maximum Total Dissolved Solids (TDS) in cooling water. The estimated efficiency is to reduce drift loss to 0.0006 There are no BACT emission limits in the permit, but there is a requirement for the permittee to equip and maintain EUCOOLTWR with mist/drift eliminators with a vendor-certified maximum drift rate of 0.0006 percent or less, and there is also a limit of 7700 ppmw maximum Total Dissolved Solids (TDS) in cooling water.
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Cooling tower, Induced draft | 99.009 |  | 1420 | GAL/MIN |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | high efficiency drift eliminators | 0.001 | % | DRIFT RATE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0708 | LA PALOMA ENERGY CENTER | LA PALOMA ENERGY CENTER, LLC | CAMERON | TX |  | USA | GARY NEUS | (281) 682-8448 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 101542 PSDTX1288 | 4911 | 221112 | unknown | 03/15/2012 &nbsp;ACT | 02/07/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is a new electric power plant, fueled by pipeline quality natural gas. The design of the plant is standard combined cycle (CC) technology. |  | cooling tower | 99.009 |  | 0 |  | LPEC proposes to limit the solids in the circulating water of the cooling tower 7,000 milligrams/liter to reduce emissions of PM/PM10/PM2.5. LPEC also proposes to use high-efficiency mist eliminators with a drift rate of 0.001% to reduce PM/PM10/PM2.5 from the cooling tower. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | mist eliminators | 0.001 | % | DRIFT | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | includes PM and PM10
TX-0712 | TRINIDAD GENERATING FACILITY | SOUTHERN POWER COMPANY | HENDERSON | TX |  | USA | KELLI MCCULLOUGH | (205) 257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tzvi Shalem 512-239-1310 tzvi.shalem@tceq.texas.gov | 111393 PSDTX1368 | 4911 | 221112 | 110007199735 | 06/27/2013 &nbsp;ACT | 11/20/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | Southern Power Company (SPC) is proposing to construct an electric generating facility near Trinidad, Henderson County, Texas. The Trinidad Generating Facility (TGF) will include a natural gas-fired combined cycle combustion turbine generator (CTG) equipped with heat recovery steam generator (HRSG) and duct burners (DB). |  | cooling tower | 99.009 |  | 0 |  | drift eliminators that limit drift to 0.001% | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | mist eliminators | 0.001 | % | DRIFT | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Cooling Tower | 99.009 |  | 159000 | gpm |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.01 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | 2 Cell Cross-Flow Cooling Tower | 99.11 |  | 15000 | gallons per minute | 2 Cell Cross-Flow Cooling Tower | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | High Efficiency Drift Eliminators | 0.002 | % DRIFT |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Urea Ship Loading | 99.11 |  | 1000 | tons urea/hour | The Urea Ship Loading Operations are conveyor systems used to load products from the Urea Plant into ships. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | B | Use of UF-85 (Hardening Agent), Product Coolers on Granulation Urea Process Lines, Loading into Partial Enclosure, and use of a Telescoping Chute. | 0.0004 | LB/TON OF UREA |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Urea Handling Units | 99.11 |  | 1000 | tons urea/hour |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | A | Fully Enclosed Conveyors and Fabric Filters | 0.005 | GRAINS/DSCF | 3 STACK TEST AVERAGE | BACT-PSD |  | U | 99 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Haul Roads | 99.14 |  | 0 |  | There are two (2) paved haul roads. The length of one is 0.97 miles and the other is 1.07 miles long. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | EPA/OAR OTM 27 and 28 | (Particulate Matter (PM)) | PM | P | paved road, water flushing, and sweeping | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | There are no numeric emission limits in the permits.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | PAVED ROADWAYS AND PARKING LOTS WITH PUBLIC ACCESS | 99.14 |  | 17160 | VEHICLE MILES TRAVELED |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | PAVE ALL PLANT HAUL ROADS, DAILY SWEEPING AND WET SUPPRESSION, PROMPT CLEANUP OF ANY SPILLED MATERIAL | 90 | % CONTROL | CONTINUOUS | BACT-PSD |  |  | 90 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | PAVED ROADS AND PARKING LOTS | 99.19 |  | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | PAVING ALL PLANT HAUL ROADS, WET SUPPRESSION, PROMPT CLEANUP OF ANY SPILLED MATERIALS. | 0 |  |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N | 2016
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COOLING TOWER | 99.999 |  | 130000 | GAL/MIN CIRCULATION RATE |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - MODIFIED METHOD 306 OR COOLING TOWER INSTITUTE TEST METHOD | (Particulate Matter (PM)) | PM | N |  | 1.6 | LB/H |  | BACT-PSD |  | U | 0 | U | 0.0005 | % DRIFT |  | 0 |  |  | 0 | 0 | N |  | Third emission limit incorrectly entered into the Standard Limit field. RBLC SysOp moved the information into this Notes field. Here is the information: 5000.00 PPM TDS
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | 245 MMBtu natural gas fired Auxiliary boiler | 12.31 | Natural Gas | 1052 | MMscf/yr | Total fuel usage of the auxiliary boiler shall not exceed 1052 MMsch/yr on a 12-month rolling basis | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 0.0075 | LB/MMBTU | 3 HR AVG | LAER | NSPS | U | 0 | U | 4 | TPY |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | DIESEL-FIRED EMERGENCY GENERATOR 3000 kW (1) | 17.11 | DIESEL FUEL | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - 201A | (Particulate Matter (PM)) | PM | P | Ultra Low Sulfur Diesel/Fuel (15 ppm max) | 0.4 | G/KR | PER HR | N/A |  | U | 0 | U | 0.7 | T/YR | 12 MO ROLLING TOTAL | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | DIESEL-FIRED WATER PUMP 376 bph (1) | 17.21 | DIESEL FUEL | 0 |  | FWP-1: 104.0 tons/year (12-month rolling total) | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Other - 201A | (Particulate Matter (PM)) | PM | P | Ultra Low Sulfur Diesel/Fuel (15 ppm max) | 0.3 | G/HP-H | HR | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | AUXILIARY COOLER | 99.19 |  | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Low total dissolved solids | 0.01 | % | DRIFT RATE | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Total dissolved content of no more than 300 mg/l
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | INLET CHILLERS (4) | 99.999 |  | 0 |  |  | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Low total dissolved solids and drift eliminators | 1500 | MG/L |  | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | Duct Burners (4) | 12.31 | Natural Gas | 140 | MMBTU/H | Each duct burner-turbine pair exhaust through a common stack | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 7.6 | LB/MMSCF | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Cost analysis not conducted since cost was not a factor in BACT determination.
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Three (3) Package Boilers | 12.31 | Natural Gas | 243 | MMBTU/H | Three (3) New Natural Gas-Fired 243 MMBtu/hr Package Boilers | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0074 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Startup Heater | 12.31 | Natural Gas | 101 | MMBTU/H | Natural Gas-Fired 101 MMBtu/hr Startup Heater. Installed in 1976. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Limited Use (200 hr/yr) | 0.0074 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 110 | MMBTU/H |  | Particulate matter, total (TPM) | Other - EPA METHODS 5 & 202, OR METHODS 201A & 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 0.8 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Startup Heater | 12.31 | Natural gas | 110.12 | MMBTU/H |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0024 | LB/MMBTU | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.01 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | NATURAL GAS AUXILIARY BOILERS (EU-012A, EU-012B, EU-012C) | 12.31 | NATURAL GAS | 218.6 | MMBTU/H |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | PROPER DESIGN AND GOOD COMBUSTION PRACTICES AT ALL TIMES THE BOILERS ARE IN OPERATION. | 1.9 | LB/MMCF EACH | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 2: SHALL COMBUST NATURAL GAS LIMIT 3: EACH SHALL NOT EXCEED 1,877.39 MMCF PER 12 CONSECUTIVE MONTH PERIOD
*IN-0287 | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING STATION | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING | KNOX | IN | 47528 | USA | PATRICK COUGHLIN | 317-838-2108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Mehul Sura 317-233-6868 msura@IDEM.IN.gov Section Chief - Tripurari P. Sinha Ph. D. 317-234-4907 | 083-38023-00003 | 4911 | 22 | Not Entered | 12/22/2016 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2018-07-25 | 2018-07-25 | C | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | stationary electric utility generating station |  | Auxiliary Boiler | 12.31 | natural gas | 213 | MMBtu/hr |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0075 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This BACT is for Startup and Shutdown emissions only
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Boiler, Nat Gas Fired | 12.31 | NATURAL GAS | 261 | MMBTU/H | 261 MMBTU/H natrual gas-fired boiler, equipped with low-NOx burners, SCR, and CO catalytic oxidation | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | N |  | 1.31 | LB/H | 3-HR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 261 MMBtU/H natural gas-fired boiler, equipped with natural gas-fired boiler, equipped with low-NOx burners, SCR, and CO catalytic oxidation
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | 245 MMBtu natural gas fired Auxiliary boiler | 12.31 | Natural Gas | 1052 | MMscf/yr | Total fuel usage of the auxiliary boiler shall not exceed 1052 MMsch/yr on a 12-month rolling basis | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices | 4 | TPY |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0.0075 | LB/MMBTU | 3 HR AVG | 0 | 0 | N
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | MR. RANDY THOMPSON | (615) 532-6825 | randall.thompson@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000370535 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Two Natural Gas-Fired Auxiliary Boilers | 12.31 | Natural Gas | 450 | MMBtu/hr | Two 450 MMBtu/hr natural gas-fired auxiliary boilers will provide steam generation during threshold transitional periods and during malfunction events when the CT and HRSG are not able to operate. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion design and practices | 0.008 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | Sigma Thermal Auxiliary Heater (1) | 13.31 | Natural Gas | 12.5 | MMBTU/H |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 7.6 | LB/MMSCF | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Cost analysis not conducted since cost was not a factor in BACT determination.
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Waste Heat Boilers | 13.31 | Natural Gas | 50 | MMBTU/H | Five (5) Natural Gas-Fired 50 MMBtu/hr Waste Heat Boilers. Installed in 1986. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0074 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Regeneration Heater, methanol to gasoline | 13.31 | NATURAL GAS | 13 | MMBTU/H | 13 MMBTU/H methanol-to-gasoline regeneration heater, equipped with low-NOx burner | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | good combustion practices (continuous oxygen trim or annual tune-ups) 13 MMBTU/H methanol-to-gasoline regeneration heater, equipped with low-NOx burner
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Reactor Heater, 5 | 13.31 | NATURAL GAS | 12 | MMBTU/H | Five 12 MMBTU/H reactor heaters, equipped with low-NOx burners | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | good combustion practices (continuous oxygen trim or annual tune-ups) Five 12 MMBTU/H reactor heaters, equipped with low-NOx burners
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | GE LM6000PF-25 Turbines (4) | 15.21 | Natural Gas | 59900 | hp ISO | Turbine-duct burner pairs exhaust through common stack | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 0.0066 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Cost analysis not conducted since cost was not a factor in BACT determination.
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COMBUSTION TURBINES (NORMAL OPERATION) | 15.21 | NATURAL GAS | 154 | MW | TWO NATURAL GAS-FIRED COMBUSTION TURBINE-GENERATORS (CTGS) RATED AT 154 MEGAWATT (MW, GROSS) EACH, TWO HEAT RECOVERY STEAM GENERATORS (HRSG), ONE STEAM TURBINE GENERATOR (STG) RATED AT 267 MW, AND 251 ACRES OF PARABOLIC SOLAR-THERMAL COLLECTORS WITH ASSOCIATED HEAT-TRANSFER EQUIPMENT | Particulate matter, total (TPM) | Other - EPA METHODS 5 & 202, OR METHODS 201A & 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY NATURAL GAS | 0.0048 | LB/MMBTU | 9-HR AVG (NO DUCT BURNING) | BACT-PSD |  | U | 0 | U | 0.0049 | LB/MMBTU | 9-HR AVG (W/ DUCT BURNING) | 0 |  |  | 0 | 0 | N
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | Large combustion turbine | 15.21 | Natural Gas | 0 |  | This process entry is for operations with the duct burner. Limits entered are for each turbine. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion practices with the use of low ash/sulfer fuels | 0.0039 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 11.8 | LB/HR |  | 0 |  |  | 0 | 0 | N
TN-0162 | JOHNSONVILLE COGENERATION | TENNESSEE VALLEY AUTHORITY | HUMPHREYS | TN | 37134-0259 | USA | CLAY CHERRY | (931) 535-8203 | CCCHERRY@TVA.GOV | 4 | TN001 | TENN.DEPT. OF ENVIRONMENT & CONSERVATION, DIV OF AIR POLLUTION CONTROL | MR. RANDY THOMPSON | (615) 532-6825 | randall.thompson@tn.gov | Travis Blake (615) 532-0617 travis.blake@tn.gov | 970816F | 4911 | 221112 | 110000370535 | 09/22/2015 &nbsp;ACT | 04/19/2016 &nbsp;ACT | 2016-05-19 | 2018-05-11 | D |  | Existing gas-fired combustion turbine with new heat recovery steam generator (HRSG) with duct burner and two new gas-fired auxiliary boilers. | Facility-wide emissions increases do not include decreases due to shutdown of coal-fired units. | Natural Gas-Fired Combustion Turbine with HRSG | 15.21 | Natural Gas | 1339 | MMBtu/hr | Turbine throughput is 1019.7 MMBtu/hr when burning natural gas and 1083.7 MMBtu/hr when burning No. 2 oil. Duct burner throughput is 319.3 MMBtu/hr. Duct burner firing will occur during natural gas combustion only. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good combustion design and practices | 0.005 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0.015 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N |  | Limit #1 is for gas combustion, limit #2 is for No. 2 oil combustion
*IN-0287 | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING STATION | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING | KNOX | IN | 47528 | USA | PATRICK COUGHLIN | 317-838-2108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Mehul Sura 317-233-6868 msura@IDEM.IN.gov Section Chief - Tripurari P. Sinha Ph. D. 317-234-4907 | 083-38023-00003 | 4911 | 22 | Not Entered | 12/22/2016 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2018-07-25 | 2018-07-25 | C | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | stationary electric utility generating station |  | combined cycle combustion turbines | 15.25 | natural gas and syn gas | 2129 | MMBtu/hr |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | good combustion practices | 14.3 | TONS/YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This BACT is for Startup and Shutdown emissions only
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Natural Gas Fired Combustion Turbines | 16.11 | Natural Gas | 37.6 | MMBTU/H | Five (5) Natural Gas-Fired Solar Combustion Turbines rated at 37.6 MMBtu/hr each. Installed in 1976. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0074 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0071 | INTERNATIONAL STATION POWER PLANT | CHUGACH ELECTRIC ASSOCIATION, INC. | MUNCIPALITY OF ANCHORAGE | AK | 99518-1074 | USA | GREG ARTHUR | (907) 762-4492 | GREG_ARTHUR@CHUGACHELECTRIC.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV | Dr. Fathima Zeena" Siddeek 410 Willoughby Way Ste. 303 Juneau | AK 99811" | AQ0164CPT01 | 4911 | 221112 | Not Applicable | 03/31/2010 &nbsp;ACT | 12/20/2010 &nbsp;ACT | 2010-12-20 | 2012-03-27 | B | http://dec.alaska.gov/air/ap/docs/AQ0164CPT01finper.pdf | Combined Cycle Power Power Plant | Caterpillar 3215C Black Start Generator (1) | 17.11 | ULSD | 1500 | KW-e |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Good Combustion Practices | 0.03 | G/HP-H | INSTANTANEOUS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Cost analysis not conducted since cost was not a factor in BACT determination.
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.11 | DIESEL | 2683 | HP | UNIT IS 2000 KW. | Particulate matter, total (TPM) | Other - EPA METHODS 5 & 202, OR 201A & 202 | (Particulate Matter (PM)) | PM | P | USE ULTRA LOW SULFUR FUEL | 0.2 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Emergency Generator | 17.11 | diesel fuel | 142 | GAL/H | rated @ 2,000 KW | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.2 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.22 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | EMERGENCY GENERATORS (EU014A AND EU-014B) | 17.11 | DISTILLATE OIL | 3600 | HP EACH |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES | 0.15 | G/HP-H EACH | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 500 | H/YR EACH |  | 0 |  |  | 0 | 0 | N | 2016
MI-0389 | KARN WEADOCK GENERATING COMPLEX | CONSUMERS ENERGY | BAY | MI | 48732-9601 | USA | JAMES M. WALKER | 5177880428 | JMWALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | FOR TECHNICAL QUESTIONS ABOUT THIS PERMIT, PLEASE CONTACT THE PERMIT ENGINEER - DAVID K. RIDDLE RIDDLED@MICHIGAN.GOV (517-373-7081) | 341-07 | 4911 | 221112 | 26-01700033 | 10/15/2007 &nbsp;ACT | 12/29/2009 &nbsp;ACT | 2010-03-08 | 2010-12-16 | U |  | ELECTRICITY GENERATING FACILITY, EXISTING CAPACITY GREATER THAN 2,000 MW. | AFTER CONSTRUCTION CONSUMERS WILL RETIRE 5 TO 7 COAL-FIRED BOILERS (638 - 958 MW) STATEWIDE. FINAL CONDITIONS WILL BE AT WWW.DEQ.STATE.MI.US/APS/FINALCONDITIONS.SHTML. MATERIAL HANDLING - CONTACT PERMIT ENGINEER FOR TECHNICAL INFORMATION (DAVID RIDDLE, 517-373-7081). INCLUDES 9 EMISSION UNITS. COAL, LIMESTONE, SORBENT AND ASH HANDLING PROCESSES. VARIOUS BACT LIMITS FOR OPACITY, PM AND PM10. BACT FOR THE MATERIAL HANDLING EQUIPMENT CONSISTED OF A COMBINATION OF PASSIVE CONTROL EQUIPMENT SUCH AS WET/CHEMICAL SUPPRESSION SYSTEMS AND ENCLOSED CONVEYORS; AND ACTIVE CONTROL SUCH AS FABRIC FILTERS. ACTIVE CONTROL IS LIMITED TO 0.004 GR/DSCF. | FIRE PUMP | 17.11 | ULTRA LOW SULFUR DIESEL | 525 | HP | OPERATIONAL LIMITS: 1 HOUR/DAY AND 500 HRS/YEAR FOR PM2.5 NAAQS. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | ENGINE DESIGN AND OPERATION. 15 PPM SULFUR FUEL. | 0.15 | G/HP-H | TEST METHOD | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0389 | KARN WEADOCK GENERATING COMPLEX | CONSUMERS ENERGY | BAY | MI | 48732-9601 | USA | JAMES M. WALKER | 5177880428 | JMWALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | FOR TECHNICAL QUESTIONS ABOUT THIS PERMIT, PLEASE CONTACT THE PERMIT ENGINEER - DAVID K. RIDDLE RIDDLED@MICHIGAN.GOV (517-373-7081) | 341-07 | 4911 | 221112 | 26-01700033 | 10/15/2007 &nbsp;ACT | 12/29/2009 &nbsp;ACT | 2010-03-08 | 2010-12-16 | U |  | ELECTRICITY GENERATING FACILITY, EXISTING CAPACITY GREATER THAN 2,000 MW. | AFTER CONSTRUCTION CONSUMERS WILL RETIRE 5 TO 7 COAL-FIRED BOILERS (638 - 958 MW) STATEWIDE. FINAL CONDITIONS WILL BE AT WWW.DEQ.STATE.MI.US/APS/FINALCONDITIONS.SHTML. MATERIAL HANDLING - CONTACT PERMIT ENGINEER FOR TECHNICAL INFORMATION (DAVID RIDDLE, 517-373-7081). INCLUDES 9 EMISSION UNITS. COAL, LIMESTONE, SORBENT AND ASH HANDLING PROCESSES. VARIOUS BACT LIMITS FOR OPACITY, PM AND PM10. BACT FOR THE MATERIAL HANDLING EQUIPMENT CONSISTED OF A COMBINATION OF PASSIVE CONTROL EQUIPMENT SUCH AS WET/CHEMICAL SUPPRESSION SYSTEMS AND ENCLOSED CONVEYORS; AND ACTIVE CONTROL SUCH AS FABRIC FILTERS. ACTIVE CONTROL IS LIMITED TO 0.004 GR/DSCF. | EMERGENCY GENERATOR | 17.11 | ULTRA LOW SULFUR DIESEL | 2000 | KW | 2980 HP. OPERATIONAL LIMITS: 1 HR/DAY, 500 HRS/YR FOR PM2.5 NAAQS. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | ENGINE DESIGN AND OPERATION. 15 PPM SULFUR FUEL. | 0.2 | G/KW-H | TEST METHOD | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Diesel Fired Well Pump | 17.21 | Diesel | 2.7 | MMBTU/H | 2.7 MMBtu/hr Diesel Fired Well Pump. Installed in 1966. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Limited Operation of 168 hr/yr. | 0.31 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | EMERGENCY IC ENGINE | 17.21 | DIESEL | 182 | HP | UNIT IS 135 KW. | Particulate matter, total (TPM) | Other - EPA METHODS 5 & 202, OR 201A & 202 | (Particulate Matter (PM)) | PM | P | USE ULTRA LOW SULFUR FUEL | 0.2 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0.15 | G/HP-H |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.2 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.03 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
MI-0389 | KARN WEADOCK GENERATING COMPLEX | CONSUMERS ENERGY | BAY | MI | 48732-9601 | USA | JAMES M. WALKER | 5177880428 | JMWALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | FOR TECHNICAL QUESTIONS ABOUT THIS PERMIT, PLEASE CONTACT THE PERMIT ENGINEER - DAVID K. RIDDLE RIDDLED@MICHIGAN.GOV (517-373-7081) | 341-07 | 4911 | 221112 | 26-01700033 | 10/15/2007 &nbsp;ACT | 12/29/2009 &nbsp;ACT | 2010-03-08 | 2010-12-16 | U |  | ELECTRICITY GENERATING FACILITY, EXISTING CAPACITY GREATER THAN 2,000 MW. | AFTER CONSTRUCTION CONSUMERS WILL RETIRE 5 TO 7 COAL-FIRED BOILERS (638 - 958 MW) STATEWIDE. FINAL CONDITIONS WILL BE AT WWW.DEQ.STATE.MI.US/APS/FINALCONDITIONS.SHTML. MATERIAL HANDLING - CONTACT PERMIT ENGINEER FOR TECHNICAL INFORMATION (DAVID RIDDLE, 517-373-7081). INCLUDES 9 EMISSION UNITS. COAL, LIMESTONE, SORBENT AND ASH HANDLING PROCESSES. VARIOUS BACT LIMITS FOR OPACITY, PM AND PM10. BACT FOR THE MATERIAL HANDLING EQUIPMENT CONSISTED OF A COMBINATION OF PASSIVE CONTROL EQUIPMENT SUCH AS WET/CHEMICAL SUPPRESSION SYSTEMS AND ENCLOSED CONVEYORS; AND ACTIVE CONTROL SUCH AS FABRIC FILTERS. ACTIVE CONTROL IS LIMITED TO 0.004 GR/DSCF. | FIRE BOOSTER PUMP | 17.21 | ULTRA LOW SULFUR DIESEL | 40 | KW | OPERATIONAL LIMITS 1 HR/DAY AND 500 HRS/YR FOR PM2.5 NAAQS. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | ENGINE DESIGN AND OPERATION. 15 PPM SULFUR FUEL. | 0.4 | G/KW-H | TEST METHOD | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | firewater pumps, diesel | 17.21 | diesel | 325 | HP, EACH | Eight 325 hp diesel firewater pumps | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | comply with NSPS IIII, 52 hr/yr non-emergency operation
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Gasoline Fired Fire Pump Engine | 17.22 | Gasoline | 2.1 | MMBTU/H | 2.1 MMBtu/hr Gasoline-Fired Fire Pump Engine. Installed in 1978. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Limited Operation of 168 hr/yr. | 0.1 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0389 | KARN WEADOCK GENERATING COMPLEX | CONSUMERS ENERGY | BAY | MI | 48732-9601 | USA | JAMES M. WALKER | 5177880428 | JMWALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | FOR TECHNICAL QUESTIONS ABOUT THIS PERMIT, PLEASE CONTACT THE PERMIT ENGINEER - DAVID K. RIDDLE RIDDLED@MICHIGAN.GOV (517-373-7081) | 341-07 | 4911 | 221112 | 26-01700033 | 10/15/2007 &nbsp;ACT | 12/29/2009 &nbsp;ACT | 2010-03-08 | 2010-12-16 | U |  | ELECTRICITY GENERATING FACILITY, EXISTING CAPACITY GREATER THAN 2,000 MW. | AFTER CONSTRUCTION CONSUMERS WILL RETIRE 5 TO 7 COAL-FIRED BOILERS (638 - 958 MW) STATEWIDE. FINAL CONDITIONS WILL BE AT WWW.DEQ.STATE.MI.US/APS/FINALCONDITIONS.SHTML. MATERIAL HANDLING - CONTACT PERMIT ENGINEER FOR TECHNICAL INFORMATION (DAVID RIDDLE, 517-373-7081). INCLUDES 9 EMISSION UNITS. COAL, LIMESTONE, SORBENT AND ASH HANDLING PROCESSES. VARIOUS BACT LIMITS FOR OPACITY, PM AND PM10. BACT FOR THE MATERIAL HANDLING EQUIPMENT CONSISTED OF A COMBINATION OF PASSIVE CONTROL EQUIPMENT SUCH AS WET/CHEMICAL SUPPRESSION SYSTEMS AND ENCLOSED CONVEYORS; AND ACTIVE CONTROL SUCH AS FABRIC FILTERS. ACTIVE CONTROL IS LIMITED TO 0.004 GR/DSCF. | FLUE GAS DESULFURIZATION QUENCH PUMP | 17.23 | ULTRA LOW SULFUR DIESEL | 305 | KW | 455 HP. OPERATIONAL LIMITS: 1 HR/DAY, 500 HRS/YR FOR PM2.5 NAAQS. | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | ENGINE DESIGN AND OPERATION. 15 PPM SULFUR FUEL. | 0.2 | G/KW-H | TEST METHOD | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Three (3) Flares | 19.31 | Natural Gas | 1.25 | MMBTU/H | 1.25 MMBtu/hr Ammonia Tank Flare, 0.4 MMBtu/hr Emergency Flare, and 1.25 MMBtu/hr Small Flare | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Work Practice Requirements and Limited Use (limit venting to 168 hr/yr each during startup, shutdown, and maintenance events) | 0.0074 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Ammonia Flare | 19.31 | natural gas | 0.4 | MMBTU/H | There are four (4) natural gas pilots | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | work practice/good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | There is no numeric emission limit in the permit.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | AMMONIA STORAGE FLARE (EU-016) | 19.39 | NATURAL GAS | 1.1 | MMBTU/H |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0019 | LB/MMBTU | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 168 | H/12 CONSEC. MONTH | COMPLIANCE DETERMINED AT END OF MONTHS | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS SHALL BE NATURAL GAS LIMIT 4: SHALL COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUT DOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) SHALL TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO TDAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANE OF REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MINS DURING ANY 2 CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMACOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FRONT END FLARE EU-017 | 19.39 | NATURAL GAS | 1.12 | MMBTU/H |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 1.9 | LB/MMCF | 3 HR AVG. | BACT-PSD |  | N | 0 |  | 336 | H/12 CONSEC. MONTH | VENTING | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS USED SHALL BE NATURAL GAS LIMIT 4: COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUTDOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ROOT CAUSE ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DUING ANY 2 CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMOCOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | BACK END FLARE (EU-018) | 19.39 | NATURAL GAS | 1.12 | MMBTU/H |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.0019 | LB/MMBTU | 3 HR AVG | BACT-PSD |  | N | 0 |  | 336 | HR/12 CONSEC. MONTH |  | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS USED SHALL BE NATURAL GAS LIMIT 4: COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUTDOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ROOT CAUSE ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DUING ANY 2 CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMOCOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE.
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | AUXILIARY HEATER | 19.6 | NATURAL GAS | 40 | MMBTU/H |  | Particulate matter, total (TPM) | Other - EPA METHODS 5 & 202, OR 201A & 202 | (Particulate Matter (PM)) | PM | P | USE PUC QUALITY PIPELINE NATURAL GAS | 0.3 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Steam Methane Reformer | 50.002 | NATURAL GAS | 10 | MMSCFH | Steam Methane Reformer, equipped with low NOx burners, SCR, and CO oxidation catalyst | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | N |  | 1.88 | LB/H | 3-HR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Steam Methane Reformer, equipped with low NOx burners, SCR, and CO oxidation catalyst
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Two (2) Urea Granulation Units | 61.012 |  | 1200 | T/D | Two (2) Urea Granulation Units rated at 1200 tons per day (each). | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | A | Wet Scrubber | 0.2 | LB/TON OF UREA |  | BACT-PSD |  | U | 90 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Primary Reformer | 61.012 | natural gas | 1.13 | million cubic feet/h |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | good combustion practices | 0.0024 | LB/MMBTU | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 11.9 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Urea Granulator | 61.012 |  | 1500 | metric tons/day |  | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | A | Wet Scrubber | 0.1 | KG/METRIC TON | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 60.4 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | UREA GRANULATION UNIT (EU-008) | 61.012 |  | 1320 | METRIC TON/DAY |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | A | WET SCRUBBER | 0.163 | LB/TON | 3HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 368040 | TON/12 CONSEC. MONTH |  | 0 |  |  | 0 | 0 | N | 2016
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | TRUCK AND RAIL LOADING OPERATION (EU-021A) | 61.012 |  | 4800 | METRIC TON/DAY |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | A | BAGHOUSE | 0.15 | LB/H | 3 HR AVG. | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N | 2016
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Cooling Tower | 61.999 |  | 0 |  | There are 2 cooling towers. One has 6 cells with a total flowrate of 74,040 gal/min and the other has 9 cells with a total flowrate of 111,060 gal/min | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | A | drift eliminator | 0.0005 | % |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | There is no numerical emission limit. The drift eliminator is required to have a control efficiency of 0.0005%.
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Granulated Urea Transfer | 61.999 |  | 1500 | metric tons/day | There are six (6) different emission points. The transfer points are for the warehouse, train loading, and truck loading. | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | A | bin vent filter | 0.005 | GR/DSCF | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The ton/yr limit varies for each of the 6 emission points depending on the flowrate.
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Cooling tower, Induced draft | 99.009 |  | 1420 | GAL/MIN |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | high efficiency drift eliminators | 0.001 | % | DRIFT RATE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Cooling Tower | 99.009 |  | 360000 | gal/hr |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | B | drift loss design specification and TDS concentration limit | 0.0005 | % | DRIFT LOSS | BACT-PSD |  | U | 0 | U | 3000 | PPM | ONCE PER MONTH | 0 |  |  | 0 | 0 | N
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Cooling Tower | 99.009 |  | 159000 | gpm |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | Drift Eliminator | 0.72 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Haul Roads | 99.14 |  | 0 |  | There are two (2) paved haul roads. The length of one is 0.97 miles and the other is 1.07 miles long. | Particulate matter, total (TPM) | EPA/OAR Mthd 5 and 202 | (Particulate Matter (PM)) | PM | P | paved road, water flushing, and sweeping | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | There is no numeric emission limit in the permits.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | PAVED ROADS AND PARKING LOTS | 99.19 |  | 0 |  |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | PAVING ALL PLANT HAUL ROADS, WET SUPPRESSION, PROMPT CLEANUP OF ANY SPILLED MATERIALS. | 0 |  |  | BACT-PSD |  | N | 90 |  | 0 |  |  | 0 |  |  | 0 | 0 | N | 2016
CA-1212 | PALMDALE HYBRID POWER PROJECT | CITY OF PALMDALE | LOS ANGELES | CA | 93535 | USA | STEVE WILLIAMS |  |  | 9 | OT010 | EPA REGION IX | MR. GERARDO RIOS | (415)972-3974 | rios.gerardo@epa.gov |  | SE 09-01 | 4911 | 221112 |  | 08/19/2011 &nbsp;ACT | 10/18/2011 &nbsp;ACT | 2012-11-11 | 2014-01-27 | A | http://www.epa.gov/region9/air/permit/r9-permits-issued.html | 570 MW NATURAL GAS FIRED COMBINED CYCLE POWER PLANT WITH AN INTEGRATED 50 MW SOLAR THERMAL PLANT | NOTE: FINAL PSD PERMIT ISSUED ON 11/18/2011. PERMIT APPEALED TO THE ENVIRONMENTAL APPEALS BOARD, AND EAB DENIED REVIEW OF THIS APPEAL ON 9/17/2012. PETITIONER FILED A PETITION FOR REVIEW WITH THE 9TH CIRCUIT FEDERAL COURT. THIS COURT CASE WAS DISMISSED ON 10/28/2013. | COOLING TOWER | 99.999 |  | 130000 | GAL/MIN CIRCULATION RATE |  | Particulate matter, total (TPM) | Other - MODIFIED METHOD 306 OR COOLING TOWER INSTITUTE TEST METHOD | (Particulate Matter (PM)) | PM | N |  | 1.6 | LB/H |  | BACT-PSD |  | U | 0 | U | 0.0005 | % DRIFT |  | 0 |  |  | 0 | 0 | N |  | Third emission limit incorrectly entered into the Standard Limit field. RBLC SysOp moved the information into this Notes field. Here is the information: 5000.00 PPM TDS
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | EIGHTEEN CELL COOLING TOWER (EU-010) | 99.999 |  | 0 |  |  | Particulate matter, total (TPM) | Unspecified | (Particulate Matter (PM)) | PM | P | HIGH EFFICIENCY DRIFT ELIMINATORS | 2000 | MG/L | AVG ON A MONTHLY BASIS | BACT-PSD |  | N | 0 |  | 0.0005 | % | DRIFT | 0 |  |  | 0 | 0 | N | 2016
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT START-UP HEATER | 12.31 | NATURAL GAS | 38 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | GOOD COMBUSTION PRACTICE | 0.03 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.007 | T/YR | ROLLING 12 MONTH AVERAGE | 0.0007 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | START-UP BOILER | 12.31 | NATURAL GAS | 240 | MMBTU/H |  | Sulfur Dioxide (SO2) | EPA/OAR Mthd 6C | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | GOOD AND EFFICIENT OPERATING PRACTICES | 0.18 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.0007 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 |  |  | 0 | 0 | N |  | PERIODIC STACK TESTING TO VERIFY COMPLIANCE
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | TUNNEL FURNACES SN-20 AND 21 | 12.31 | NATURAL GAS | 234 | MMBTU/H | 2 TUNNEL FURNCE SECTIONS 234 MMBTU/HR AND 192 MMBTU/HR MADE UP OF A SERIES OF INDIVIDUAL 3 MMBTU BURNERS. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.88 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0238 | ALLIANCE REFINERY | CONOCOPHILLIPS COMPANY | PLAQUEMINES | LA | 70037 | USA | CHRIS CHANDLER | 5046567711 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CORBET MATHIS - PHONE: 225-219-3181 | PSD-LA-75(M3) | 2911 | 324110 | 2207500003 | 01/22/2008 &nbsp;ACT | 07/10/2009 &nbsp;ACT | 2009-09-11 | 2012-05-18 | C |  | A PETROLEUM REFINERY IN BELLE CHASSE, LA. | PSD-LA-75 (OCTOBER 22, 1978): TO EXPAND THE FCCU CAPACITY FROM 78,000 TO 89,000 BPD. PSD-LA-75(M3): INCLUDING STARTUP SHUTDOWN EMISSIONS, RECONCILE SO2 AND CO EMISSIONS FROM HEATER AND BOILERS | FCCU FEED HEATER | 12.31 | REFINERY GAS | 181.7 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | COMPLY WITH 40 CFR 60 SUBPART J | 4.79 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUAUXBOILER (Auxiliary Boiler) | 12.31 | natural gas | 182 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 182 MMBTU/H fuel heat input. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and the use of pipeline quality natural gas. | 0.6 | LB/MMSCF | BASED ON FUEL RECEIPT RECORDS | BACT-PSD | NSPS , SIP | N | 0 | N | 2000 | GR/MMSCF | BASED UPON FUEL RECEIPT RECORDS | 0 |  |  | 0 | 0 | N |  | The emission limit 2 above is 2,000 grains of sulfur per MMscf. The natural gas material limit of 2,000 grains of sulfur per MMscf is what the emission factor is based upon.
OH-0310 | AMERICAN MUNICIPAL POWER GENERATING STATION | AMERICAN MUNICIPAL POWER | MEIGS | OH | 45771 | USA | RANDY MEYER | 6143376222 | RMEYER@AMP-OHIO.ORG | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104461 | 4911 | 221112 | 110000384325 | 05/15/2006 &nbsp;ACT | 10/08/2009 &nbsp;ACT | 2008-04-15 | 2009-11-06 | A |  | TWO 5191 MMBTU/HOUR PULVERIZED COAL-FIRED BOILERS; ONE 150 MMBTU/HOUR NATURAL GAS AUXILIARY BOILER, ONE FLY ASH AND GYPSUM LANDFILL, COAL STORAGE, CRUSHERS, FERTILIZER PLANT, LIMESTONE AND FLY ASH HANDLING EQUIPMENT, AND COOLING CELLS. ADMINISTRATIVE MODIFICATION 10/09 TO ADD CASE-BY-CASE MACT FOR BOILERS. 1ST ISSUED 2/7/08 AS PTI#06-08138; STILL INITIAL INSTALLATION | FUGITIVE EMISSIONS FROM STORAGE PILES (COAL,LIMESTONE, UREA), CONVEYING, HANDLING, ROADWAYS, BARGE OR TRUCK UNLOADING WERE NOT ENTERED INTO THE DATABASE DUE TO THE INSIGNIFICANT EMISSIONS (MOST < 1 TON FUGITIVE PM) AND LACK OF PROCESS CODES TO ENTER THEM. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 150 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.09 | LB/H |  | BACT-PSD | SIP | U | 0 | U | 0.04 | T/YR | PER ROLLING 12 MONTHS | 0.6 | LB/MMCF |  | 0 | 0 | N
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Heating Medium Heaters | 12.31 | natural gas | 130 | MMBTU/H | There are (5) heaters each at 130 MMBtu/hr which operate when the turbine exhaust is not providing enough heat for the amine regenrating heating oil system | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.01 | LB/H | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | low sulfur natural gas is the fuel
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, VACUUM DEGASSER | 13.29 | NATURAL GAS | 51.2 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.88 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACE, ANNEALING PICKLING LINE | 13.29 | NATURAL GAS | 66 | MMBTU/H | ANNEALING PICKLING LINE FURNACE SN-47; ANNEALING COATING LINE FURNACE , SN 51; | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.88 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, PICKLE LINE | 13.31 | NATURAL GAS | 67 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.88 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILERS SN-26 AND 27, GALVANIZING LINE | 13.31 | NATURAL GAS | 24.5 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.88 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.88 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGFUELHTR (Two fuel pre-heaters identified as EUFUELHTR1 &amp; EUFUELHTR2) | 13.31 | Natural gas | 27 | MMBTU/H | Two natural gas fired dew point heaters for warming the natural gas fuel (EUFUELHTR1 & EUFUELHTR2 in flexible group FGFUELHTR). The total combined heat input during operation shall not exceed 27 MMBTU/H (each) as well. The CO2e limit is for both units combined; however the other limits are per unit. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and the use of pipeline quality natural gas. | 2000 | GR/MMSCF | BASED UPON FUEL RECEIPT RECORDS. | BACT-PSD | SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NOTE: The limit is 2,000 grains of sulfur per MMscf. The natural gas material limit of 2000 grains of sulfur per MMscf is what the emission factor is based upon.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good Combustion Practices and the use of pipeline quality natural gas. | 11.7 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD | NSPS , SIP | N | 0 | N | 0.06 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME | 0 |  |  | 0 | 0 | N |  | The emission limits above are for EACH CTGHRSG. There is also a NSPS natural gas material limit of 20 grains of sulfur per 100 scf.
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Combustion Turbine | 15.21 | natural gas | 87 | MW | The exhaust heat from the turbine will be used to heat a heating medium which is used to regenerate rich amine from the acid gas removal system. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 3.68 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | low sulfur natural-gas fired
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EMERGENCY GENERATORS | 17.11 | DIESEL | 1500 | KW |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | GOOD O | 20 | % |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUEMENGINE (Diesel fuel emergency engine) | 17.11 | Diesel Fuel | 22.68 | MMBTU/H | a 2,922 horsepower (HP) (2,179 kilowatts (kW)) diesel fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Restricted to 4 hours/day, except during emergency conditions and stack testing, and 500 hours/year on a 12-month rolling time period basis. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and meeting NSPS Subpart IIII requirements. | 15 | PPM | FUEL SUPPLIER CERTIFICATION RECORDS | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NOTE: The &lsquo;&lsquo;Avg. Time/Conditions&lsquo;&lsquo; for the emission limit of 15 ppm identified above is fuel supplier certification records or fuel sample test data, for each delivery of diesel fuel oil. The diesel material limit is 15 ppm of sulfur (0.0015 percent) by weight.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Good combustion practices and meeting NSPS Subpart IIII requirements. | 15 | PPM | FUEL SUP. CERT. RECORDS OR SAMPLE TEST | BACT-PSD | NSPS , SIP | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The Avg. Time/Conditions for the emission limit above is fuel supplier certification records or fuel sample test data, for each delivery of diesel fuel oil. The diesel material limit is 15 ppm of sulfur (0.0015 percent) by weight.
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | SMALL HEATERS AND DRYERS SN-05 THROUGH 19 | 17.23 | NATURAL GAS | 0 |  | RH VESSEL PREHEATER STATION, VESSEL TOP PART DRYER, RH VESSEL NOZZLE DRYER RH DEGASSER BURNER/LANCE LADLE PREHEATERS LADLE DRYOUT STATION VERTICAL LADLE HOLDING STATION TUNDISH PREHEATERS #1 THROUGH #4 | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.88 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT AMMONIA VENT FLARE | 19.31 | NATURAL GAS | 0.26 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | GOOD COMBUSTION PRACTICE | 0.0008 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.0034 | T/YR | ROLLING 12 MONTH AVERAGE | 0.0007 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT PROCESS SSM FLARE | 19.31 | NATURAL GAS | 0.05 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | GOOD COMBUSTION PRACTICE | 0.0007 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.0031 | T/YR | ROLLING 12 MONTH AVERAGE | 0.0007 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA STORAGE FLARE | 19.31 | NATURAL GAS | 0.05 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | GOOD AND EFFICIENT OPERATING PRACTICES | 0.0001 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.0006 | T/YR | ROLLING 12 MONTH AVERAGE | 0.0006 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 | 0 | N
NM-0052 | ZIA II GAS PLANT | DCP MIDSTREAM L.P. | LEA | NM | 88255 | USA | JENNIFER HANNA | 4326205460 | JHANNA@DCPMIDSTREAM.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Joseph Kimbrell, 505-476-4300, joseph.kimbrell@state.nm.us | PSD-5217 | 1311 | 211111 | 110056438083 | 11/13/2013 &nbsp;ACT | 04/25/2014 &nbsp;ACT | 2015-11-19 | 2016-07-07 | A | https://www.env.nm.gov/aqb/ | Natural Gas Processing plant using cryogenic process and designed to operate at 230 MMscf/day of natural gas. | The permittee submitted an application on 5/13/2015 to revise the permit. Most BACT determinations will not change. | Units FL1 &amp; FL2: Refinery Flares (Inlet Gas Flare &amp; Acid Gas Flare) | 19.33 | natural gas, acid gas | 2.3 | mmBtu/hr | Only for routine or predictable Startup, Shutdown, or Maintenance of units controlled by Flares (Blowdown/Venting, Amine Unit-Acid Gas Injection well maintenance) | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | NOx, CO, PM10, PM2.5, SO2 controlled through Good Combustion Practices (GCP), pipeline quality natural gas for pilot; limits on flaring events. VOC & CO2e controlled through GCP, limits on flaring and meet 40 CFR 60.18. | 13023.6 | PPH |  | BACT-PSD | NSPS , SIP , OPERATING PERMIT | N | 98 | U | 5427.4 | PPH |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EMERGENCY GENERATOR SN-62 | 19.8 | DIESEL | 625 | HP |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | GOOD OPERATING PRACTICES, LIMITED HOURS OF OPERATION, COMPLIANCE WITH NSPS SUBPART IIII | 0.0015 | % SULFUR FUEL |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0238 | ALLIANCE REFINERY | CONOCOPHILLIPS COMPANY | PLAQUEMINES | LA | 70037 | USA | CHRIS CHANDLER | 5046567711 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CORBET MATHIS - PHONE: 225-219-3181 | PSD-LA-75(M3) | 2911 | 324110 | 2207500003 | 01/22/2008 &nbsp;ACT | 07/10/2009 &nbsp;ACT | 2009-09-11 | 2012-05-18 | C |  | A PETROLEUM REFINERY IN BELLE CHASSE, LA. | PSD-LA-75 (OCTOBER 22, 1978): TO EXPAND THE FCCU CAPACITY FROM 78,000 TO 89,000 BPD. PSD-LA-75(M3): INCLUDING STARTUP SHUTDOWN EMISSIONS, RECONCILE SO2 AND CO EMISSIONS FROM HEATER AND BOILERS | FCCU REGEN VENT - SU/SD OPERATIONS | 50.003 |  | 89000 | BBL/D |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | COMPLY WITH 40 CFR 60 SUBPART J | 1286 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT PRIMARY REFORMER | 61.012 | NATURAL GAS | 1400 | T/D AMMONIA | 824 MMBTU/HR | Sulfur Dioxide (SO2) | EPA/OAR Mthd 6C | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | GOOD AND EFFICIENT COMBUSTION PRACTICES | 0.61 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.44 | T/YR | ROLLING 12 MONTH AVERAGE | 0.0007 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 | 0 | N |  | PERIODIC STACK TESTING TO VERIFY COMPLIANCE
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EAFS SN-01 AND SN-02 | 81.21 | NATURAL GAS | 0 |  |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | SCRAP MANAGEMENT PLAN | 0.18 | LB/TON |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | LMFS SN-01 AND SN-02 | 81.29 | NATURAL GAS | 0 |  |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | SCRAP MANAGEMENT PLAN | 0.2 | LB/TON OF STEEL |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | RH DEGASSER | 81.29 | NATURAL GAS | 0 |  |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.88 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-39, ANNEALING | 81.29 | NATURAL GAS | 98.25 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.88 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | ANNEALING COATING LINE FURNACE SECTION | 81.29 | NATURAL GAS | 50 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.88 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACE, SN-53, ANNEALING COATING LINE DRYING | 81.29 | NATURAL GAS | 38 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.88 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | DRYERS, MGO COATING LINE | 81.29 | NATURAL GAS | 38 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.88 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-58 AND 60, FINAL ANNEALING AND COATING LINE | 81.29 | NATURAL GAS | 32 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.88 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0354 | KRATON POLYMERS U.S. LLC | KRATON POLYMERS U.S. LLC | WASHINGTON | OH | 45714-0235 | USA | DALE LOUDERMILK | 740-423-2299 | DALE.LOUDERMILK@KRATON.CC | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0108853 | 2822 | 325212 | 110030900997 | 08/29/2012 &nbsp;ACT | 01/15/2013 &nbsp;ACT | 2013-09-27 | 2016-05-04 | B |  | Thermoplastic elastomer manufacturing facility | Two new 249 MMBtu/hour natural gas, distillate oil, and belpre naphtha-fired boilers installed to replace 2 existing coal, distillate oil, and belpre naphtha-fired boilers. | Two 249 MMBtu/H boilers | 12.31 | Natural Gas | 249 | MMBtu/H | Two boilers, burning natural gas or distillate oil w/ less than 0.05% sulfur; and co-fired with maximum of 54.8 MMBtu/H Belpre naphtha. Fitted with low-NOx burners with flue gas recirculation, as needed. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Burning low sulfur fuels with less than 0.05 % sulfur. | 11.24 | T/YR |  | N/A | SIP | U | 0 | U | 0 |  |  | 1.6 | LB/MMBTU | BURNING DISTILLATE OIL | 0 | 0 | N |  | Netted out for SO2 by replacing old coal/oil-fired boilers.
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | AUXILIARY BOILER (1) AND FUEL GAS HEATERS (6) | 12.31 | NATURAL GAS | 185 | MMBTU/HR | The auxiliary boiler will provide steam to the steam turbine at startup and at cold starts to warm up the ST rotor. The steam from the auxiliary boiler will not be used to augment the power generation of the combustion turbines or steam turbine. The boiler is proposed to operate 8760 hrs/yr but will be limited by an annual fuel throughput based on a capacity factor of 10%. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Low sulfur fuel | 0.0011 | LB/MMBTU |  | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | COMBUSTION TURBINE GENERATOR WITH DUCT-FIRED HEAT RECOVERY STEAM GENERATORS (3) | 15.21 | natural gas | 3227 | MMBTU/HR | 3227 MMBTU/HR CT with 500 MMBTU/HR Duct Burner, 3 on 1 configuration. | Sulfur Dioxide (SO2) | EPA/OAR Mthd 6 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Low Sulfur fuel | 0.0011 | LB/MMBTU | DURING NORMAL OPERATION INCLUDING SU/SD | N/A |  | U | 0 | U | 18.7 | T/YR | PER TURBINE | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | DIESEL-FIRED EMERGENCY GENERATOR 3000 kW (1) | 17.11 | DIESEL FUEL | 0 |  |  | Sulfur Dioxide (SO2) | Other - NA | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Ultra Low Sulfur Diesel/Fuel (15 ppm max) | 0.0015 | LB/MMBTU |  | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | DIESEL-FIRED WATER PUMP 376 bph (1) | 17.21 | DIESEL FUEL | 0 |  | FWP-1: 104.0 tons/year (12-month rolling total) | Sulfur Dioxide (SO2) | Other - NA | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Ultra Low Sulfur Diesel/Fuel (15 ppm max) | 0.0015 | LB/MMBTU |  | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MN-0076 | BLANDIN PAPER/RAPIDS ENERGY CENTER | BLANDIN PAPER COMPANY/MINNESOTA POWER | ITASCA | MN | 55744 | USA | NATHAN WAECH | 2183276269 |  | 5 | MN001 | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | MR. RICHARD CORDES | (651)757-2291 | RICHARD.CORDES@STATE.MN.US |  | 06100001-011 | 2621 | 322110 | 110000426290 | 08/16/2007 &nbsp;ACT | 09/18/2008 &nbsp;ACT | 2008-12-01 | 2009-02-10 | B |  | BLANDIN PAPER PRODUCES PAPER FOR ADVERTISING SUPPLEMENTS, CATALOGS, AND MAGAZINES. |  | BOILER | 12.31 | NATURAL GAS | 280 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | NATURAL GAS ONLY | 0 |  | SEE NOTE | Other Case-by-Case | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NO EMISSION LIMITS AVAILABLE
OH-0336 | CAMPBELL SOUP COMPANY | CAMPBELL SOUP COMPANY | HENRY | OH |  | USA | ANN CURNOW | 763-278-5932 | ANN.CURNOW@HDRIC.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0106678 | 2032 | 311422 | 110041176679 | 07/28/2010 &nbsp;ACT | 12/14/2010 &nbsp;ACT | 2011-03-31 | 2011-10-13 | B |  | Canned food maufacturing facility. | Replacing 5 natural gas boilers with 3 new ones. Facility is a Major PSD facility for SO2, NOx, PE, and CO. This permit is PSD for CO. Five old natural gas steam boilers will be decommissioned upon the installation of the 3 new ones. The boilers will burn natural gas and use #2 fuel oil as backup. The facility took a restriction on the #2 fuel oil used to avoid PSD on all but the CO. The boilers are used for steam production for process lines and cogeneration for building heat. | Boilers (3) | 12.31 | Natural Gas | 0 |  | The natural gas throughput is unknown; the limits are based on the potential of 8760 hours of operation. Boilers used for cogeneration of heat to facility. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.0006 | LB/MMBTU | AP-42 FACTOR | OTHER CASE-BY-CASE | OPERATING PERMIT | U | 0 | U | 0.96 | T/YR | ROLLING 12 MO. FROM 3 BOILERS TOGETHER | 0 |  |  | 0 | 0 | N
NM-0052 | ZIA II GAS PLANT | DCP MIDSTREAM L.P. | LEA | NM | 88255 | USA | JENNIFER HANNA | 4326205460 | JHANNA@DCPMIDSTREAM.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Joseph Kimbrell, 505-476-4300, joseph.kimbrell@state.nm.us | PSD-5217 | 1311 | 211111 | 110056438083 | 11/13/2013 &nbsp;ACT | 04/25/2014 &nbsp;ACT | 2015-11-19 | 2016-07-07 | A | https://www.env.nm.gov/aqb/ | Natural Gas Processing plant using cryogenic process and designed to operate at 230 MMscf/day of natural gas. | The permittee submitted an application on 5/13/2015 to revise the permit. Most BACT determinations will not change. | Industrial Sized Boilers/Furnaces &gt;100 mmBtu/hr | 12.31 | Natural gas | 114 | mmBtu/hr |  | Sulfur Oxides (SOx) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 7446 | N |  | 0 |  |  | BACT-PSD | NSPS , SIP , OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | BOILERS - UNITS CC026, CC027 AND CC028 AT CITY CENTER | 12.31 | NATURAL GAS | 44 | MMBTU/H | THE THREE UNITS ARE IDENTICAL CATERPILLAR BOILERS, EACH RATED AT 44 MMBTU/HR. EACH UNIT IS SUBJECT TO THE ANNUAL LIMIT OF OPERATING TIME TO 5,800 HOURS. THE EMISSION LIMITS ARE BASED ON THE ATC PERMIT FOR MODIFICATION #13 DATED NOVEMBER 30, 2009. | Sulfur Oxides (SOx) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 7446 | P | LIMITING THE FUEL TO NATURAL GAS ONLY | 0.0007 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | Y | 0.03 | LB/H |  | 0.0007 | LB/MMBTU |  | 0 | 0 | N |  | EMISSION LIMIT 2 APPLIES TO EACH UNIT.
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT FL01 | 13.31 | NATURAL GAS | 14.34 | MMBTU/H | UNIT FL01 IS A JOHNSTON BOILER AT FLAMINGO LAS VEGAS. THIS UNIT MAY OPERATE 8,760 HOURS PER YEAR. | Sulfur Oxides (SOx) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 7446 | P | FUEL IS LIMITED TO NATURAL GAS. | 0.0006 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 0.0091 | LB/H |  | 0.0006 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | SMALL INTERNAL COMBUSTION ENGINE (&lt;600 HP) - UNIT FL12 | 13.31 | DIESEL OIL | 536 | HP | UNIT FL12 IS A DETROIT DIESEL GENERATOR AT FLAMINGO LAS VEGAS. LIKE ALL THE OTHER DIESEL GENERATORS, THE UNIT IS SUBJECT TO THE LIMIT OF MONTHLY AND ANNUAL OPERATING TIMES FOR 2 HOURS PER MONTH AND 36 HOURS PER YEAR RESPECTIVELY. EMISSION FACTORS LISTED IN AP-42 ARE USED TO CALCULATE THE EMISSION LIMITS FOR EACH AND EVERY DIESEL GENERATOR IN THIS MAJOR STATIONARY SOURCE, AND ARE NOT REPEATED FURTHER FOR REPORTING THE BACT DETERMINATIONS. | Sulfur Oxides (SOx) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 7446 | P | FUEL IS LIMITED TO NATURAL GAS. | 0.0021 | LB/HP-H |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 1.1 | LB/H |  | 0.0021 | LB/HP-H |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT BA01 | 13.31 | NATURAL GAS | 16.8 | MMBTU/H | UNIT BA01 IS A KEWANEE BOILER AT BALLY'S LAS VEGAS. UNIT BA01 IS IDENTICAL TO UNIT BA02. THE TWO BOILERS ARE SUBJECT TO THE ANNUAL LIMIT OF COMBINED TOTAL OPERATING TIME FOR 10,900 HOURS PER YEAR. | Sulfur Oxides (SOx) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 7446 | P | FUEL IS LIMITED TO NATURAL GAS. | 0.0042 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 0.01 | LB/H |  | 0.0042 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT BA03 | 13.31 | NATURAL GAS | 31.38 | MMBTU/H | UNIT BA03 IS A KIWANEE BOLER AT BALLY'S LAS VEGAS. THE ANNUAL OPERATING TIME IS LIMITED TO 2,920 HOURS PER YEAR. | Sulfur Oxides (SOx) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 7446 | P | FUEL IS LIMITED TO NATURAL GAS. | 0.0006 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 0.02 | LB/H |  | 0.0006 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP01 | 13.31 | NATURAL GAS | 35.4 | MMBTU/H | UNIT CP01 IS A HURST BOILER AT CAESAR'S PALACE. UNIT CP01 IS IDENTICAL TO UNIT CP02. UNITS CP01 THROUGH CP05 (FIVE BOILERS) ARE SUBJECT TO THE ANNUAL LIMIT OF TOTAL OPERATING TIME FOR 33,520 HOURS PER YEAR. | Sulfur Oxides (SOx) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 7446 | P | FUEL IS LIMITED TO NATURAL GAS. | 0.0006 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 0.02 | LB/H |  | 0.0006 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP03 | 13.31 | NATURAL GAS | 33.48 | MMBTU/H | UNIT CP03 IS A BURNHAM BOILER AT CAESAR'S PALACE. UNITS CP01 THROUGH CP05 (FIVE BOILERS) ARE SUBJECT TO THE ANNUAL LIMIT OF TOTAL OPERATING TIME FOR 33,520 HOURS PER YEAR. | Sulfur Oxides (SOx) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 7446 | P | FUEL IS LIMITED TO NATURAL GAS. | 0.0006 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 0.02 | LB/H |  | 0.0006 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP26 | 13.31 | NATURAL GAS | 24 | MMBTU/H | UNIT CP26 IS A UNILUX BOILER AT CAESAR'S PALACE. THE UNIT IS ALLOWED TO OPERATE UP TO 8,760 HOURS PER YEAR. | Sulfur Oxides (SOx) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 7446 | P | FUEL IS LIMITED TO NATURAL GAS. | 0.0006 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 0.01 | LB/H |  | 0.0006 | LB/MMBTU |  | 0 | 0 | N
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | TURBINE GENERATORS - UNITS CC007 AND CC008 AT CITY CENTER | 16.11 | NATURAL GAS | 4.6 | MMBTU/H | THE TWO UNITS ARE IDENTICAL SOLAR MERCURY COMBUSTION GAS TURBINES FOR ELECTRIC POWER GENERATION. EACH UNIT IS RATED AT 4.6 MMBTU/HR, AND IS ALLOWED TO OPERATE 24 HOURS/DAY AND 8,760 HOURS/YEAR. | Sulfur Oxides (SOx) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 7446 | P | LIMITING THE FUEL TO NATURAL GAS ONLY. | 0.0065 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 0.03 | LB/H |  | 0.0065 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | LARGE INTERNAL COMBUSTION ENGINES (&gt;600 HP) - UNIT HA13 | 17.11 | DIESEL OIL | 1232 | HP | UNIT HA13 IS A MARATHON DIESEL GENERATOR AT HARRAH'S LAS VEGAS. ALL THE SEVEN (7) DIESEL GENERATORS AT HARRAH'S LAS VEGAS ARE FOR EMERGENCY USE ONLY. EACH ONE OF THEM IS SUBJECT TO THE SAME LIMIT OF OPERATING TIME FOR 2 HOURS PER DAY AND 36 HOURS PER YEAR. THE EMISSION LIMITS ARE CALCULATED BASED ON THE EMISSION FACTORS TAKEN FROM AP-42. | Sulfur Oxides (SOx) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 7446 | P | THE UNIT SHALL COMBUST ONLY LOW-SULFUR DIESEL OIL WITH A SULFUR CONTENT LESS THAN 0.05%. | 0.0004 | LB/HP-H |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 0.55 | LB/H |  | 0.0004 | LB/HP-H |  | 0 | 0 | N
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | EMERGENCY GENERATORS - UNITS LX024 AND LX025 AT LUXOR | 17.11 | DIESEL OIL | 2206 | HP | THE TWO UNITS ARE IDENTICAL CATERPILLAR GENERATORS MODEL 3512C. EACH UNIT HAS A FOUR-STROKE COMPRESSION-IGNITION ENGINE RATED AT 2,206 HORSE POWER (HP). THE EMISSION LIMITS REPORTED HEREIN ARE BASED ON THE ATC PERMIT FOR MODIFICATION #10 DATED SEPTEMBER 20, 2006. EACH UNIT IS ALLOWED TO OPERATE UP TO ONE HOUR PER DAY AND FIFTY TWO HOURS PER YEAR. | Sulfur Oxides (SOx) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 7446 | P | LIMITING SULFUR CONTENT IN THE DIESEL OIL TO 0.03% | 0.0002 | LB/HP-H |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 0.54 | LB/H |  | 0.0002 | LB/HP-H |  | 0 | 0 | N |  | EMISSION LIMIT 2 APPLIES TO EACH UNIT.
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | WATER HEATERS - UNITS NY037 AND NY038 AT NEW YORK - NEW YORK | 13.31 | NATURAL GAS | 2 | MMBTU/H | THE TWO UNITS ARE IDENTICAL RBI FUTURA III WATER HEATERS.THE EMISSION LIMITS REPORTED HEREIN ARE BASED ON THE ATC PERMIT FOR MODIFICATION #9 DATED SEPTEMBER 6, 2006. EACH UNIT IS ALLOWED TO OPERATE 24 HOURS/DAY AND 8,760 HOURS/YEAR. | Sulfur Oxides (SOx) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 7446 | P | LIMITING FUEL TO NATURAL GAS ONLY. | 0.0006 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 0.0012 | LB/H |  | 0.0006 | LB/MMBTU |  | 0 | 0 | N |  | EMISSION LIMIT 2 APPLIES TO EACH UNIT.
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Three (3) Package Boilers | 12.31 | Natural Gas | 243 | MMBTU/H | Three (3) New Natural Gas-Fired 243 MMBtu/hr Package Boilers | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.0054 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 143952 | 0 | N | 2014 | The economic analysis indicates the level of VOC reduction does not justify the use of catalytic oxidation. Based on the excessive cost per ton of VOC removed per year, installing catalytic oxidation on the package boilers is not considered a feasible option for reducing VOC emissions.
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Startup Heater | 12.31 | Natural Gas | 101 | MMBTU/H | Natural Gas-Fired 101 MMBtu/hr Startup Heater. Installed in 1976. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Limited Use (200 hr/yr) | 0.0054 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT START-UP HEATER | 12.31 | NATURAL GAS | 38 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICE | 0.19 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.048 | T/YR | ROLLING 12 MONTH AVERAGE | 0.002 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | START-UP BOILER | 12.31 | NATURAL GAS | 240 | MMBTU/H |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD AND EFFICIENT OPERATING PRACTICES | 0.96 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.004 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 |  |  | 0 | 0 | N |  | PERIODIC STACK TESTING TO VERIFY COMPLIANCE
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | TUNNEL FURNACES SN-20 AND 21 | 12.31 | NATURAL GAS | 234 | MMBTU/H | 2 TUNNEL FURNCE SECTIONS 234 MMBTU/HR AND 192 MMBTU/HR MADE UP OF A SERIES OF INDIVIDUAL 3 MMBTU BURNERS. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.0054 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Startup Heater | 12.31 | Natural gas | 110.12 | MMBTU/H |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0.0014 | LB/MMBTU | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.01 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Startup Heater | 12.31 | natural gas | 104 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0.0054 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | FOUR (4) NATURAL GAS-FIRED BOILERS | 12.31 | NATURAL GAS | 218 | MMBTU/HR, EACH | FUEL INPUT TO ALL FOUR BOILERS SHALL NOT EXCEED 2,802 MMCF/YEAR | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | PROPER DESIGN AND GOOD COMBUSTION PRACTICES | 5.5 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0221 | SUBARU OF INDIANA AUTOMOTIVE, INC. | SUBARU OF INDIANA AUTOMOTIVE, INC. | TIPPECANOE | IN | 47905 | USA | DENISE COOGAN | 7654491111 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: AIDA DEGUZMAN 317-233-4972 ADEGUZMA@IDEM.IN.GOV SECTION CHIEF: CHRYSTAL WAGNER 317-234-1203 | 157-34774-00050 | 3711 | 336111 | 110000404205 | 07/28/2014 &nbsp;ACT | 12/23/2014 &nbsp;ACT | 2015-08-14 | 2016-07-06 | C | HTTP://PERMITS.AIR.IDEM.IN.GOV/34774D.PDF | AUTOMOBILE AND LIGHT DUTY-TRUCKS MANUFACTURING |  | PAINT HEATERS, OVENS | 12.31 | NATURAL GAS | 50 | MMBTU/H | VARIOUS HEATERS AND OVENS RANGES FROM 1 MMBTU/HR TO <50 MMBTU/HR | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.005 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADDITIONAL PSD BACT: (A) THE COMBUSTION OF ONLY NATURAL GAS FUEL; AND (B) GOOD COMBUSTION PRACTICES, WHICH INCLUDES PROPER CARE AND MAINTENANCE OF THE NATURAL GAS BURNER SYSTEMS.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | NATURAL GAS AUXILIARY BOILERS (EU-012A, EU-012B, EU-012C) | 12.31 | NATURAL GAS | 218.6 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES AT ALL TIMES THE BOILERS ARE IN OPERATION | 5.5 | LB/MMCF EACH | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 1877.39 | MMCF/12 MONTH EACH | ROLLING AVERAGE | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: SHALL COMBUST NATURAL GAS
*IN-0287 | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING STATION | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING | KNOX | IN | 47528 | USA | PATRICK COUGHLIN | 317-838-2108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Mehul Sura 317-233-6868 msura@IDEM.IN.gov Section Chief - Tripurari P. Sinha Ph. D. 317-234-4907 | 083-38023-00003 | 4911 | 22 | Not Entered | 12/22/2016 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2018-07-25 | 2018-07-25 | C | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | stationary electric utility generating station |  | Auxiliary Boiler | 12.31 | natural gas | 213 | MMBtu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0.005 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This BACT is for Startup and Shutdown emissions only
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Auxiliary boilers | 12.31 | natural gas | 171 | mm btu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | boiler A and B (010 and 011) | 12.31 | natural gas/fuel gas | 248 | mm btu/hr (each) |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices and proper operation and maintenance | 0.0054 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | boiler B-201 | 12.31 | natural gas/fuel gas | 229 | mm btu |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices and proper operation and maintenance | 0.0054 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0389 | KARN WEADOCK GENERATING COMPLEX | CONSUMERS ENERGY | BAY | MI | 48732-9601 | USA | JAMES M. WALKER | 5177880428 | JMWALKER@CMSENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | FOR TECHNICAL QUESTIONS ABOUT THIS PERMIT, PLEASE CONTACT THE PERMIT ENGINEER - DAVID K. RIDDLE RIDDLED@MICHIGAN.GOV (517-373-7081) | 341-07 | 4911 | 221112 | 26-01700033 | 10/15/2007 &nbsp;ACT | 12/29/2009 &nbsp;ACT | 2010-03-08 | 2010-12-16 | U |  | ELECTRICITY GENERATING FACILITY, EXISTING CAPACITY GREATER THAN 2,000 MW. | AFTER CONSTRUCTION CONSUMERS WILL RETIRE 5 TO 7 COAL-FIRED BOILERS (638 - 958 MW) STATEWIDE. FINAL CONDITIONS WILL BE AT WWW.DEQ.STATE.MI.US/APS/FINALCONDITIONS.SHTML. MATERIAL HANDLING - CONTACT PERMIT ENGINEER FOR TECHNICAL INFORMATION (DAVID RIDDLE, 517-373-7081). INCLUDES 9 EMISSION UNITS. COAL, LIMESTONE, SORBENT AND ASH HANDLING PROCESSES. VARIOUS BACT LIMITS FOR OPACITY, PM AND PM10. BACT FOR THE MATERIAL HANDLING EQUIPMENT CONSISTED OF A COMBINATION OF PASSIVE CONTROL EQUIPMENT SUCH AS WET/CHEMICAL SUPPRESSION SYSTEMS AND ENCLOSED CONVEYORS; AND ACTIVE CONTROL SUCH AS FABRIC FILTERS. ACTIVE CONTROL IS LIMITED TO 0.004 GR/DSCF. | AUXILARY BOILER | 12.31 | NATURAL GAS | 220 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N | EFFICIENT COMBUSTION | 0.0013 | LB/MMBTU | TEST METHOD | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | EMISSIONS ARE LESS THAN 10 PPM.
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUAUXBOILER (Auxiliary Boiler) | 12.31 | natural gas | 182 | MMBTU/H | One natural gas-fired auxiliary boiler rated at 182 MMBTU/H fuel heat input. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices. | 0.004 | LB/MMBTU | TEST PROTOCOL WILL SPECIFY AVG TIME. | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | An oxidation catalyst is greater than $40,000/ton for CO and VOC together.
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Boiler, Nat Gas Fired | 12.31 | NATURAL GAS | 261 | MMBTU/H | 261 MMBTU/H natrual gas-fired boiler, equipped with low-NOx burners, SCR, and CO catalytic oxidation | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | good combustion practices (continuous oxygen trim/tune ups requires)
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Boiler #1 | 12.31 | natural gas | 200 | MMBTU/H | The boiler is capable of combusting natural gas and Fuel Oil | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.0054 | LB/MMBTU | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | VOC must be measured as mass
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Boiler #2 | 12.31 | natural gas | 200 | MMBTU/H | The boiler is capable of combusting natural gas and Fuel Oil | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.0054 | LB/MMBTU | 3-HOUR OR TEST METHOD AVERAGE | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | VOC must be measured as mass
NM-0052 | ZIA II GAS PLANT | DCP MIDSTREAM L.P. | LEA | NM | 88255 | USA | JENNIFER HANNA | 4326205460 | JHANNA@DCPMIDSTREAM.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Joseph Kimbrell, 505-476-4300, joseph.kimbrell@state.nm.us | PSD-5217 | 1311 | 211111 | 110056438083 | 11/13/2013 &nbsp;ACT | 04/25/2014 &nbsp;ACT | 2015-11-19 | 2016-07-07 | A | https://www.env.nm.gov/aqb/ | Natural Gas Processing plant using cryogenic process and designed to operate at 230 MMscf/day of natural gas. | The permittee submitted an application on 5/13/2015 to revise the permit. Most BACT determinations will not change. | Industrial Sized Boilers/Furnaces &gt;100 mmBtu/hr | 12.31 | Natural gas | 114 | mmBtu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0 |  |  | BACT-PSD | NSPS , SIP , OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
OH-0310 | AMERICAN MUNICIPAL POWER GENERATING STATION | AMERICAN MUNICIPAL POWER | MEIGS | OH | 45771 | USA | RANDY MEYER | 6143376222 | RMEYER@AMP-OHIO.ORG | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0104461 | 4911 | 221112 | 110000384325 | 05/15/2006 &nbsp;ACT | 10/08/2009 &nbsp;ACT | 2008-04-15 | 2009-11-06 | A |  | TWO 5191 MMBTU/HOUR PULVERIZED COAL-FIRED BOILERS; ONE 150 MMBTU/HOUR NATURAL GAS AUXILIARY BOILER, ONE FLY ASH AND GYPSUM LANDFILL, COAL STORAGE, CRUSHERS, FERTILIZER PLANT, LIMESTONE AND FLY ASH HANDLING EQUIPMENT, AND COOLING CELLS. ADMINISTRATIVE MODIFICATION 10/09 TO ADD CASE-BY-CASE MACT FOR BOILERS. 1ST ISSUED 2/7/08 AS PTI#06-08138; STILL INITIAL INSTALLATION | FUGITIVE EMISSIONS FROM STORAGE PILES (COAL,LIMESTONE, UREA), CONVEYING, HANDLING, ROADWAYS, BARGE OR TRUCK UNLOADING WERE NOT ENTERED INTO THE DATABASE DUE TO THE INSIGNIFICANT EMISSIONS (MOST < 1 TON FUGITIVE PM) AND LACK OF PROCESS CODES TO ENTER THEM. | AUXILIARY BOILER | 12.31 | NATURAL GAS | 150 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.83 | LB/H |  | BACT-PSD | SIP | U | 0 | U | 0.36 | T/YR | PER ROLLING 12 MONTHS | 5.5 | LB/MMCF |  | 0 | 0 | N
*TX-0641 | PINECREST ENERGY CENTER | PINECREST ENERGY CENTER LLC | ANGELINA | TX |  | USA | KATHLEEN SMITH | 281-253-4385 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | PSDTX1298 | 4911 |  |  | 06/22/2012 &nbsp;ACT | 11/12/2013 &nbsp;ACT | 2013-11-21 | 2017-11-17 | A |  | Combinec Cycle Electric Generating Plant | 103839 | Auxiliary boiler | 12.31 | natural gas | 150 | MMBTU/H | limited to 876 hours per year of operation | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | pipeline quality natural gas and good combustion | 0.9 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Heating Medium Heaters | 12.31 | natural gas | 130 | MMBTU/H | There are (5) heaters each at 130 MMBtu/hr which operate when the turbine exhaust is not providing enough heat for the amine regenrating heating oil system | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0.26 | LB/H | 1 HOUR | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0708 | LA PALOMA ENERGY CENTER | LA PALOMA ENERGY CENTER, LLC | CAMERON | TX |  | USA | GARY NEUS | (281) 682-8448 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 101542 PSDTX1288 | 4911 | 221112 | unknown | 03/15/2012 &nbsp;ACT | 02/07/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is a new electric power plant, fueled by pipeline quality natural gas. The design of the plant is standard combined cycle (CC) technology. |  | boiler | 12.31 | natural gas | 150 | MMBTU/H | annual usage limitation to 876 hours per year | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | natural gas as fuel
TX-0813 | ODESSA PETROCHEMICAL PLANT | REXTAC, LLC | ECTOR | TX |  | USA | STEVE MCHANEY | 432-332-0058 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, 512-239-1541, joseph.janecka@tceq.texas.gov | 16963, PSDTX1478, GHGPSDTX148 | 2821 | 325211 | Not Found | 09/23/2016 &nbsp;ACT | 11/22/2016 &nbsp;ACT | 2016-11-30 | 2017-11-16 | D |  | Petrochemical Manufacturing Facility |  | Boilers | 12.31 | natural gas | 223 | MMBTU/H | 2 boilers | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Best combustion practices | 0.0005 | LB/MMBTU |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Db
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Auxiliary Boiler | 12.31 | Natural Gas | 100 | mmBtu/hr | Limited to 2,000 hours of operation per year. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Use of Natural Gas & Good Combustion Practices | 0.6 | LB/H |  | BACT-PSD |  | U | 0 | U | 0.006 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | AMMONIA CATALYST STARTUP HEATER | 12.39 | NATURAL GAS | 106.3 | MMBTU/H | ANNUAL NATURAL GAS USAGE LIMITED TO 20.84 MMCF. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | NATURAL GAS COMBUSTION ONLY, PROPER DESIGN AND GOOD COMBUSTION PRACTICES | 5.5 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS TYPICALLY CONSIDERED NOT FEASIBLE ON LIMITED USE EMISSION UNITS.
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILER, VACUUM DEGASSER | 13.29 | NATURAL GAS | 51.2 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.0054 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACE, ANNEALING PICKLING LINE | 13.29 | NATURAL GAS | 66 | MMBTU/H | ANNEALING PICKLING LINE FURNACE SN-47; ANNEALING COATING LINE FURNACE , SN 51; | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 5.4 | X10^-4 LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Waste Heat Boilers | 13.31 | Natural Gas | 50 | MMBTU/H | Five (5) Natural Gas-Fired 50 MMBtu/hr Waste Heat Boilers. Installed in 1986. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.0054 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | BOILERS SN-26 AND 27, GALVANIZING LINE | 13.31 | NATURAL GAS | 24.5 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.0054 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-40 AND SN-42, DECARBURIZING LINE | 13.31 | NATURAL GAS | 22 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.0054 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | STARTUP HEATER EU-002 | 13.31 | NATURAL GAS | 70 | MMBTU/HR |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.378 | LB/H | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 200 | H/YR |  | 0 |  |  | 0 | 0 | N | 2016 | SHALL COMBUST NATURAL GAS
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Regenerative Heaters | 13.31 | natural gas | 7.37 | mm btu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGFUELHTR (Two fuel pre-heaters identified as EUFUELHTR1 &amp; EUFUELHTR2) | 13.31 | Natural gas | 27 | MMBTU/H | Two natural gas fired dew point heaters for warming the natural gas fuel (EUFUELHTR1 & EUFUELHTR2 in flexible group FGFUELHTR). The total combined heat input during operation shall not exceed 27 MMBTU/H (each) as well. The CO2e limit is for both units combined; however the other limits are per unit. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices. | 0.15 | LB/H | HOURLY; EACH FUEL HEATER | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | An oxidation catalyst is greater than $40,000/ton for CO and VOC together, factoring in the redundancy of the heaters (limited joint operation).
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Regeneration Heater, methanol to gasoline | 13.31 | NATURAL GAS | 13 | MMBTU/H | 13 MMBTU/H methanol-to-gasoline regeneration heater, equipped with low-NOx burner | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | good combustion practices (continuous oxygen trim or annual tune-ups) 13 MMBTU/H methanol-to-gasoline regeneration heater, equipped with low-NOx burner
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Reactor Heater, 5 | 13.31 | NATURAL GAS | 12 | MMBTU/H | Five 12 MMBTU/H reactor heaters, equipped with low-NOx burners | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | good combustion practices (continuous oxygen trim or annual tune-ups) Five 12 MMBTU/H reactor heaters, equipped with low-NOx burners
TX-0813 | ODESSA PETROCHEMICAL PLANT | REXTAC, LLC | ECTOR | TX |  | USA | STEVE MCHANEY | 432-332-0058 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, 512-239-1541, joseph.janecka@tceq.texas.gov | 16963, PSDTX1478, GHGPSDTX148 | 2821 | 325211 | Not Found | 09/23/2016 &nbsp;ACT | 11/22/2016 &nbsp;ACT | 2016-11-30 | 2017-11-16 | D |  | Petrochemical Manufacturing Facility |  | small Boiler | 13.31 | natural gas | 39.9 | MMBtu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | best combustion practices | 0.0005 | MMBTU/HR |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Dc
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Dryer Regenerator Heater - 005 | 13.39 | process fuel gas | 29 | mm btu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices and proper operation and maintenance | 0.0054 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Gas Turbines (8 units) | 15.11 | natural gas | 333 | mm btu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices and fueled by natural gas | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | FGCTGHRSG (2 Combined Cycle CTGs with HRSGs) | 15.21 | Natural gas | 8322 | MMBTU/H | There are 2 combined cycle natural gas-fired combustion turbine generators (CTGs) with heat recovery steam generators (HRSG) identified as EUCTGHRSG1 & EUCTGHRSG2 in the flexible group FGCTGHRSG. The total hours for startup and shutdown for each train shall not exceed 500 hours per 12-month rolling time period. The throughput capacity is 3421 MMBTU/H for each turbine, and 740 MMBTU/H for each duct burner for a combined throughput of 4161 MMBTU/H or 8322 MMBTU/H for both trains. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation Catalyst Technology and Good Combustion Practices | 4 | PPM | TEST PROTOCOL WILL SPECIFY | BACT-PSD |  | N | 85 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit above is 4 ppmvd at 15%O2 and is for EACH CTGHRSG. Startup and shutdown operations are limited to 500 hours per 12-month rolling time period for each CTGHRSG train. Startup is defined as the period of time from initiation of the combustion process (flame-on) from shutdown status and continues until steady state operation (loads greater than a demonstrated percent of design capacity) is achieved. Shutdown is defined as that period of time from the lowering of the turbine output below the demonstrated steady state level, with the intent to shut down, until the point at which the fuel flow to the combustor is terminated. The demonstrated percent of design capacity, or demonstrated steady state level, shall be described in the startup and shutdown emission minimization plan. The efficiency range is 85-90 percent.
*TX-0641 | PINECREST ENERGY CENTER | PINECREST ENERGY CENTER LLC | ANGELINA | TX |  | USA | KATHLEEN SMITH | 281-253-4385 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Marc Sturdivant 512-239-1313 marc.sturdivant@tceq.texas.gov | PSDTX1298 | 4911 |  |  | 06/22/2012 &nbsp;ACT | 11/12/2013 &nbsp;ACT | 2013-11-21 | 2017-11-17 | A |  | Combinec Cycle Electric Generating Plant | 103839 | combined cycle turbine | 15.21 | natural gas | 700 | MW | The generating equipment consists of two natural gas-fired combustion turbines (CTs), each exhausting to a fired heat recovery steam generator (HRSG) to produce steam to drive a shared steam turbine generator. The steam turbine is rated at 271 MW of electric output. Three models of combustion turbines are being considered for this site: the General Electric 7FA.05, the Siemens SGT6-5000F(4), and the Siemens SGT6-5000F(5). The final selection of the combustion turbine will not be made until after the permit is issued. Plant output will range between 637 and 735 MW, depending on the model turbine selected. Duct Burners are rated at 750 MMBtu/hr each. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 2 | PPMVD | INITIAL STACK TEST, 15% OXYGEN | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Combustion Turbine | 15.21 | natural gas | 87 | MW | The exhaust heat from the turbine will be used to heat a heating medium which is used to regenerate rich amine from the acid gas removal system. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 2 | PPMVD | 1 HOUR BASED ON STACK TEST | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0708 | LA PALOMA ENERGY CENTER | LA PALOMA ENERGY CENTER, LLC | CAMERON | TX |  | USA | GARY NEUS | (281) 682-8448 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Randy Hamilton 512-239-1512 randy.hamilton@tceq.texas.gov | 101542 PSDTX1288 | 4911 | 221112 | unknown | 03/15/2012 &nbsp;ACT | 02/07/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | The proposed project is a new electric power plant, fueled by pipeline quality natural gas. The design of the plant is standard combined cycle (CC) technology. |  | (2) combined cycle turbines | 15.21 | natural gas | 650 | MW | The specific equipment includes two combustion turbines (CTs) connected to electric generators, producing between 183 and 232 MW of electricity, depending on ambient temperature and the selected CT. The two HRSGs use duct burners rated at 750 MMBtu/hr each to supplement the heat energy from the CTs. The steam from the two HRSGs is combined and routed to a single steam turbine driving a third electric generator with an electricity output capacity of 271 MW. Depending on the selected CT, total plant output at 59Â°F is between 637 MW and 735 MW. The applicant is considering three models of CT; one model will be selected and the permit revised to reflect the selection before construction begins. The three CT models are: (1) General Electric 7FA.04; (2) Siemens SGT6-5000F(4); or (3) Siemens SGT6-5000F(5). | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 2 | PPMVD | @15% O2, 3-HR ROLLING | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0712 | TRINIDAD GENERATING FACILITY | SOUTHERN POWER COMPANY | HENDERSON | TX |  | USA | KELLI MCCULLOUGH | (205) 257-6720 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Tzvi Shalem 512-239-1310 tzvi.shalem@tceq.texas.gov | 111393 PSDTX1368 | 4911 | 221112 | 110007199735 | 06/27/2013 &nbsp;ACT | 11/20/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | Southern Power Company (SPC) is proposing to construct an electric generating facility near Trinidad, Henderson County, Texas. The Trinidad Generating Facility (TGF) will include a natural gas-fired combined cycle combustion turbine generator (CTG) equipped with heat recovery steam generator (HRSG) and duct burners (DB). |  | combined cycle turbine | 15.21 | natural gas | 497 | MW | The facility will consist of a Mitsubishi Heavy Industries (MHI) J model gas fired combustion turbine nominally rated at 497 megawatts (MW) equipped with a HRSG and DB with a maximum design capacity of 402 million British thermal units per hour (MMBtu/hr). The gross nominal output of the CTG with HRSG and DB is 530 MW. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 4 | PPMVD | @15% O2 1-HR | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Combined Cycle Turbine/Duct Burner | 15.21 | Natural Gas | 2419.61 | mmBtu/Hr | This entry is for both of two identical units at the facility. Nominal 197 mW General Electric Frame 7FA.04 Turbine w/ Duct Burner - throughput denotes aggregate heat input of turbine and duct burner (HHV). | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 18 | (Volatile Organic Compounds (VOC)) | VOC | B | Oxidation Catalyst & Good Combustion Practices | 5.3 | LB/H |  | BACT-PSD |  | U | 0 | U | 0.0022 | LB/MMBTU |  | 2 | PPM | @ 15% O2 | 0 | 0 | N |  | The above VOC limit is applicable with duct firing. The limit without duct firing is 1 ppm @ 15% O2.
*IN-0287 | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING STATION | DUKE ENERGY INDIANA, LLC - EDWARDSPORT GENERATING | KNOX | IN | 47528 | USA | PATRICK COUGHLIN | 317-838-2108 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | Permit Writer: Mehul Sura 317-233-6868 msura@IDEM.IN.gov Section Chief - Tripurari P. Sinha Ph. D. 317-234-4907 | 083-38023-00003 | 4911 | 22 | Not Entered | 12/22/2016 &nbsp;ACT | 07/10/2018 &nbsp;ACT | 2018-07-25 | 2018-07-25 | C | https://www.in.gov/apps/idem/caats/permitDetail.xhtml | stationary electric utility generating station |  | combined cycle combustion turbines | 15.25 | natural gas and syn gas | 2129 | MMBtu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 48.5 | TONS/YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | This BACT is for Startup and Shutdown emissions only
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Five (5) Natural Gas Fired Combustion Turbines | 16.11 | Natural Gas | 37.6 | MMBTU/H | Five (5) Natural Gas-Fired Solar Combustion Turbines rated at 37.6 MMBtu/hr each. Installed in 1976. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.0021 | LB/MMBTU | 3-HR AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 291788 | 0 | N | 2014 | The economic analysis indicates the level of VOC reduction does not justify the use of catalytic oxidation. Based on the excessive cost per ton of VOC removed per year, installing catalytic oxidation on the turbines is not considered a feasible option for reducing VOC emissions.
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Emergency Generator | 17.11 | diesel fuel | 142 | GAL/H | rated @ 2,000 KW | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0.4 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.44 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Emergency Generator | 17.11 | distillate fuel oil | 3755 | HP |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 0.4 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY GENERATOR | 17.11 | NO. 2 FUEL OIL | 4690 | B-HP | ANNUAL HOURS OF OPERATION NOT TO EXCEED 200 HOURS. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.31 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | EMERGENCY GENERATORS (EU014A AND EU-014B) | 17.11 | DISTILLATE OIL | 3600 | HP EACH |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.35 | G/HP-H EACH | 3 HOUR AVERAGE | BACT-PSD |  | N | 0 |  | 500 | H/YR EACH |  | 0 |  |  | 0 | 0 | N | 2016
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Diesel Engines | 17.11 | Diesel | 0 |  | Water Pumps (2 units) = 355 hp Tank Deluge Pumps (2 units) = 800 hp Generator = 1340 hp | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices, Use ultra low sulfur diesel, and comply with 40 CFR 60 Subpart IIII | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUEMENGINE (Diesel fuel emergency engine) | 17.11 | Diesel Fuel | 22.68 | MMBTU/H | a 2,922 horsepower (HP) (2,179 kilowatts (kW)) diesel fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Restricted to 4 hours/day, except during emergency conditions and stack testing, and 500 hours/year on a 12-month rolling time period basis. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices. | 1.87 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | On average, an oxidation catalyst is greater than $88,000/ton for CO and VOC together.
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Emergency Generator | 17.11 | Diesel | 2015.7 | HP | Nominal 1,500 kW. Limited to 100 hours/year. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 1.24 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Diesel Fired Well Pump | 17.21 | Diesel | 2.7 | MMBTU/H | 2.7 MMBtu/hr Diesel Fired Well Pump. Installed in 1966. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Limited Operation of 168 hr/yr. | 0.36 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Fire Pump | 17.21 | diesel fuel | 14 | GAL/H | rated @ 235 KW | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0.25 | G/KW-H | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 0.03 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Firewater Pump Engine | 17.21 | distillate fuel oil | 373 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Tier IV standards for non-road engines at 40 CFR 1039.102, Table 7. | 0.4 | G/KW-H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | DIESEL-FIRED EMERGENCY WATER PUMP | 17.21 | NO. 2 FUEL OIL | 481 | BHP | ANNUAL OPERATION LIMITED TO 200 HR, | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 0.141 | G/B-HP-H | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | ADD ON CONTROLS ARE NOT NORMALLY REQUIRED FOR LIMITED USE EMISSION UNITS.
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel Firewater pump engines (6 units) | 17.21 | diesel | 425 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Diesel emergency generator engine - EGEN | 17.21 | diesel | 350 | hp |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | complying with 40 CFR 63 subpart ZZZZ | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MI-0423 | INDECK NILES, LLC | INDECK NILES, LLC | CASS | MI | 49120 | USA | MICHAEL DUBOIS | 847-520-3212 | MDUBOIS@INDECKENERGY.COM | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Catherine Asselin at 517-284-6786, or at asselinc@michigan.gov, for technical questions regarding the permit. Thank you. | 75-16 | 4911 | 221112 | Not Found | 10/25/2016 &nbsp;ACT | 01/04/2017 &nbsp;ACT | 2017-06-02 | 2018-03-08 | A |  | Natural gas combined cycle power plant. | The permit includes equipment not entered into the RBLC due to a lack of emission limits or material limits; these include a cold cleaner, a number of space heaters, and two fuel tanks. | EUFPENGINE (Emergency engine--diesel fire pump) | 17.21 | Diesel | 1.66 | MMBTU/H | A 260 brake horsepower (bhp) diesel-fueled emergency engine manufactured in 2011 or later and a displacement of <10 liters/cylinder. Powers a fire pump used for a back up during an emergency (EUFPENGINE). Restricted to 1 hour/day, except during emergency conditions and stack testing, and 100 hours/year on a 12-month rolling time period basis. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 0.64 | LB/H | TEST PROTOCOL WILL SPECIFY AVG TIME | BACT-PSD |  | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | On average, an oxidation catalyst is greater than $308,000/ton for CO and VOC together.
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | firewater pumps, diesel | 17.21 | diesel | 325 | HP, EACH | Eight 325 hp diesel firewater pumps | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | comply with NSPS IIII, 52 hr/yr non-emergency operation
WV-0025 | MOUNDSVILLE COMBINED CYCLE POWER PLANT | MOUNDSVILLE POWER, LLC | MARSHALL | WV | 26041 | USA | JON WILLIAMS | 716-856-3333 | JMWILLIAMS@MOUNDSVILLE-POWER.COM | 3 | WV001 | WEST VIRGINIA DEPT. OF ENVRIONMENTAL PROTECTION; DIV. OF AIR QUALITY | MR. JOE KESSLER, PE | (304)926-0499X1219 | Joseph.r.kessler@wv.gov | Permit Writer: Mr. Steve Pursley, PE WV Division of Air Quality 304-926-0499 x1218 | R14-0030 | 4911 | 221112 | Not Found | 05/14/2014 &nbsp;ACT | 11/21/2014 &nbsp;ACT | 2015-01-05 | 2018-05-01 | U |  | Nominal 549 mW(output) natural gas-fired combined cycle power plant. |  | Fire Pump Engine | 17.21 | Diesel | 251 | HP | Limited to 100 Hours/year. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.17 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Gasoline Fired Fire Pump Engine | 17.22 | Gasoline | 2.1 | MMBTU/H | 2.1 MMBtu/hr Gasoline-Fired Fire Pump Engine. Installed in 1978. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Limited Operation of 168 hr/yr. | 3.03 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | SMALL HEATERS AND DRYERS SN-05 THROUGH 19 | 17.23 | NATURAL GAS | 0 |  | RH VESSEL PREHEATER STATION, VESSEL TOP PART DRYER, RH VESSEL NOZZLE DRYER RH DEGASSER BURNER/LANCE LADLE PREHEATERS LADLE DRYOUT STATION VERTICAL LADLE HOLDING STATION TUNDISH PREHEATERS #1 THROUGH #4 | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.0054 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Three (3) Flares | 19.31 | Natural Gas | 1.25 | MMBTU/H | 1.25 MMBtu/hr Ammonia Tank Flare, 0.4 MMBtu/hr Emergency Flare, and 1.25 MMBtu/hr Small Flare | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Work Practice Requirements and Limited Use (limit venting to 168 hr/yr each during startup, shutdown, and maintenance events) | 0.0054 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT AMMONIA VENT FLARE | 19.31 | NATURAL GAS | 0.26 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICE | 0.0057 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.025 | T/YR | ROLLING 12 MONTH AVERAGE | 0.0054 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT PROCESS SSM FLARE | 19.31 | NATURAL GAS | 0.05 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICE | 0.0051 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.023 | T/YR | ROLLING 12 MONTH AVERAGE | 0.0054 | LB/MMBTU |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA STORAGE FLARE | 19.31 | NATURAL GAS | 0.05 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD AND EFFICIENT OPERATING PRACTICES | 0.0011 | LB/H | ROLLINIG 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 0.0041 | T/YR | ROLLING 12 MONTH AVERAGE | 0.0054 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Ammonia Flare | 19.31 | natural gas | 0.4 | MMBTU/H | There are four (4) natural gas pilots | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | work practice/good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | There is no numeric emission limit in the permit.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | FRONT END PROCESS FLARE | 19.31 | NATURAL GAS PILOT | 0.25 | MMBTU/H | HEAT INPUT IS FOR NATURAL GAS PILOT ONLY. SSM EMISSIONS ARE CONTROLLED BY THE FLARE AND ARE LIMITED TO 336 HOURS OF VENTING PER YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | NATURAL GAS FOR PILOT, FLARE MINIMIZATION PRACTICES | 0.0054 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 47.26 | LB/H, SSM VENTING | 3-HR AVERAGE | 0 |  |  | 0 | 0 | N |  | SSM VENTING LIMITED TO 336 HR PER YEAR.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | BACK END AMMONIA FLARE | 19.31 | NATURAL GAS | 0.25 | MMBTU/H | HEAT INPUT IS FOR PILOT ONLY. SSM EMISSIONS ARE CONTROLLED BY THE FLARE AND ARE LIMITED TO 336 HR/YR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.0054 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 11.73 | LB/H, SSM VENTING | 3-HR AVERAGE | 0 |  |  | 0 | 0 | N |  | SSM VENTING LIMITED TO 336 HR PER YEAR.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | AMMONIA STORAGE FLARE | 19.31 | NATURAL GAS | 0.13 | MMBTU/H | HEAT INPUT IS FOR PILOT ONLY. SSM EVENTS HAVE SEPARATE LIMITS. SSM VENTING IS LIMITED TO 168 HOURS PER YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.0054 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | SSM VENTING LIMITED TO 168 HR PER YEAR.
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | UAN PLANT VENT FLARE | 19.31 |  | 0.19 | MMBTU/H | HEAT INPUT IS FOR NATUAL GAS PILOT. SSM EMISSIONS HAVE SEPARATE LIMITS. SSM VENTING LIMITED TO 336 HOURS PER YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | NATURAL GAS PILOT, FLARE MINIMIZATION PRACTICES | 0.0054 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Flare No. 1 - 008 | 19.31 | natural gas | 85097 | MM BTU/yr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | complying with 40 CFR 60.18; good combustion practices (including establishment of flare minimization practices) | 98 | % | REMOVAL EFFICIENCY | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Pyrolysis Gasoline Tank Flare - 009 | 19.31 | natural gas | 0.66 | mm btu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | complying with 40 CFR 60.18 and 63.11; good combustion practices (including establishment of flare minimization practices) | 98 | % | REMOVAL EFFICIENCY | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | vessel evacuation flare - 018 | 19.31 | natural gas | 3.04 | mm btu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices (including establishment of flare minimization practices) | 98 | % | REMOVAL EFFICIENCY | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NM-0052 | ZIA II GAS PLANT | DCP MIDSTREAM L.P. | LEA | NM | 88255 | USA | JENNIFER HANNA | 4326205460 | JHANNA@DCPMIDSTREAM.COM | 6 | NM001 | NEW MEXICO ENVIRONMENT DEPT/AIR QUALITY BUREAU | MS. CEMBER HARDISON | (505)476-4346 | cember.hardison@state.nm.us | Joseph Kimbrell, 505-476-4300, joseph.kimbrell@state.nm.us | PSD-5217 | 1311 | 211111 | 110056438083 | 11/13/2013 &nbsp;ACT | 04/25/2014 &nbsp;ACT | 2015-11-19 | 2016-07-07 | A | https://www.env.nm.gov/aqb/ | Natural Gas Processing plant using cryogenic process and designed to operate at 230 MMscf/day of natural gas. | The permittee submitted an application on 5/13/2015 to revise the permit. Most BACT determinations will not change. | Units FL1 &amp; FL2: Refinery Flares (Inlet Gas Flare &amp; Acid Gas Flare) | 19.33 | natural gas, acid gas | 2.3 | mmBtu/hr | Only for routine or predictable Startup, Shutdown, or Maintenance of units controlled by Flares (Blowdown/Venting, Amine Unit-Acid Gas Injection well maintenance) | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | NOx, CO, PM10, PM2.5, SO2 controlled through Good Combustion Practices (GCP), pipeline quality natural gas for pilot; limits on flaring events. VOC & CO2e controlled through GCP, limits on flaring and meet 40 CFR 60.18. | 2558.4 | PPH |  | BACT-PSD | NSPS , SIP , OPERATING PERMIT | U | 98 | U | 7.8 | PPH |  | 0 |  |  | 0 | 0 | N
TX-0812 | CRUDE OIL PROCESSING FACILITY | GRAVITY MIDSTREAM CORPUS CHRISTI LLC | NUECES | TX |  | USA | ANTONIO MARTINEZ | 361-537-1782 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, 512-239-1284, jesse.lovegren@tceq.texas.gov | 9342A, 9343A, PSDTX963M1, GHGP | 2911 | 324110 | Not Found | 09/23/2016 &nbsp;ACT | 10/31/2016 &nbsp;ACT | 2016-10-06 | 2017-11-16 | D |  | Marine Terminal and Condensate Splitter |  | Refinery Flares | 19.33 |  | 0 |  | Flare used for process turnarounds and upsets only. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | The flare must conform to 40 CFR Â§ 60.18 requirements. Vent stream composition and flow must be continuously monitored to demonstrate compliance. | 0 |  |  | BACT-PSD | NSPS , SIP | N | 98 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Ja, 30 TAC 115, SUBCHAPTER D
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | AMMONIA STORAGE FLARE (EU-016) | 19.39 | NATURAL GAS | 1.1 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.0054 | LB/MMBTU | NORMAL OPERATIONS 3 HR AVG. | BACT-PSD |  | N | 0 |  | 168 | H/12 CONSEC. MONTH | COMPLIANCE DETERMINED AT END OF EA MONTH | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS USED SHALL BE NATURAL GAS LIMIT 4: COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUTDOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ROOT CAUSE ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DUING ANY 2 CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMOCOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | FRONT END FLARE EU-017 | 19.39 | NATURAL GAS | 1.12 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.0054 | LB/MMBTU | NORMAL OPS. 3 HR AVG | BACT-PSD |  | N | 0 |  | 47.26 | LB/H | VENTING OPS. 3 HR AVG. | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS USED SHALL BE NATURAL GAS LIMIT 4: COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUTDOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ROOT CAUSE ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DUING ANY 2 CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMOCOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE. LIMIT 6: SHALL NOT EXCEED 336 HOURS PER TWELVE CONSECUTIVE MONTH PERIOD WITH COMPLIANCE DETERMINED AT THE END OF EACH MONTH.
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | BACK END FLARE (EU-018) | 19.39 | NATURAL GAS | 1.12 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.0054 | LB/MMBTU | NORMAL OPS. 3 HR AVG. | BACT-PSD |  | N | 0 |  | 11.73 | LB/H | VENTING OPS. 3 HR AVG. | 0 |  |  | 0 | 0 | N | 2016 | LIMIT 3: PILOT AND PURGE GAS FUELS USED SHALL BE NATURAL GAS LIMIT 4: COMPLY WITH THE FOLLOWING FLARE MINIMIZATION PRACTICES TO REDUCE EMISSIONS DURING STARTUPS, SHUTDOWNS, AND OTHER FLARING EVENTS: (1) SHALL LIMIT PERIODS WHEN THE BACKUP STORAGE COMPRESSOR AND THE AMMONIA REFRIGERATION COMPRESSOR ARE OFFLINE AT THE SAME TIME TO THE EXTENT PRACTICABLE; (2) TRAIN ALL OPERATORS RESPONSIBLE FOR THE DAY TO DAY OPERATION OF THE FLARES ON THE FLARE MINIMIZATION PRACTICES AND THE SPECIFIC PROCEDURES TO FOLLOW DURING PROCESS STARTUP, SHUT DOWN, AND OTHER FLARING EVENTS; (3) SHALL INVESTIGATE THE &lsquo;&lsquo;ROOT CAUSE&lsquo;&lsquo; OF MALFUNCTION EVENTS THAT CAUSE FLARING EVENTS OTHER THAN AT STARTUP OR SHUT DOWN. THIS ROOT CAUSE ANALYSIS SHALL IDENTIFY THE APPARENT CAUSE OF UNANTICIPATED FLARING EVENT AND SHALL RECOMMEND ADDITIONAL PREVENTIVE MEASURES THAT WILL MINIMIZE THE CHANCE OF A REPEAT EVENT. LIMIT 5: FLARES SHALL BE DESIGNED FOR AND OPERATED WITH NO VES, EXCEPT FOR PERIODS NOT TO EXCEED 5 MIN DUING ANY 2 CONSEC. HOURS; SHALL BE OPERATED WITH A FLAME PRESENT AT ALL TIMES; SHALL BE CONTINUOUSLY MONITORED TO ASSURE THE PRESENCE OF A PILOT FLAME WITH A THERMOCOUPLE, INFRARED MONITOR, OR OTHER APPROVED DEVICE. LIMIT 6: SHALL NOT EXCEED 336 HOURS PER 12 CONSECUTIVE MONTH PERIOD WITH COMPLIANCE DETERMINED AT END OF EACH MONTH.
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | flares | 19.39 | natural gas | 7.33 | kg/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Flare | 19.39 | natural gas | 0 |  | Ground flare is pressure-assisted. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Designed for 99% DRE for less than C3 and 99% control for C3+ compounds | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | EMERGENCY GENERATOR SN-62 | 19.8 | DIESEL | 625 | HP |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD OPERATING PRACTICES, LIMITED HOURS OF OPERATION, COMPLIANCE WITH NSPS SUBPART IIII | 19 | G/KW-H |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | wastewater treatment system | 22.2 |  | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Complying with 40 CFR 63 Subpart XX | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MN-0076 | BLANDIN PAPER/RAPIDS ENERGY CENTER | BLANDIN PAPER COMPANY/MINNESOTA POWER | ITASCA | MN | 55744 | USA | NATHAN WAECH | 2183276269 |  | 5 | MN001 | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | MR. RICHARD CORDES | (651)757-2291 | RICHARD.CORDES@STATE.MN.US |  | 06100001-011 | 2621 | 322110 | 110000426290 | 08/16/2007 &nbsp;ACT | 09/18/2008 &nbsp;ACT | 2008-12-01 | 2009-02-10 | B |  | BLANDIN PAPER PRODUCES PAPER FOR ADVERTISING SUPPLEMENTS, CATALOGS, AND MAGAZINES. |  | PRESSURIZED GROUNDWOOD MILL | 30.49 |  |  |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | REGENERATIVE THERMAL OXIDIZER | 0.081 | LB/T BONE DRY PULP | CONTINUOUS | BACT-PSD |  | Y | 83 | U | 217150 | T/YR BONE DRY PULP | 365 DAY ROLLING SUM | 0 |  |  | 0 | 0 | N |  | EXISTING UNIT, BACT DETERMINED TO BE EXISTING SITUATION OF PARTIAL CAPTURE EFFICIENCY, FOR COMBINED CAPTURE/CONTROL OF 83%
MN-0076 | BLANDIN PAPER/RAPIDS ENERGY CENTER | BLANDIN PAPER COMPANY/MINNESOTA POWER | ITASCA | MN | 55744 | USA | NATHAN WAECH | 2183276269 |  | 5 | MN001 | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | MR. RICHARD CORDES | (651)757-2291 | RICHARD.CORDES@STATE.MN.US |  | 06100001-011 | 2621 | 322110 | 110000426290 | 08/16/2007 &nbsp;ACT | 09/18/2008 &nbsp;ACT | 2008-12-01 | 2009-02-10 | B |  | BLANDIN PAPER PRODUCES PAPER FOR ADVERTISING SUPPLEMENTS, CATALOGS, AND MAGAZINES. |  | THERMOMECHANICAL PULP MILL | 30.49 |  |  |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | REGENERATIVE THERMAL OXIDIZER | 0.021 | LB/T BONE-DRY PULP | CONTINUOUS | BACT-PSD |  | Y | 67 | U | 0 |  |  | 0 |  |  | 5600 | 0 | N |  | BASED ON 70% CAPTURE, 95% DESTRUCTION. COST TO INCREASE TO 100% CAPTURE IS $31000/TON.
TX-0731 | CORPUS CHRISTI TERMINAL CONDENSATE SPLITTER | MAGELLAN PROCESSING LP | NUECES | TX |  | USA | SHAHANA BANOO | 918-574-7767 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, 512-239-1284, jesse.lovegren@tceq.texas.gov | 118270 AND PSDTX1398 | 2911 | 324110 | 110017840782 | 02/19/2015 &nbsp;ACT | 04/10/2015 &nbsp;ACT | 2015-04-14 | 2016-05-16 | B |  | 100 MBpd topping refinery |  | Petroleum Liquid Marketing | 42.004 |  | 20000 | Bbl/hr/vessel | Loading of crude oil/condensate and petroleum liquids into marine vessels (ships and barges). Loading of LPG into pressurized trucks. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | BACT for control of VOC emissions from marine vessel loading operations is use of bottom or submerged fill for products with VOC vapor pressure of less than 0.5 psia. For loading of products with VOC vapor pressure of 0.5 psia or greater, BACT is loading under vacuum (non-inerted vessels), loading into MACT Y vapor-tight vessels (inerted vessels), and use of a vapor combustor with a guaranteed DRE of 99.5%. BACT for VOC emissions from hose disconnects is isolation of the line or hose; draining the line/hose either into the receiving vessel or a sump; and capping, plugging or blinding the line/hose after it has been drained. For LPG truck loading, limit the total isolated volume of connectors that may be vented during hose disconnects. LPG truck connectors must vent no more than 650 cubic centimeters of vapor to the atmosphere on being disconnected. | 0 |  |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Unleaded Gasoline Tank TK-33 | 42.005 |  | 1000 | gallons |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Submerged fill pipe and LAC 33:III.2103 | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0731 | CORPUS CHRISTI TERMINAL CONDENSATE SPLITTER | MAGELLAN PROCESSING LP | NUECES | TX |  | USA | SHAHANA BANOO | 918-574-7767 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, 512-239-1284, jesse.lovegren@tceq.texas.gov | 118270 AND PSDTX1398 | 2911 | 324110 | 110017840782 | 02/19/2015 &nbsp;ACT | 04/10/2015 &nbsp;ACT | 2015-04-14 | 2016-05-16 | B |  | 100 MBpd topping refinery |  | Petroleum Liquids Storage in Fixed Roof Tanks | 42.005 |  | 3.4 | MMBbl/yr/tank | (4) Heated atmospheric residuum (â€œresidâ€) tanks | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Temperature reduced to maintain volatile organic compound (VOC) vapor pressure < 0.5 pounds per square inch actual (psia) at all times. | 15.78 | TONS/YR/TANK |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0813 | ODESSA PETROCHEMICAL PLANT | REXTAC, LLC | ECTOR | TX |  | USA | STEVE MCHANEY | 432-332-0058 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, 512-239-1541, joseph.janecka@tceq.texas.gov | 16963, PSDTX1478, GHGPSDTX148 | 2821 | 325211 | Not Found | 09/23/2016 &nbsp;ACT | 11/22/2016 &nbsp;ACT | 2016-11-30 | 2017-11-16 | D |  | Petrochemical Manufacturing Facility |  | Petroleum Liquid Storage in Fixed Roof tanks | 42.005 |  | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Submerged fill pipe, reflective or white exterior paint. | 0.01 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Xylene, spent xylene, and isopropyl alcohol tanks
TX-0731 | CORPUS CHRISTI TERMINAL CONDENSATE SPLITTER | MAGELLAN PROCESSING LP | NUECES | TX |  | USA | SHAHANA BANOO | 918-574-7767 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, 512-239-1284, jesse.lovegren@tceq.texas.gov | 118270 AND PSDTX1398 | 2911 | 324110 | 110017840782 | 02/19/2015 &nbsp;ACT | 04/10/2015 &nbsp;ACT | 2015-04-14 | 2016-05-16 | B |  | 100 MBpd topping refinery |  | Petroleum Liquids Storage in Floating Roof Tanks | 42.006 |  | 8 | MMBbl/yr/tank | (19) internal floating roof tanks for storage of crude oil/condensate, light naphtha, heavy naphtha, jet fuel and distillate. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Required floating roof with welded deck seams if the tank will store products with VOC vapor pressure of 0.5 psia or greater. Proper fitting and seal integrity for the floating roof is ensured through visual inspections and any seal gap measurements specified in 40 CFR Â§ 60.113b. The vapor space under the floating roof must be routed to a control device during standing idle periods until the vapor space VOC concentration is 10,000 ppmv or less. The tank roof must be landed on its lowest legs unless tank entry is planned. Refilling must also be controlled if the product stored has a VOC vapor pressure of 0.5 psia or greater. | 5.09 | TONS/YR/TANK |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0812 | CRUDE OIL PROCESSING FACILITY | GRAVITY MIDSTREAM CORPUS CHRISTI LLC | NUECES | TX |  | USA | ANTONIO MARTINEZ | 361-537-1782 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, 512-239-1284, jesse.lovegren@tceq.texas.gov | 9342A, 9343A, PSDTX963M1, GHGP | 2911 | 324110 | Not Found | 09/23/2016 &nbsp;ACT | 10/31/2016 &nbsp;ACT | 2016-10-06 | 2017-11-16 | D |  | Marine Terminal and Condensate Splitter |  | Petroleum Liquid Storage in Floating Roof tanks | 42.006 |  | 0 |  | (26) internal floating roof tanks with capacity of 125 MBbl/each in petroleum liquid service | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Internal floating roof. Integrity of the floating roof seal must be verified through periodic visual inspections and seal gap measurements. The tank must be constructed with a drain dry sump, and an available connection to a control device. | 3.04 | T/YR | PER TANK | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Kb
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Urea UF-85 Storage Tank | 42.009 |  | 30440 | gallons | Urea UF-85 Storage Tank. 30,440 gallon capacity | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Wet Scrubber | 0 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Two (2) Methyl-diethanol Amine (MDEA) Storage Tanks | 42.009 |  | 158420 | gallons | Two (2) MDEA Storage Tanks with rated capacities of 158,420 gallons and 16,000 gallons. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Submerged Fill Design | 0.002 | TONS/YEAR | COMBINED | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | TWO (2) UAN STORAGE TANKS | 42.009 |  | 30000 | TONS UAN, EACH |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | WHITE TANK SHELLS, USE SUBMERGED FILL. | 0 |  |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | THREE (3) UAN DAY TANKS | 42.009 |  | 750 | TONS UAN, EACH |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | WHITE TANK SHELLS, SUBMERGED FILL | 0 |  |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | ONE (1) DIESEL EXHAUST FLUID (DEF) TANK | 42.009 |  | 100 | TONS UAN |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | WHITE TANK SHELL, SUBMERGED FILL | 0 |  |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Storage Tank, crude methanol storage | 42.009 | crude methanol | 1470000 | GAL | 1,470,000-gallon crude methanol tank with fixed roof venting to a water scrubber | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Water scrubber | 0 |  |  | BACT-PSD | NSPS | U | 98 | N | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 1,470,000-gallon crude methanol tank with fixed roof venting to a water scrubber
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Storage Tanks, 2 - methanol day tanks | 42.009 | methanol | 2940000 | GAL, EACH | Two 2,940,000-gallon methanol day tanks with internal floating roofs | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Internal floating roof, white or aluminum surface | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Two 2,940,000-gallon methanol day tanks with internal floating roofs
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Storage Tanks, 4 - MTG product gasoline tanks | 42.009 | Gasoline | 8400000 | GAL, EACH | Four 8,400,000-gallon MTG product gasoline tanks with internal floating roofs | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | internal floating roof, white or aluminum surface | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Four 8,400,000-gallon MTG product gasoline tanks with internal floating roofs
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Starage Tanks, 2 - gasoline day tanks | 42.009 | Gasoline | 630000 | GAL, each | Two 630,000-gallon MTG gasoline day tanks with internal floating roofs | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | internal floating roof, white or aluminum surface | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Storage Tank, MTG Heavy Gasoline | 42.009 | MTG heavy gasoline | 714000 | GAL | One 714,000-gallon MTG heavy gasoline day tank with internal floating roof | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | internal floating roof, white or aluminum surface | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | LIQUID UAN LOADOUT | 42.01 |  | 1314000 | TONS UAN PER YEAR |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | SUBMERGED FILL AND CLEAN CARGO CARRIER OPERATION | 0 |  |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | ONE (1) DIESEL EXHAUST FLUID (DEF) TRUCK LOADOUT | 42.01 |  | 1314000 | TONS UAN PER YEAR |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | USE OF SUBMERGED FILL | 0 |  |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Steam Methane Reformer | 50.002 | NATURAL GAS | 10 | MMSCFH | Steam Methane Reformer, equipped with low NOx burners, SCR, and CO oxidation catalyst | Volatile Organic Compounds (VOC) | Other - CEMS | (Volatile Organic Compounds (VOC)) | VOC | N |  | 5 | PPMV @ 3% O2 | 3-HR ROLLING AVG | BACT-PSD |  | U | 0 | U | 21.5 | LB/H | 3-HR ROLLING AVG | 0 |  |  | 0 | 0 | N |  | Steam Methane Reformer, equipped with low NOx burners, SCR, and CO oxidation catalyst
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Process fugitives | 50.002 |  | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | LDAR for all equipment in VOC service, equivalent to NSPS VVa | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0678 | FREEPORT LNG PRETREATMENT FACILITY | FREEPORT LNG DEVELOPMENT LP | BRAZORIA | TX |  | USA | RUBEN VELASQUEZ | (512) 342-3395 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 104840 N170 PSDTX1302 | 1321 | 211112 | 110027375105 | 07/20/2012 &nbsp;ACT | 07/16/2014 &nbsp;ACT | 2015-03-13 | 2016-05-09 | A |  | In support of the proposed Liquefaction Plant pending TCEQ review under Air Quality Permit Nos. 100114, PSDTX1282, and N150, Freeport LNG plans to construct a natural gas Pretreatment Facility to purify pipeline quality natural gas to be sent to the Liquefaction Plant for the production of LNG. The Pretreatment Facility will be located approximately 3.5 miles inland to the northeast of the Quintana Island Terminal along Freeport LNGâ€™s existing 42-inch natural gas pipeline route. Pipeline quality natural gas will be delivered from interconnecting intrastate pipeline systems through Freeport LNG Developmentâ€™s existing Stratton Ridge meter station. The gas will be pretreated in the Pretreatment Facility to remove carbon dioxide, sulfur compounds, water, mercury, BTEX, and natural gas liquids. The pre-treated natural gas will then be delivered to the Liquefaction Plant through Freeport LNGâ€™s existing 42-inch gas pipeline. |  | Thermal Oxidizer | 50.002 | natural gas | 0 |  | There are 3 LNG trains and each train has a thermal oxidizer. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | 99% DRE of acid gas VOC | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT is a DRE.
TX-0812 | CRUDE OIL PROCESSING FACILITY | GRAVITY MIDSTREAM CORPUS CHRISTI LLC | NUECES | TX |  | USA | ANTONIO MARTINEZ | 361-537-1782 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, 512-239-1284, jesse.lovegren@tceq.texas.gov | 9342A, 9343A, PSDTX963M1, GHGP | 2911 | 324110 | Not Found | 09/23/2016 &nbsp;ACT | 10/31/2016 &nbsp;ACT | 2016-10-06 | 2017-11-16 | D |  | Marine Terminal and Condensate Splitter |  | Transfer Operations | 50.004 |  | 80 | MM BBL / YR | Tanker ship dock for loading of crude oil and refinery products | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | B | If the product loaded has a VOC vapor pressure in excess of 0.50 psia, all displaced loading vapors must be captured and directed to a vapor combustor with a destruction/removal efficiency (DRE) of 99.5% or greater. For non-inerted ships (inland barges), capture system integrity is ensured by loading under vacuum. For inerted vessels (oceangoing tankers and barges), the ship must possess a recent vapor tightness certification prior to start of loading. | 0 |  |  | BACT-PSD |  | N | 99.5 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0731 | CORPUS CHRISTI TERMINAL CONDENSATE SPLITTER | MAGELLAN PROCESSING LP | NUECES | TX |  | USA | SHAHANA BANOO | 918-574-7767 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, 512-239-1284, jesse.lovegren@tceq.texas.gov | 118270 AND PSDTX1398 | 2911 | 324110 | 110017840782 | 02/19/2015 &nbsp;ACT | 04/10/2015 &nbsp;ACT | 2015-04-14 | 2016-05-16 | B |  | 100 MBpd topping refinery |  | Petroleum Refining Separation Processes | 50.005 | natural gas | 100000 | Bbl/day | throughout based on total processing capacity | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | No direct emissions to atmosphere from process vents. | 0 |  |  | BACT-PSD | MACT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0812 | CRUDE OIL PROCESSING FACILITY | GRAVITY MIDSTREAM CORPUS CHRISTI LLC | NUECES | TX |  | USA | ANTONIO MARTINEZ | 361-537-1782 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, 512-239-1284, jesse.lovegren@tceq.texas.gov | 9342A, 9343A, PSDTX963M1, GHGP | 2911 | 324110 | Not Found | 09/23/2016 &nbsp;ACT | 10/31/2016 &nbsp;ACT | 2016-10-06 | 2017-11-16 | D |  | Marine Terminal and Condensate Splitter |  | Petroleum Refining Separation Processes | 50.005 |  | 35000 | BBL/DAY | Flexible processing unit which may function either as a Condensate Splitter (atmospheric pressure) or a vacuum distillation unit. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Continuous flaring of distillation unit overheads must be discontinued following start of operation of the condensate splitter (including gas plant). All process vents or pressure relief devices (including steam ejectors and intermittent process vents) must be directed to a flare meeting 40 CFR Â§60.18 requirements. | 0 |  |  | BACT-PSD | NSPS , SIP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Ja, 30 TAC 115, SUBCHAPTER D
TX-0731 | CORPUS CHRISTI TERMINAL CONDENSATE SPLITTER | MAGELLAN PROCESSING LP | NUECES | TX |  | USA | SHAHANA BANOO | 918-574-7767 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, 512-239-1284, jesse.lovegren@tceq.texas.gov | 118270 AND PSDTX1398 | 2911 | 324110 | 110017840782 | 02/19/2015 &nbsp;ACT | 04/10/2015 &nbsp;ACT | 2015-04-14 | 2016-05-16 | B |  | 100 MBpd topping refinery |  | , Petroleum Refining Equipment Leaks/Fugitive Emissions | 50.007 |  | 100000 | Bbl/day | throughput based on total processing capacity | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Quarterly instrumental monitoring using a method 21 gas analyzer for all valves, pump seals, compressor seals, and agitator seals with a leak definition of 500 parts per million volume (ppmv) for valves and 2,000 ppmv for pump, compressor and agitator seals. Leaking components must be repaired within 15 days of detection of the leak. | 36.6 | TPY |  | BACT-PSD | NSPS , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0812 | CRUDE OIL PROCESSING FACILITY | GRAVITY MIDSTREAM CORPUS CHRISTI LLC | NUECES | TX |  | USA | ANTONIO MARTINEZ | 361-537-1782 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, 512-239-1284, jesse.lovegren@tceq.texas.gov | 9342A, 9343A, PSDTX963M1, GHGP | 2911 | 324110 | Not Found | 09/23/2016 &nbsp;ACT | 10/31/2016 &nbsp;ACT | 2016-10-06 | 2017-11-16 | D |  | Marine Terminal and Condensate Splitter |  | Equipment Leaks | 50.007 |  | 0 |  |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 21 | (Volatile Organic Compounds (VOC)) | VOC | P | Quarterly instrumental monitoring of accessible pumps, compressors and valves in vapor or light liquid service, with leak definitions of 500 ppmv (valves) and 2,000 ppmv (pump and compressor seals). Upon detection of a leak, a first attempt to repair must be made within 5 days, and repairs must be completed within 15 days. | 8.72 | T/YR |  | BACT-PSD | NSPS , SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS GGG, GGGa, 30 TAC 115, SUBCHAPTER D
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | Thermal oxidizers (2 units) | 50.008 | natural gas | 21 | mm btu/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0731 | CORPUS CHRISTI TERMINAL CONDENSATE SPLITTER | MAGELLAN PROCESSING LP | NUECES | TX |  | USA | SHAHANA BANOO | 918-574-7767 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, 512-239-1284, jesse.lovegren@tceq.texas.gov | 118270 AND PSDTX1398 | 2911 | 324110 | 110017840782 | 02/19/2015 &nbsp;ACT | 04/10/2015 &nbsp;ACT | 2015-04-14 | 2016-05-16 | B |  | 100 MBpd topping refinery |  | Petroleum Refining Wastewater and Wastewater Treatment | 50.009 |  | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Process wastewater shall be immediately directed to a covered system. All lift stations, manholes, junction boxes, conveyances, and any other wastewater facilities shall be covered and all emissions routed to a vapor combustor with a guaranteed DRE of 99% for control. | 0.4 | TPY |  | BACT-PSD | NSPS , MACT | N | 99 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Two (2) Urea Granulation Units | 61.012 |  | 1200 | T/D | Two (2) Urea Granulation Units rated at 1200 tons per day (each). | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Wet Scrubber | 90 | % CONTROL METHANOL | WHICHEVER IS LESS RESTRICTIVE | BACT-PSD |  | U | 0 | U | 2 | PPMV | WHICHEVER IS LESS RESTRICTIVE | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT PRIMARY REFORMER | 61.012 | NATURAL GAS | 1400 | T/D AMMONIA | 824 MMBTU/HR | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD AND EFFICIENT COMBUSTION PRACTICES | 1.15 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 5.05 | T/YR | ROLLING 12 MONTH AVERAGE | 0.0014 | LB/MMBTU | ROLLING 3 HOUR AVERAGE | 0 | 0 | N |  | PERIODIC STACK TESTING TO VERIFY COMPLIANCE
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT CO2 REGENERATOR | 61.012 |  | 1400 | T/D AMMONIA PRODUCTION |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD AND EFFICIENT OPERATING PRACTICES | 33.64 | LB/H | ROLLING 3 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 147.35 | T/YR | ROLLING 12 MONTH AVERAGE | 0.106 | LB/TON | ROLLING 3 HOUR AVERAGE | 0 | 0 | N |  | PERIODIC STACK TESTING TO VERIFY COMPLIANCE
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Primary Reformer | 61.012 | natural gas | 1.13 | million cubic feet/h |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0.0014 | LB/MMBTU | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 6.95 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | CO2 Regenerator | 61.012 |  | 3012 | metric tons/day |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | good operational practices | 0.106 | LB/TON OF AMMONIA | AVERAGE OF 3 STACK TEST RUNS | BACT-PSD |  | U | 0 | U | 51.2 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Ammonia Plant, Flares | 61.012 | natural gas | 2789 | tpd |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Flare | 11.6 | TPY |  | BACT-PSD |  | U | 98 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Reformer Furnace | 61.012 | natural gas | 955 | MMBTU/H |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices | 0.0054 | LB/MMBTU | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Ammonia Plant, CO2 Vents | 61.012 | natural gas | 2789 | tpd |  | Volatile Organic Compounds (VOC) | Other - sampling and analysis of process gas streams | (Volatile Organic Compounds (VOC)) | VOC | N |  | 13.1 | LB/H | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Ammonia Pressure Tanks | 61.012 |  | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Flare; flare minimization | 0.21 | TPY |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Urea Plant | 61.012 |  | 4880 | tpd | while the urea granulator in the urea plant is the principal emitter, there are other units that contribute. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | use of urea formaldehyde is specified as a required constituent of the product | 0.36 | LB/H | 3-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Components (valves, flanges, etc.) | 61.012 |  | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | LDAR; &lsquo;&lsquo;leakless&lsquo;&lsquo; component | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | PRIMARY REFORMER | 61.012 | NATURAL GAS | 1006.4 | MMBTU/H | NOX CEMS | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES | 5.51 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | CO2 PURIFICATION PROCESS | 61.012 |  | 3570 | TON CO2 PER DAY | AMMONIA PRODUCTION LIMITED TO 1,022,000 TONS PER YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | LOW VOC CATALYST | 0.0558 | LB/TON AMMONIA | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0121 | EL DORADO CHEMICAL COMPANY | LSB INDUSTRIES, INC. | UNION | AR | 71730 | USA | GREG WITHROW | 8708631484 | GWITHROW@EDC-ARK.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us | THOMAS RHEAUME, PERMIT BRANCH MANAGER JOSEPH HURT, ENGINEER | 0573-AOP-R16 | 2873 | 325311 | 110000746373 | 01/31/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2015-08-12 | 2016-06-17 | B | HTTP://WWW.ADEQ.STATE.AR.US/FTPROOT/PUB/WEBDATABASES/PERMITSONLINE/AIR/0573-AOP-R16.PDF | CHEMICAL MANUFACTURING, INCLUDING NITRIC ACID PRODUCTION, SUFLURIC ACID PRODUCTION, AMMONIA PRODUCTION, AND AMMONIA NITRATE PRODUCTION |  | AMMONIA PLANT CONDENSATE STEAM STRIPPER | 61.999 |  | 1400 | T/D AMMONIA PRODUCTION |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD AND EFFICIENT OPERATING PRACTICES | 5.83 | LB/H | ROLLING 24 HOUR AVERAGE | BACT-PSD | SIP | N | 0 | N | 25.55 | T/YR | ROLLING 12 MONTH AVERAGE | 0.1 | LB/TON | ROLLING 24 HOUR AVERAGE | 0 | 0 | N |  | PERIODIC STACK TESTING TO VERIFY COMPLIANCE
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | MDEA storage tank | 61.999 |  | 0 |  | The storage tank capacity is 390,000 gallons | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | A | Nitrogen gas blanket | 0.1 | TONS/YR | ROLLING 12 MONTH TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | TWO (2) NITRIC ACID STORAGE TANKS | 62.014 |  | 806842 | TONS OF 57% ACID PER YEAR. | PERMIT LIMITS NITRIC ACID THROUGHPUT TO 806,842 TONS OF 57% ACID PER YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | SUBMERGED FILL | 0.0015 | LB NOX/TON 57% ACID | 3-HR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Ammonia Plant, CO2 Vent | 62.999 | Natural Gas | 1800 | T/D | The CO2 vent, vents excess CO2 from ammonia process. During times when ammonia plant is operating and Urea plant is not operating, all CO2 generated by ammonia plant operations is vented through this vent. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 11.4 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0179 | OHIO VALLEY RESOURCES, LLC | OHIO VALLEY RESOURCES, LLC | SPENCER | IN | 47635 | USA | DOUG WILSON | 6185990015 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV | 147-32322-00062 | 2873 | 325311 | 110055148273 | 09/17/2012 &nbsp;ACT | 09/25/2013 &nbsp;ACT | 2014-08-12 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32322F.PDF | NITROGENOUS FERTILIZER PRODUCTION PLANT |  | FUGITIVE VOC EMISSIONS | 64.002 |  | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | USE OF A LEAK DETECTION AND REPAIR (LDAR) PROGRAM USING 40 CFR 60, SUBPART VVA PROCEDURES. | 0 |  |  | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0307 | MAGNOLIA LNG FACILITY | MAGNOLIA LNG, LLC | CALCASIEU | LA | 70669 | USA | KOMI HASSAN | 713-815-6900 | KHASSAN@MAGNOLIALNG.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Dan Nguyen - (225)219-3395 | PSD-LA-792 | 4922 | 221210 | 110069422958 | 11/15/2015 &nbsp;ACT | 03/21/2016 &nbsp;ACT | 2017-03-08 | 2017-04-28 | A |  | A new facility to liquefy 8.0 million metric tons per year of natural gas |  | fugitives | 64.002 |  | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Comply with LAC 33:III.2111 | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Fugitive Emissions | 64.002 |  | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | proper piping design, complying with LAC 33:III.2111, and conduct an LDAR meeting requirements of 40 CFR 63 Subpart UU | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0813 | ODESSA PETROCHEMICAL PLANT | REXTAC, LLC | ECTOR | TX |  | USA | STEVE MCHANEY | 432-332-0058 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, 512-239-1541, joseph.janecka@tceq.texas.gov | 16963, PSDTX1478, GHGPSDTX148 | 2821 | 325211 | Not Found | 09/23/2016 &nbsp;ACT | 11/22/2016 &nbsp;ACT | 2016-11-30 | 2017-11-16 | D |  | Petrochemical Manufacturing Facility |  | FUGITIVES | 64.002 |  | 0 |  | Includes fugitive components leaks in VOC service for utilities, flare, propylene fractionation, and loading areas. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 21 | (Volatile Organic Compounds (VOC)) | VOC | P | Quarterly instrumental monitoring of accessible pumps, compressors and valves in vapor or light liquid service, with leak definitions of 500 ppmv (valves) and 2,000 ppmv (pump and compressor seals). Upon detection of a leak, a first attempt to repair must be made within 5 days, and repairs must be completed within 15 days. | 88.52 | T/YR |  | BACT-PSD | NSPS | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS DDD
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Modular Ethylene Cracking Furnaces - 001 | 64.003 | natural gas/fuel gas | 1028 | MM BTU/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices and proper operation and maintenance | 0.0054 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Ethylene Cracking Furnace - 015 | 64.003 | natural gas/fuel gas | 168 | mm btu |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | good combustion practices and proper operation and maintenance | 0.0054 | LB/MM BTU | THREE ONE-HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0813 | ODESSA PETROCHEMICAL PLANT | REXTAC, LLC | ECTOR | TX |  | USA | STEVE MCHANEY | 432-332-0058 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, 512-239-1541, joseph.janecka@tceq.texas.gov | 16963, PSDTX1478, GHGPSDTX148 | 2821 | 325211 | Not Found | 09/23/2016 &nbsp;ACT | 11/22/2016 &nbsp;ACT | 2016-11-30 | 2017-11-16 | D |  | Petrochemical Manufacturing Facility |  | Polypropylene Process Vents | 64.003 |  | 437.5 | MM LB / YR | POLYPROPYLENE | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Emissions minimized by limited venting, and waste stream controlled by flare. The flare must conform to 40 CFR Â§ 60.18 requirements. Vent stream composition and flow must be continuously monitored to demonstrate compliance. | 0 |  |  | BACT-PSD | NSPS | N | 98 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS DDD
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | oil tank FA-712 - 012 | 64.004 |  | 66150 | gal |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | IFR with liquid mounted seal, double seal, or mechanical seal | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | storm water surge tank TK-9 - 013 | 64.004 |  | 291410 | gallons |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | fixed roof | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | process water storage tanks TK-301A/B - 017 | 64.004 |  | 350000 | gallons |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | EFR with primary and secondary seal, submerged fill pipe, and complying with 40 CFR 63 Subpart WW | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | Methanol Tank TK-2 | 64.004 |  | 1469 | gallons |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Submerged fill pipe and LAC 33:III.2103 | 0 |  |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | pyrolysis gasoline tank V-410 | 64.004 |  | 946996 | gallons |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Closed vent system and routed to a flare, Complying with 40 CFR 60 Subpart Kb and LAC 33:III.2103 | 0 |  |  | BACT-PSD | NSPS | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0813 | ODESSA PETROCHEMICAL PLANT | REXTAC, LLC | ECTOR | TX |  | USA | STEVE MCHANEY | 432-332-0058 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Joseph A. Janecka, 512-239-1541, joseph.janecka@tceq.texas.gov | 16963, PSDTX1478, GHGPSDTX148 | 2821 | 325211 | Not Found | 09/23/2016 &nbsp;ACT | 11/22/2016 &nbsp;ACT | 2016-11-30 | 2017-11-16 | D |  | Petrochemical Manufacturing Facility |  | Liquid VOC Laoding | 64.005 |  | 6000 | gal/hr |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | Regenerative thermal oxidizer | 0 |  |  | BACT-PSD |  | N | 99 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*NE-0059 | AGP SOY | AG PROCESSING INC., A COOPERATIVE | ADAMS | NE | 68901 | USA |  |  |  | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | CP14-007 | 2075 | 311225 |  | 12/19/2014 &nbsp;ACT | 03/25/2015 &nbsp;ACT | 2015-08-18 | 2015-08-18 | B |  | Soybean Processing Facility | Permit is currently being contested. | Soybean Extraction Process | 70.35 |  | 85000 | bushel/day |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Mineral Oil Absorber. During SSM the source must comply with 40 CFR 63.2852 as amended April 20, 2006 | 381.26 | TON/YR | 12-MONTH ROLLING TOTAL | BACT-PSD | NESHAP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | LMFS SN-01 AND SN-02 | 81.29 | NATURAL GAS | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | SCRAP MANAGEMENT PLAN AND GOOD PORATION PRACTICES | 0.005 | LB/TON |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | RH DEGASSER | 81.29 | NATURAL GAS | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.0054 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-39, ANNEALING | 81.29 | NATURAL GAS | 98.25 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.0054 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | ANNEALING COATING LINE FURNACE SECTION | 81.29 | NATURAL GAS | 50 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | RTO | 0.0054 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | EMISSION LIMIT 1 FOR NATURAL GAS COMBUSTION ONLY.
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACE, SN-53, ANNEALING COATING LINE DRYING | 81.29 | NATURAL GAS | 38 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | RTO | 0.0054 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | DRYERS, MGO COATING LINE | 81.29 | NATURAL GAS | 38 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.0054 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0140 | BIG RIVER STEEL LLC | BIG RIVER STEEL LLC | MISSISSIPPI | AR | 72370 | USA | DAVID STICKLER | 3309080813 |  | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2305-AOP-R0 | 3312 | 331111 | 110067436625 | 03/14/2013 &nbsp;ACT | 09/18/2013 &nbsp;ACT | 2016-11-09 | 2016-12-13 | A | HTTP: | THE FACILITY WILL CONSIST OF TWO ELECTRIC ARC FURNACES TO MELT SCRAP IRON AND STEEL, LADLE METALLURGY FURNACES (LMF) TO ADJUST THE CHEMISTRY, A RH DEGASSER AND BOILER FOR FURTHER REFINEMENT, AND CASTERS. |  | FURNACES SN-58 AND 60, FINAL ANNEALING AND COATING LINE | 81.29 | NATURAL GAS | 32 | MMBTU/H |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | COMBUSTION OF NATURAL GAS AND GOOD COMBUSTION PRACTICE | 0.0054 | LB/MMBTU |  | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0314 | INDORAMA LAKE CHARLES FACILITY | INDORAMA VENTURES OLEFINS, LLC | CALCASIEU | LA | 70669 | USA | SUSAN WEDEMEYER | 337-476-7451 | SUSAN.WEDEMEYER@US.INDORAMA.NET | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen (225)219-3395 | PSD-LA-813 | 2869 | 325199 | 110000748040 | 04/30/2016 &nbsp;ACT | 08/03/2016 &nbsp;ACT | 2017-03-13 | 2017-04-28 | C |  | modify and restart-up a mothballed facility to produce 1,009 million lbs/yr of ethylene |  | cooling towers - 007 | 99.009 |  | 86500 | gpm |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | monitored as required by 40 CFR 63 subpart XX | 0 |  |  | BACT-PSD | NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MS-0092 | EMBERCLEAR GTL MS | EMBERCLEAR GTL MS LLC | ADAMS | MS | 39120 | USA |  |  |  | 4 | MS001 | MISSISSIPPI DEPT OF ENVIRONMENTAL QUALITY | MS. CARLA BROWN, P.E. | (601) 961-5235 | cbrown@deq.ms.gov |  | 0040-00055 | 2869 | 325110 | 110066860123 | 11/18/2013 &nbsp;ACT | 05/08/2014 &nbsp;ACT | 2015-01-15 | 2016-11-07 | A | http://opc.deq.state.ms.us/ai_info.aspx?ai=64314 | Proposed gas-to-liquids (GTL) plant, processing pipeline natural gas into gasoline and LPG through a series of reforming processes, including a Steam Methane Reformer (SMR) and an Auto Thermal Reformer (ATR) |  | Cooling tower, Induced draft | 99.009 |  | 1420 | GAL/MIN |  | Volatile Organic Compounds (VOC) | Other - Water test method | (Volatile Organic Compounds (VOC)) | VOC | P | Monthly strippable VOC monitoring (modified El Paso Method) | 0.7 | LB VOC/MMGAL WATER | 12-MONTH ROLLING AVG | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
GA-0127 | PLANT MCDONOUGH COMBINED CYCLE | SOUTHERN COMPANY/GEORGIA POWER | COBB | GA | 30080 | USA |  |  |  | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us | JOHN YNTEMA 404-363-7117 JOHN.YNTEMA@DNR.STATE.GA.US | 4911-067-0003-V-02-2 | 4911 | 221112 | 110000355972 | 03/08/2007 &nbsp;ACT | 01/07/2008 &nbsp;ACT | 2008-06-17 | 2008-10-09 | B |  | THREE NATURAL GAS FIRED COMBINED CYCLE POWER BLOCKS. EACH BLOCK CONSISTS OF TWO COMBUSTION TURBINES, TWO HEAT RECOVERY STEAM GENERATORS WITH DUCT BURNERS AND A STEAM TURBINE. TWO TURBINES WILL BE CAPABLE OF FIRING ULTRA LOW SULFUR DIESEL AS BACKUP FUEL. EACH COMBINED-CYCLE BLOCK WILL HAVE OUTPUT OF 840 MW. TURBINES ARE REPLACING TWO COAL-FIRED UTILITY BOILERS |  | AUXILLARY BOILERS | 12.31 | NATURAL GAS | 200 | MMBTU/H | THREE 200 MMBTU/H BOILERS, EACH LIMITED TO 10% ANNUAL CAPACITY FACTOR | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.0051 | LB/MMBTU | 3-HOUR | LAER |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | 245 MMBtu natural gas fired Auxiliary boiler | 12.31 | Natural Gas | 1052 | MMscf/yr | Total fuel usage of the auxiliary boiler shall not exceed 1052 MMsch/yr on a 12-month rolling basis | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practice | 0.0054 | LB/MMBTU |  | LAER |  | U | 0 | U | 2.89 | TPY |  | 0 |  |  | 0 | 0 | N
TX-0811 | LINEAR ALPHA OLEFINS PLANT | INEOS OLIGOMERS USA LLC | BRAZORIA | TX |  | USA | JOHN WALTER | 281-535-4224 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, PhD, 512-239-1284, jesse.lovegren@tceq.texas.gov | 136130 AND N250 | 2869 | 325110 | Not Found | 09/20/2016 &nbsp;ACT | 11/03/2016 &nbsp;ACT | 2016-10-06 | 2017-11-16 | B |  | Manufactures linear alpha olefins (LAO) from ethylene |  | Industrial-Sized Furnaces, Natural Gas-fired | 12.31 | natural gas | 217 | MM BTU / H | Thermal Fluid (â€œhot oilâ€) Heater, throughput based on higher heating value basis | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 2.15 | T/YR |  | LAER | MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | MACT DDDDD
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | Large Combustion turbine | 15.11 | Natural gas | 0 |  | This process entry is for the VOC emissions of turbine operation without the duct burner. Limit entered is for one turbine | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Ox Cat and good combustion practices | 1.4 | PPMVD @ 15% O2 |  | LAER |  | U | 0 | U | 9.4 | LB/HR |  | 0 |  |  | 0 | 0 | N
GA-0127 | PLANT MCDONOUGH COMBINED CYCLE | SOUTHERN COMPANY/GEORGIA POWER | COBB | GA | 30080 | USA |  |  |  | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us | JOHN YNTEMA 404-363-7117 JOHN.YNTEMA@DNR.STATE.GA.US | 4911-067-0003-V-02-2 | 4911 | 221112 | 110000355972 | 03/08/2007 &nbsp;ACT | 01/07/2008 &nbsp;ACT | 2008-06-17 | 2008-10-09 | B |  | THREE NATURAL GAS FIRED COMBINED CYCLE POWER BLOCKS. EACH BLOCK CONSISTS OF TWO COMBUSTION TURBINES, TWO HEAT RECOVERY STEAM GENERATORS WITH DUCT BURNERS AND A STEAM TURBINE. TWO TURBINES WILL BE CAPABLE OF FIRING ULTRA LOW SULFUR DIESEL AS BACKUP FUEL. EACH COMBINED-CYCLE BLOCK WILL HAVE OUTPUT OF 840 MW. TURBINES ARE REPLACING TWO COAL-FIRED UTILITY BOILERS |  | COMBINED CYCLE COMBUSTION TURBINE | 15.21 | NATURAL GAS | 254 | MW | 6 TURBINES, 254 MW EACH (NOT INCLUDING STEAM RECOVERY), LIMITS ARE FOR EACH TURBINE (MITSUBISHI MODEL M501G). BACKUP FUEL FOR TWO TURBINES IS ULTRA-LOW SULFUR FUEL OIL | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | OXIDATION CATALYST | 1.8 | PPM @ 15% O2 | 3-HOUR, WITH DUCT BURNER | LAER |  | U | 0 | U | 1 | PPM @ 15% O2 | 3-HOUR, WITHOUT DUCT BURNER | 0 |  |  | 0 | 0 | N |  | FUEL OIL HAS ITS OWN LAER LIMITS FOR CO AND VOC
*PA-0306 | TENASKA PA PARTNERS/WESTMORELAND GEN FAC | TENASKA PA PARTNERS LLC | WESTMORELAND | PA |  | USA |  |  |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 65-00990 C/E | 4911 | 221112 | 110059949864 | 11/06/2013 &nbsp;ACT | 02/12/2016 &nbsp;ACT | 2017-06-09 | 2017-07-12 | U |  | The plan approval will allow construction and temporary operation of a power plant is a single 2 on 1 combined cycle turbine configuration with 2 combustion turbines serving a single steam turbine generator equipped with heat recovery steam generator with supplemental 400MMBtu/hr natural gas fired duct burners. The approximate maximum plant nominal generating capacity is 930-1065 MW. Additional facilities will include 245 MMBtu/hr Auxiliary Boiler, one cooling tower, one diesel-fired emergency generator, and one diesel-fired emergency fire pump engine. | Application for plan approval 65-00990E received on 12/10/2015 from Tenaska to reduce the facility wide PTE authorized under plan approval 65-00990C based on revised emission information for startup and shutdown from the manufacturer. | Large combustion turbine | 15.21 | Natural Gas | 0 |  | This process entry is for operations with the duct burner. Limits entered are for each turbine. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | Ox Cat and good combustion practices | 2.4 | PPMDV@15% O2 |  | LAER |  | U | 0 | U | 9.4 | LB/HR |  | 0 |  |  | 0 | 0 | N |  | Limit is for turbine operation with duct burners.
GA-0127 | PLANT MCDONOUGH COMBINED CYCLE | SOUTHERN COMPANY/GEORGIA POWER | COBB | GA | 30080 | USA |  |  |  | 4 | GA001 | GEORGIA DEPARTMENT OF NATURAL RESOURCES | MR. ERIC CORNWELL | (404) 363-7020 | Eric.Cornwell@dnr.state.ga.us | JOHN YNTEMA 404-363-7117 JOHN.YNTEMA@DNR.STATE.GA.US | 4911-067-0003-V-02-2 | 4911 | 221112 | 110000355972 | 03/08/2007 &nbsp;ACT | 01/07/2008 &nbsp;ACT | 2008-06-17 | 2008-10-09 | B |  | THREE NATURAL GAS FIRED COMBINED CYCLE POWER BLOCKS. EACH BLOCK CONSISTS OF TWO COMBUSTION TURBINES, TWO HEAT RECOVERY STEAM GENERATORS WITH DUCT BURNERS AND A STEAM TURBINE. TWO TURBINES WILL BE CAPABLE OF FIRING ULTRA LOW SULFUR DIESEL AS BACKUP FUEL. EACH COMBINED-CYCLE BLOCK WILL HAVE OUTPUT OF 840 MW. TURBINES ARE REPLACING TWO COAL-FIRED UTILITY BOILERS |  | COMBINED CYCLE COMBUSTION TURBINE | 15.29 | NG, WITH FUEL OIL BACKUP | 254 | MW | 6 TURBINES, 254 MW EACH (NOT INCLUDING HEAT RECOVERY), EACH WITH AN OPTIONAL 650MMBTU/HR DUCT BURNER. EMISSION LIMITS WHEN FIRING FUEL OIL. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | OXIDATION CATALYST | 4 | PPM@15% O2 | 3-HOUR, FIRING FUEL OIL | LAER |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0682 | GALENA PARK TERMINAL | KM LIQUIDS TERMINALS LLC | HARRIS | TX |  | USA | NEAL NYGAARD | 832-239-8018 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ozden Tamer Phone: 512-239-4577 e-mail: ozden.tamer@tceq.texas.gov | 101199 & N158 | 4226 | 325110 | 110037844376 | 02/23/2012 &nbsp;ACT | 06/12/2013 &nbsp;ACT | 2015-03-17 | 2016-05-09 | B |  | Tank Terminal | This project is for a new 100,000 barrel per day condensate splitter that takes condensate from a pipeline and separates it into light naphtha, heavy naphtha, kerosene/distillate, residual and Y-grade products which are stored in tanks and loaded in marine vessels at existing docks at this tank terminal. Natural gas used at the facility will be sampled for sulfur every 6 months. | Storage Tanks | 42.009 |  | 0 |  | A combination of IFR tanks, fixed roof tanks and frac tanks wil be used at the facility | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Vapor space degassing will be directed to control until VOC level in the tank is less than 5,000 ppmv (2,000 if vented to atmosphere). | 5000 | PPMV |  | LAER | NSPS , MACT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0811 | LINEAR ALPHA OLEFINS PLANT | INEOS OLIGOMERS USA LLC | BRAZORIA | TX |  | USA | JOHN WALTER | 281-535-4224 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, PhD, 512-239-1284, jesse.lovegren@tceq.texas.gov | 136130 AND N250 | 2869 | 325110 | Not Found | 09/20/2016 &nbsp;ACT | 11/03/2016 &nbsp;ACT | 2016-10-06 | 2017-11-16 | B |  | Manufactures linear alpha olefins (LAO) from ethylene |  | SOCMI Equipment Leaks | 64.002 |  | 0 |  |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 21 | (Volatile Organic Compounds (VOC)) | VOC | P | Quarterly instrumental monitoring of all accessible piping components (pumps, compressors, valves, flanges) in vapor and light liquid service with a leak definition of 500 ppmv VOC. Weekly audio-visual-olfactory monitoring for all components in heavy liquid service. Upon detection of a leak, a first attempt must be made to repair within 5 days, and repairs must be completed within 15 days. | 6.87 | T/YR |  | LAER | SIP , MACT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | MACT FFFF, 30 TAC 115, SUBCHAPTER H
TX-0811 | LINEAR ALPHA OLEFINS PLANT | INEOS OLIGOMERS USA LLC | BRAZORIA | TX |  | USA | JOHN WALTER | 281-535-4224 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, PhD, 512-239-1284, jesse.lovegren@tceq.texas.gov | 136130 AND N250 | 2869 | 325110 | Not Found | 09/20/2016 &nbsp;ACT | 11/03/2016 &nbsp;ACT | 2016-10-06 | 2017-11-16 | B |  | Manufactures linear alpha olefins (LAO) from ethylene |  | Process Vents | 64.003 |  | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | All process vents and pressure relief devices must vent to a control device specified by the permit (flare or thermal oxidizer). No pressure relief device may emit directly to the atmosphere under any circumstance. The capture system must be inspected regularly to verify integrity. | 0.53 | T/YR |  | LAER | NSPS , MACT , SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS NNN, NSPS RRR, MACT FFFF, 30 TAC 115, SUBCHAPTER H
TX-0811 | LINEAR ALPHA OLEFINS PLANT | INEOS OLIGOMERS USA LLC | BRAZORIA | TX |  | USA | JOHN WALTER | 281-535-4224 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, PhD, 512-239-1284, jesse.lovegren@tceq.texas.gov | 136130 AND N250 | 2869 | 325110 | Not Found | 09/20/2016 &nbsp;ACT | 11/03/2016 &nbsp;ACT | 2016-10-06 | 2017-11-16 | B |  | Manufactures linear alpha olefins (LAO) from ethylene |  | SOCMI Floating Roof Storage Tanks | 64.004 |  | 0 |  | (9) Internal Floating Roof tanks in 1-hexene, 1-octene and 1-decene service with capacities of 300â€“450 Mgal | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | A vapor recovery system captures all vapor under tank shell and routes them to a thermal oxidizer. For alpha olefins, product quality considerations dictate the use of a nitrogen blanketing system | 0.01 | T/YR |  | LAER | NSPS | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Kb
TX-0811 | LINEAR ALPHA OLEFINS PLANT | INEOS OLIGOMERS USA LLC | BRAZORIA | TX |  | USA | JOHN WALTER | 281-535-4224 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, PhD, 512-239-1284, jesse.lovegren@tceq.texas.gov | 136130 AND N250 | 2869 | 325110 | Not Found | 09/20/2016 &nbsp;ACT | 11/03/2016 &nbsp;ACT | 2016-10-06 | 2017-11-16 | B |  | Manufactures linear alpha olefins (LAO) from ethylene |  | SOCMI Fixed Roof Storage Tanks | 64.004 |  | 0 |  | (10) fixed roof storage in C12â€“C24 alpha olefin service with capacities of 50â€“160 Mgal. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Fixed roof tanks: no add-on controls. Volatility of stock limited to 0.10 psia by permit condition. For alpha olefins, product quality considerations dictate the use of a nitrogen blanketing system. | 0.17 | T/YR |  | LAER | NSPS | Y | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | NSPS Kb
TX-0682 | GALENA PARK TERMINAL | KM LIQUIDS TERMINALS LLC | HARRIS | TX |  | USA | NEAL NYGAARD | 832-239-8018 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ozden Tamer Phone: 512-239-4577 e-mail: ozden.tamer@tceq.texas.gov | 101199 & N158 | 4226 | 325110 | 110037844376 | 02/23/2012 &nbsp;ACT | 06/12/2013 &nbsp;ACT | 2015-03-17 | 2016-05-09 | B |  | Tank Terminal | This project is for a new 100,000 barrel per day condensate splitter that takes condensate from a pipeline and separates it into light naphtha, heavy naphtha, kerosene/distillate, residual and Y-grade products which are stored in tanks and loaded in marine vessels at existing docks at this tank terminal. Natural gas used at the facility will be sampled for sulfur every 6 months. | Loading | 64.005 |  | 0 |  | Loading emissions must be controlled if the VOC vapor pressure is greater than 0.10 psia | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | If VOC vapor pressure is greater than 0.10 psia, then vacuum loading is required unless vessel is inerted during loading. Vessel must be leak checked and 5% leakage is assumed. Loading hoses must be drained to vessel being loaded or to a controlled sump. Loading emissions that require control must be directed to VCUs that achieve 99.8%DRE | 500 | PPMV | FOR VACUUM TRUCKS | LAER | NSPS , MACT | N | 99.8 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0811 | LINEAR ALPHA OLEFINS PLANT | INEOS OLIGOMERS USA LLC | BRAZORIA | TX |  | USA | JOHN WALTER | 281-535-4224 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Jesse Lovegren, PhD, 512-239-1284, jesse.lovegren@tceq.texas.gov | 136130 AND N250 | 2869 | 325110 | Not Found | 09/20/2016 &nbsp;ACT | 11/03/2016 &nbsp;ACT | 2016-10-06 | 2017-11-16 | B |  | Manufactures linear alpha olefins (LAO) from ethylene |  | SOCMI Transfer Operations | 64.005 |  | 120000 | gal/hr | Truck, railcar and barge loading | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25 | (Volatile Organic Compounds (VOC)) | VOC | B | Control requirements apply when the product loaded has a vapor pressure of 0.10 psia or greater. Truck and railcar vessels must possess a valid vapor tightness certificate prior to commencement of loading. Barge cargo vessels must be loaded under vacuum. All captured loading emissions must be routed to a thermal oxidizer achieving destruction/removal efficiency (DRE) of 99.9%, or a vapor combustor achieving DRE of 99.5%. | 99.9 | % | TXO | LAER | MACT | N | 0 | U | 99.5 | % | VAPOR COMBUSTOR | 0 |  |  | 0 | 0 | N |  | MACT FFFF
TX-0682 | GALENA PARK TERMINAL | KM LIQUIDS TERMINALS LLC | HARRIS | TX |  | USA | NEAL NYGAARD | 832-239-8018 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ozden Tamer Phone: 512-239-4577 e-mail: ozden.tamer@tceq.texas.gov | 101199 & N158 | 4226 | 325110 | 110037844376 | 02/23/2012 &nbsp;ACT | 06/12/2013 &nbsp;ACT | 2015-03-17 | 2016-05-09 | B |  | Tank Terminal | This project is for a new 100,000 barrel per day condensate splitter that takes condensate from a pipeline and separates it into light naphtha, heavy naphtha, kerosene/distillate, residual and Y-grade products which are stored in tanks and loaded in marine vessels at existing docks at this tank terminal. Natural gas used at the facility will be sampled for sulfur every 6 months. | Fugitives | 99.999 |  | 0 |  | Fugitive VOCs are monitored and minimized through the implementation of 28 LAER monitoring program. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | 28 LAER monitoring program with a leak definition of 500 ppmv will be used for control of fugitives. A weekly visual inspection will also be performed on components in heavy liquid service | 500 | PPMV | LEAK DEFINITION | LAER | NSPS , MACT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | AUXILIARY BOILER (1) AND FUEL GAS HEATERS (6) | 12.31 | NATURAL GAS | 185 | MMBTU/HR | The auxiliary boiler will provide steam to the steam turbine at startup and at cold starts to warm up the ST rotor. The steam from the auxiliary boiler will not be used to augment the power generation of the combustion turbines or steam turbine. The boiler is proposed to operate 8760 hrs/yr but will be limited by an annual fuel throughput based on a capacity factor of 10%. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 320 | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion pratices | 0.5 | T/12 MO ROLL AVG | 12 MONTH ROLLING TOTAL | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | COMBUSTION TURBINE GENERATOR WITH DUCT-FIRED HEAT RECOVERY STEAM GENERATORS (3) | 15.21 | natural gas | 3227 | MMBTU/HR | 3227 MMBTU/HR CT with 500 MMBTU/HR Duct Burner, 3 on 1 configuration. | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 320 | (Volatile Organic Compounds (VOC)) | VOC | A | Oxidation Catalyst and good combustion practices | 1.4 | PPMVD |  | N/A |  | U | 0 | U | 214.8 | T/YR | PER TURBINE-12 MO ROLLING TOTAL | 0 |  |  | 0 | 0 | N |  | Emission Limit 1: Turbine: 0.7 ppmvd without DB
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | DIESEL-FIRED EMERGENCY GENERATOR 3000 kW (1) | 17.11 | DIESEL FUEL | 0 |  |  | Volatile Organic Compounds (VOC) | Other - NA | (Volatile Organic Compounds (VOC)) | VOC | P | Good Combustion Practices/Maintenance | 6.4 | G/KW | PER HR | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The diesel generator (EG-1) will have a combined NOx+NMHC limit of 6.4 g/kW-hr
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | DIESEL-FIRED WATER PUMP 376 bph (1) | 17.21 | DIESEL FUEL | 0 |  | FWP-1: 104.0 tons/year (12-month rolling total) | Volatile Organic Compounds (VOC) | Other - NA | (Volatile Organic Compounds (VOC)) | VOC | P | Good Combustion Practices/Maintenance | 3 | G/HP-H | PER HR | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The Fire Water Pump (FWP-1) will have acombined NOx+NMHC limit of 3.0 g/hp-hr.
*VA-0325 | GREENSVILLE POWER STATION | VIRGINIA ELECTRIC AND POWER COMPANY | GREENSVILLE | VA | 23847 | USA | MARK MITCHELL | (804) 273-4543 | MARK.D.MITCHELL@DOM.COM | 3 | VA001 | VIRGINIA DEPT. OF ENVIRONMENTAL QUALITY; DIVISION OF AIR QUALITY | MR. YOGESH DOSHI | (804)698-4017 | Yogesh.doshi@deq.virginia.gov | For technical information about this facility, please contact the Air Permit Writer, Ms. Alison Sinclair, by phone at (804) 527-5155 or by e-mail: Alison.Sinclair@deq.virginia.gov | 52525 | 4911 | 221112 | Not Found | 02/10/2016 &nbsp;ACT | 06/17/2016 &nbsp;ACT | 2016-09-16 | 2017-02-24 | A | http://www.deq.virginia.gov/Programs/Air/PermittingCompliance/Permitting/IssuedPSDNANSRPermits.aspx | The proposed project will be a new, nominal 1,600 MW combined-cycle electrical power generating facility utilizing three combustion turbines each with a duct-fired heat recovery steam generator (HRSG) with a common reheat condensing steam turbine generator (3 on 1 configuration). The proposed fuel for the turbines and duct burners is pipeline-quality natural gas. |  | PROPANE-FIRED EMERGENCY GENERATORS 150 kW (2) | 17.23 | PROPANE | 0 |  |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 1 | G/HP-H | PER HR | N/A |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | BOILERS - UNITS CC026, CC027 AND CC028 AT CITY CENTER | 12.31 | NATURAL GAS | 44 | MMBTU/H | THE THREE UNITS ARE IDENTICAL CATERPILLAR BOILERS, EACH RATED AT 44 MMBTU/HR. EACH UNIT IS SUBJECT TO THE ANNUAL LIMIT OF OPERATING TIME TO 5,800 HOURS. THE EMISSION LIMITS ARE BASED ON THE ATC PERMIT FOR MODIFICATION #13 DATED NOVEMBER 30, 2009. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | LIMITING THE FUEL TO NATURAL GAS ONLY AND GOOD COMBUSTION PRACTICES | 0.0055 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 0.24 | LB/H |  | 0.0055 | LB/MMBTU |  | 0 | 0 | N
OH-0336 | CAMPBELL SOUP COMPANY | CAMPBELL SOUP COMPANY | HENRY | OH |  | USA | ANN CURNOW | 763-278-5932 | ANN.CURNOW@HDRIC.COM | 5 | OH001 | OHIO ENVIRONMENTAL PROTECTION AGENCY | MR. DANA THOMPSON | 614-644-3701 | Dana.thompson@epa.ohio.gov |  | P0106678 | 2032 | 311422 | 110041176679 | 07/28/2010 &nbsp;ACT | 12/14/2010 &nbsp;ACT | 2011-03-31 | 2011-10-13 | B |  | Canned food maufacturing facility. | Replacing 5 natural gas boilers with 3 new ones. Facility is a Major PSD facility for SO2, NOx, PE, and CO. This permit is PSD for CO. Five old natural gas steam boilers will be decommissioned upon the installation of the 3 new ones. The boilers will burn natural gas and use #2 fuel oil as backup. The facility took a restriction on the #2 fuel oil used to avoid PSD on all but the CO. The boilers are used for steam production for process lines and cogeneration for building heat. | Boilers (3) | 12.31 | Natural Gas | 0 |  | The natural gas throughput is unknown; the limits are based on the potential of 8760 hours of operation. Boilers used for cogeneration of heat to facility. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N |  | 0.0054 | LB/MMBTU | AP-42 FACTOR | OTHER CASE-BY-CASE | OPERATING PERMIT | U | 0 | U | 8.5 | T/YR | ROLLING 12 MO. FROM 3 BOILERS TOGETHER | 0 |  |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT FL01 | 13.31 | NATURAL GAS | 14.34 | MMBTU/H | UNIT FL01 IS A JOHNSTON BOILER AT FLAMINGO LAS VEGAS. THIS UNIT MAY OPERATE 8,760 HOURS PER YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | FLUE GAS RECIRCULATION | 0.0054 | LB/MMBTU |  | OTHER CASE-BY-CASE | SIP , OPERATING PERMIT | N | 0 | Y | 0.078 | LB/H |  | 0.0054 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | SMALL INTERNAL COMBUSTION ENGINE (&lt;600 HP) - UNIT FL12 | 13.31 | DIESEL OIL | 536 | HP | UNIT FL12 IS A DETROIT DIESEL GENERATOR AT FLAMINGO LAS VEGAS. LIKE ALL THE OTHER DIESEL GENERATORS, THE UNIT IS SUBJECT TO THE LIMIT OF MONTHLY AND ANNUAL OPERATING TIMES FOR 2 HOURS PER MONTH AND 36 HOURS PER YEAR RESPECTIVELY. EMISSION FACTORS LISTED IN AP-42 ARE USED TO CALCULATE THE EMISSION LIMITS FOR EACH AND EVERY DIESEL GENERATOR IN THIS MAJOR STATIONARY SOURCE, AND ARE NOT REPEATED FURTHER FOR REPORTING THE BACT DETERMINATIONS. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | THE UNIT IS EQUIPPED WITH A TURBOCHARGER. | 0.0025 | LB/HP-H |  | Other Case-by-Case | SIP , OPERATING PERMIT | N | 0 | Y | 1.35 | LB/H |  | 0.0025 | LB/HP-H |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT BA01 | 13.31 | NATURAL GAS | 16.8 | MMBTU/H | UNIT BA01 IS A KEWANEE BOILER AT BALLY'S LAS VEGAS. UNIT BA01 IS IDENTICAL TO UNIT BA02. THE TWO BOILERS ARE SUBJECT TO THE ANNUAL LIMIT OF COMBINED TOTAL OPERATING TIME FOR 10,900 HOURS PER YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | FLUE GAS RECIRCULATION | 0.0054 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT | N | 0 | Y | 0.09 | LB/H |  | 0.0054 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT BA03 | 13.31 | NATURAL GAS | 31.38 | MMBTU/H | UNIT BA03 IS A KIWANEE BOLER AT BALLY'S LAS VEGAS. THE ANNUAL OPERATING TIME IS LIMITED TO 2,920 HOURS PER YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | OPERATING IN ACCORDANCE WITH THE MANUFACTURER'S SPECIFICATION | 0.0054 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT | N | 0 | Y | 0.17 | LB/H |  | 0.0054 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP01 | 13.31 | NATURAL GAS | 35.4 | MMBTU/H | UNIT CP01 IS A HURST BOILER AT CAESAR'S PALACE. UNIT CP01 IS IDENTICAL TO UNIT CP02. UNITS CP01 THROUGH CP05 (FIVE BOILERS) ARE SUBJECT TO THE ANNUAL LIMIT OF TOTAL OPERATING TIME FOR 33,520 HOURS PER YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | FLUE GAS RECIRCULATION AND OPERATING IN ACCORDANCE WITH THE MANUFACTURER'S SPECIFICATION | 0.0054 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 0.19 | LB/H |  | 0.0054 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP03 | 13.31 | NATURAL GAS | 33.48 | MMBTU/H | UNIT CP03 IS A BURNHAM BOILER AT CAESAR'S PALACE. UNITS CP01 THROUGH CP05 (FIVE BOILERS) ARE SUBJECT TO THE ANNUAL LIMIT OF TOTAL OPERATING TIME FOR 33,520 HOURS PER YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | OPERATING IN ACCORDANCE WITH THE MANUFACTURER'S SPECIFICATION | 0.0054 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT | N | 0 | Y | 0.18 | LB/H |  | 0.0054 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT CP26 | 13.31 | NATURAL GAS | 24 | MMBTU/H | UNIT CP26 IS A UNILUX BOILER AT CAESAR'S PALACE. THE UNIT IS ALLOWED TO OPERATE UP TO 8,760 HOURS PER YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | OPERATING IN ACCORDANCE WITH THE MANUFACTURER'S SPECIFICATION | 0.0054 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 0.13 | LB/H |  | 0.0054 | LB/MMBTU |  | 0 | 0 | N
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | WATER HEATERS - UNITS NY037 AND NY038 AT NEW YORK - NEW YORK | 13.31 | NATURAL GAS | 2 | MMBTU/H | THE TWO UNITS ARE IDENTICAL RBI FUTURA III WATER HEATERS.THE EMISSION LIMITS REPORTED HEREIN ARE BASED ON THE ATC PERMIT FOR MODIFICATION #9 DATED SEPTEMBER 6, 2006. EACH UNIT IS ALLOWED TO OPERATE 24 HOURS/DAY AND 8,760 HOURS/YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | LIMITING THE FUEL TO NATURAL GAS ONLY AND GOOD COMBUSTION PRACTICES | 0.0054 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 0.0108 | LB/H |  | 0.0054 | LB/MMBTU |  | 0 | 0 | N |  | EMISSION LIMIT 2 APPLIES TO EACH UNIT.
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | TURBINE GENERATORS - UNITS CC007 AND CC008 AT CITY CENTER | 16.11 | NATURAL GAS | 4.6 | MMBTU/H | THE TWO UNITS ARE IDENTICAL SOLAR MERCURY COMBUSTION GAS TURBINES FOR ELECTRIC POWER GENERATION. EACH UNIT IS RATED AT 4.6 MMBTU/HR, AND IS ALLOWED TO OPERATE 24 HOURS/DAY AND 8,760 HOURS/YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | LIMITING THE FUEL TO NATURAL GAS ONLY AND OPERATING IN ACCORDANCE WITH THE MANUFACTURER'S SPECIFICATION. | 0.024 | LB/MMBTU |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 0.11 | LB/H |  | 0.024 | LB/MMBTU |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | LARGE INTERNAL COMBUSTION ENGINES (&gt;600 HP) - UNIT HA13 | 17.11 | DIESEL OIL | 1232 | HP | UNIT HA13 IS A MARATHON DIESEL GENERATOR AT HARRAH'S LAS VEGAS. ALL THE SEVEN (7) DIESEL GENERATORS AT HARRAH'S LAS VEGAS ARE FOR EMERGENCY USE ONLY. EACH ONE OF THEM IS SUBJECT TO THE SAME LIMIT OF OPERATING TIME FOR 2 HOURS PER DAY AND 36 HOURS PER YEAR. THE EMISSION LIMITS ARE CALCULATED BASED ON THE EMISSION FACTORS TAKEN FROM AP-42. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | THE UNIT IS EQUIPPED WITH A TURBOCHARGER. | 0.0007 | LB/HP-H |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 8.7 | LB/H |  | 0.0007 | LB/HP-H |  | 0 | 0 | N
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | EMERGENCY GENERATORS - UNITS LX024 AND LX025 AT LUXOR | 17.11 | DIESEL OIL | 2206 | HP | THE TWO UNITS ARE IDENTICAL CATERPILLAR GENERATORS MODEL 3512C. EACH UNIT HAS A FOUR-STROKE COMPRESSION-IGNITION ENGINE RATED AT 2,206 HORSE POWER (HP). THE EMISSION LIMITS REPORTED HEREIN ARE BASED ON THE ATC PERMIT FOR MODIFICATION #10 DATED SEPTEMBER 20, 2006. EACH UNIT IS ALLOWED TO OPERATE UP TO ONE HOUR PER DAY AND FIFTY TWO HOURS PER YEAR. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | TURBOCHARGER AND GOOD COMBUSTION PRACTICES | 0.0003 | LB/HP-H |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | N | 0.71 | LB/H |  | 0.0003 | LB/HP-H |  | 0 | 0 | N |  | EMISSION LIMIT 2 APPLIES TO EACH UNIT.
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | PAINT SPRAY BOOTH - UNIT HA23 | 41.013 | N/A | 500 | GAL/YR | UNIT HA23 IS A GLOBAL FINISHING SPRAY PAINT BOOTH AT HARRAH'S LAS VEGAS. BACT FOR VOC, HAP, AND PM-10 CONSISTS OF: (1) USE HIGH-VOLUME-LOW-PRESSURE SPRAY GUNS FOR THE SURFACE COATING OPERATION; (2) KEEP VOC-CONTAINING MATERIALS IN CLOSED CONTAINERS; (3) EXHAUST AIR FROM THE SURFACE COATING OPERATION SHALL BE FILTERED AT 99% CONTROL EFFICIENCY FOR PARTICULATE MATTER; (4) CONSUMPTIONS OF PAINTS, LACQUERS, THINNERS, AND SOLVENTS ARE LIMITED TO A TOTAL OF 50 GALLONS PER MONTH AND 500 GALLONS PER YEAR BASED ON A WEIGHTED AVERAGE VOC CONTENT OF 7.25 POUNDS PER GALLON. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | MINIMIZING VOC EMISSIONS THROUGH THE MEASURES SPECIFIED IN THE PROCESS DESCRIPTION AND LIMITING CONSUMPTION OF VOC CONTAINING MATERIALS TO 50 GALLONS PER MONTH AND 500 GALLONS PER YEAR. | 362.5 | LB/MO |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 1.81 | T/YR |  | 0 |  |  | 0 | 0 | N |  | EMISSION LIMIT 1 APPLIES TO VOC-CONTAINING PAINTS, LACQUERS, THINNERS, SOLVENTS, ETC.
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | PAINT SPRAY BOOTH - UNIT FL23 | 41.013 | N/A | 600 | GAL/YR | UNIT FL23 IS A DEVILBISS SPRAY PAINT BOOTH AT FLAMINGO LAS VEGAS. BACT FOR VOC, HAP, AND PM-10 CONSISTS OF THE SAME ELEMENTS AS THOSE DESCRIBED IN THE PROCESS FOR UNIT HA23 EXCEPT THAT THE MONTHLY AND ANNUAL CONSUPTIONS ARE LIMITED TO 60 GALLONS AND 600 GALLONS RESPECTIVELY. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | B | BACT CONSISTS OF THE FOUR REQUIREMENTS DESCRIBED IN THE PROCESS. | 435 | LB/MO |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 2.12 | T/YR |  | 0 |  |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | PAINT SPRAY BOOTH - UNIT BA13 | 41.013 | N/A | 600 | GAL/YR | UNIT BA13 IS A SPRAY KING PAINT BOOTH. BACT FOR VOC, HAP AND PM10 INCLUDES: (1) USE HIGH-VOLUME-LOW-PRESSURE SPRAY GUNS FOR THE COATING OPERATION; (2) KEEP VOC-CONTAINING MATERIALS IN CLOSED CONTAINERS; (3) EXHAUST AIR FROM THE COATING OPERATION SHALL BE FILTERED AT A MINIMUM OF 99% CONTROL EFFICIENCY FOR PARTICULATE MATTER; (4) CONSUMPTIONS OF PAINTS, LACQUERS, THINNERS, AND SOLVENTS ARE LIMITED TO A TOTAL OF 60 GALLONS PER MONTH AND 600 GALLONS PER YEAR BASED ON A WEIGHTED AVERAGE VOC CONTENT OF 7.25 POUNDS PER GALLON. THE SAME BACT DETERMINATION APPLIES TO PAINT SPRAY BOOTHS AT PARIS CASINO RESORT AND IMPERIAL PALACE, AND NEED NOT BE REPEATED FROM HEREON. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | BACT CONSISTS OF THE FOUR REQUIREMENTS DESCRIBED IN THE PROCESS. | 435 | LB/MO |  | Other Case-by-Case | SIP , OPERATING PERMIT | N | 0 | Y | 2.18 | T/YR |  | 0 |  |  | 0 | 0 | N
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | PAINT SPRAY BOOTH - UNIT MG39 AT MGM GRAND | 41.013 | N/A | 200 | GAL/MO | THE UNIT IS A MCMASTER-CARR SPRAY BOOTH. THE EMISSION LIMITS ARE BASED ON THE ATC PERMIT FOR MODIFICATION #13 DATED NOVEMBER 30, 2009. THE THROUGHPUT LIMIT MEANS THAT THE TOTAL MONTHLY CONSUMPTION OF ALL VOC CONTAINING MATERIALS, SUCH AS PAINTS, PAINT STRIPPERS, BASECOATS, PRIMERS, REDUCERS, THINNERS, SOLVENTS, ETC., IS LIMITED TO 200 GALLONS PER MONTH AND 2,000 GALLONS PER YEAR. THE AVERAGE VOC CONTENT IS LIMITED TO 6.84 POUNDS PER GALLON. THE AVERAGE HAP CONTENT IS LIMITED TO 3.21 POUNDS PER GALLON. THE UNIT IS SUBJECT TO NESHAP SUBPART 6H. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | LIMITING THE AVERAGE VOC CONTENT TO 6.84 LBS/GALLON | 1368 | LB/MONTH |  | Other Case-by-Case | SIP , OPERATING PERMIT | N | 0 | N | 6.84 | T/YR |  | 0 |  |  | 0 | 0 | N
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | GASOLINE STORAGE AND DISPENSING STATION - UNIT BE108 AT BELLAGIO | 42.003 | N/A | 26400 | GAL/MO | THE EMISSION UNIT IS A 3,700 GALLON STORAGE TANK EQUIPPED WITH A STAGE 1 VAPOR RECOVERY SYSTEM BASED ON CARB EO G-70-132 SERIES FOR TANK TRUCK DELIVERY OF GASOLINE AND A STAGE 2 VAPOR CONTROL SYSTEM BASED ON CARB EO G-70-17 FOR GASOLINE DISPENSING. THROUGHPUT OF GASOLINE IS LIMITED TO 26,400 GALLONS/MONTH AND 264,000 GALLONS/YEAR FOR THIS EMISSION UNIT. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | STAGE 1 VAPOR RECOVERY SYSTEM FOR GASOLINE DELIVERY TO THE TANK AND STAGE 2 VAPOR CONTROL SYSTEM FOR GASOLINE DISPENSING | 3.3 | LB/1000 GAL |  | Other Case-by-Case | SIP , OPERATING PERMIT |  | 0 | Y | 87.12 | LB/MO |  | 3.3 | LB/1,000 GAL |  | 0 | 0 | N
IN-0263 | MIDWEST FERTILIZER COMPANY LLC | MIDWEST FERTILIZER COMPANY LLC | POSEY | IN | 47620 | USA | RON OGLESBY | 9703057850 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DEENA P. LEVERING 317-234-5400 DLEVERIN@IDEM.IN.GOV SECTION CHIEF: TRIPURARI SINHA PH.D. 317-234-4907 | 129-36943-00059 | 2873 | 325311 | 110059696841 | 03/11/2016 &nbsp;ACT | 03/23/2017 &nbsp;ACT | 2017-07-07 | 2017-08-22 | C | HTTP:PERMITS.AIR.IDEM.IN.GOV/36943F.PDF | STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | UREA SYNTHESIS PLANT (EU-006) | 61.012 |  | 2640 | METRIC TON/DAY |  | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD OPERATIONAL PRACTICES | 0 |  |  | OTHER CASE-BY-CASE | OTHER | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N | 2016 | Basis is State VOC BACT (326 IAC 8-1-6)