## All Pollutants_Large Boilers 11
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
AL-0276 | MOUNT VERNON MILL | THYSSENKRUP STEEL USA, LLC | MOBILE | AL | 36513 | USA | JORDAN COLLINS | 251-289-3833 | JORDAN.COLLINS@ARCELORMITTAL.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-0095-X001 | 3312 | 331221 | Unknown | 08/03/2009 &nbsp;ACT | 03/25/2010 &nbsp;ACT | 2015-02-27 | 2016-05-05 | C |  | The carbon steel mill would receive slabs primarily by barge. These carbon steel slabs would be heated and rolled to from a long strip in the hot strip mill. After rolling, the coils would be prepared for sale or would proceed to the picklin lines. After pickling, if needed, the strips would be cold-rolled for sale or would be further processed in the galvanizing lines. |  | Walking Beam Furnaces | 11.31 | Natural Gas | 845 | MMBTU/H | Throughput Capacity/Size: 845 mmbtu/hr (51-53) | Sulfur Dioxide (SO2) | EPA/OAR Mthd 6C | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.0006 | LB/MMBTU |  | BACT-PSD |  | U | 0 | N | 0.507 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Test Method Info: 6 or 6c
AR-0094 | JOHN W. TURK JR. POWER PLANT | SOUTHWEST ELECTRIC POWER COMPANY | FULTON | AR | 71838 | USA | KRIS GAUS | 214771113 | KPGAIS@AEP.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2123-AOP-R0 | 4911 | 221112 | UNKNOWN | 07/08/2008 &nbsp;ACT | 11/05/2008 &nbsp;ACT | 2009-01-09 | 2010-04-09 | A |  | 600 MW POWDER RIVER BASIN SUB-BITUMINOUS PULVERIZED COAL FIRED POWER PLANT | PSD AND 112(G) PERMIT DECISION | AUXILIARY BOILER | 11.31 | NATURAL GAS | 555 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.0006 | LB/MMBTU | 3 HOUR AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
*FL-0330 | PORT DOLPHIN ENERGY LLC |  | HILLSBOROUGH | FL | 33616 | USA |  |  |  | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | DPA-EPA-R4001 | 4923 | 213112 | 110029520141 | &nbsp; | 12/01/2011 &nbsp;ACT | 2012-02-03 | 2018-03-23 | A |  | Port Dolphin is a deepwater port designed to moor liquefied natural gas shuttle and regasification vessels 28 miles off the cost of Florida. |  | Boilers (4 - 278 mmbtu/hr each) | 11.31 | natural gas | 0 |  |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | use of natural gas | 0.0006 | LB/MMBTU | 3-HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0166 | INDIANA GASIFICATION, LLC | INDIANA GASIFICATION, LLC | SPENCER | IN | 47635 | USA | MARK LUBBERS | 3174905078 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | T147-30464-00060 | 4925 | 221210 | 110045439888 | 04/20/2011 &nbsp;ACT | 06/27/2012 &nbsp;ACT | 2013-08-16 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/30464F.PDF | THE PERMITTEE OWNS AND OPERATES A STATIONARY SUBSTITUTE NATURAL GAS (SNG) AND LIQUEFIED CARBON DIOXIDE (CO2) PRODUCTION PLANT ALSO SIC: 2819 NAICS: 211112 | ALSO SIC: 2819 NAICS: 211112 | TWO (2) AUXILIARY BOILERS | 11.31 | NATURAL GAS | 408 | MMBTU/H, EACH | IDENTIFIED AS EU-005A AND EU-005B. ALSO COMBUSTS SUBSTITIUTE NATURAL GAS (SNG) | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | USE OF NATURAL GAS OR SNG | 0.0006 | MMBTU/H | 3 HR | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0234 | GRAIN PROCESSING CORPORATION | GRAIN PROCESSING CORPORATION | DAVIESS | IN | 47501 | USA | WENDY BOUVIER | 8122572759 | WENDY.BOUVIER@GRAINPROCESSING.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | MADHURIMA MOULIK 317-233-0868 JASON KRAWCZYK, SECTION CHIEF IDEM OFFICE OF AIR QUALITY 100 N. SENATE AVENUE 317-234-5174 | 027-35177-00046 | 2046 | 311221 | 110041204265 | 11/26/2014 &nbsp;ACT | 12/08/2015 &nbsp;ACT | 2016-02-25 | 2016-07-06 | B | HTTP:PERMITS.AIR.IDEM.IN.GOV/35177F.PDF | THIS FACILITY IS A STATIONARY CORN WET MILLING PLANT. |  | BOILER 1 | 11.31 | NATURAL GAS | 271 | MMBTU/H | NATURAL GAS FIRED, ALSO CAPACBLE OF BURNING ALCOHOL. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | SULFUR CONTENT OF ALCOHOL AND BY-PRODUCT WASTE OIL | 0.0006 | LB/MMBTU | NATURAL GAS ALONE | BACT-PSD |  | N | 0 |  | 0.0008 | LB/MMBTU | NATURAL GAS AND ALCOHOL | 0 |  |  | 0 | 0 | N |  | AMOUNT OF ALCOHOL HEADS AND BY-PRODUCT WASTE OIL SHALL NOT EXCEED 600 GALLONS PER HR. SULFUR CONTENT OF ALCOHOL HEADS AND BY-RPODUCT WASTE OIL SHALL NOT EXCEED 6.9 PPM BY WEIGHT. SO2 EMISSIONS SHALL NOT EXCEED 0.21 LB/HR WHEN COMBUSTING NATURAL GAS WITH ALCOHOL
IN-0234 | GRAIN PROCESSING CORPORATION | GRAIN PROCESSING CORPORATION | DAVIESS | IN | 47501 | USA | WENDY BOUVIER | 8122572759 | WENDY.BOUVIER@GRAINPROCESSING.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | MADHURIMA MOULIK 317-233-0868 JASON KRAWCZYK, SECTION CHIEF IDEM OFFICE OF AIR QUALITY 100 N. SENATE AVENUE 317-234-5174 | 027-35177-00046 | 2046 | 311221 | 110041204265 | 11/26/2014 &nbsp;ACT | 12/08/2015 &nbsp;ACT | 2016-02-25 | 2016-07-06 | B | HTTP:PERMITS.AIR.IDEM.IN.GOV/35177F.PDF | THIS FACILITY IS A STATIONARY CORN WET MILLING PLANT. |  | BOILER 2 | 11.31 | NATURAL GAS | 271 | MMBTU/H | NATURAL GAS BOILER WITH CAPABILITY OF BURNING ALCOHOL | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.0006 | LB/MMBTU | NATURAL GAS ALONE | BACT-PSD |  | N | 0 |  | 0.0008 | LB/MMBTU | NATURAL GAS WITH ALCOHOL | 0 |  |  | 0 | 0 | N |  | SHALL NOT EXCEED 0.16 LB/HR FOR NATURAL GAS ALONE AND 0.21 LB/HR FOR NATURAL GAS AND ALCOHOL. SULFUR CONTENT OF ALCOHOL HEADS AND BY-PRODUCT WASTE OIL SHALL NOT EXCEED 6.9 PPM BY WEIGHT.. AMOUNT OF ALCOHOL HEADS AND BY-PRODUCT WASTE OIL SHALL NOT EXCEED 600 GALLONS PER HOUR.
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT HA08 | 11.31 | NATURAL GAS | 8.37 | MMBTU/H | THE EMISSION UNIT IS A CLEAVER BROOKS BOILER AT HARRAH'S LAS VEGAS. UNIT HA08 IS IDENTICAL TO HA09 AND HA10. THE SAME SET OF EMISSION LIMITS APPLIES TO EACH OF THE THREE BOILERS. THE THREE BOILERS ARE SUBJECT TO THE LIMIT OF TOTAL ANNUAL OPERATING TIME FOR 20,000 HOURS PER YEAR. THERE ARE NO BOILERS AT HARRAH'S LAS VEGAS, WHICH HAS A THROUGHPUT CAPACITY IN EXCESS OF 10 MMBTU/HR. NO BACT DETERMINATIONS FOR ANY EMISSION UNITS AT BILL'S GAMBLIN' HALL & SALON ARE REPORTED HEREIN BECAUSE ALL OF THEM HAVE A VERY SMALL POTENTIAL TO EMIT FOR ANY POLLUTANT. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | FUEL IS LIMITED TO NATURAL GAS. | 0.0006 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | Y | 0.005 | LB/H |  | 0.0006 | LB/MMBTU |  | 0 | 0 | N
NV-0050 | MGM MIRAGE | MGM MIRAGE | CLARK | NV | 89109 | USA | CINDY ORTEGA | 7026506765 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | DAVID C. LEE, RBLC COORDINATOR, 702-455-1673 | 825 | 701 | 721120 | UNKNOWN | 05/22/2008 &nbsp;ACT | 11/30/2009 &nbsp;ACT | 2010-02-16 | 2010-03-15 | A |  | THE FACILITY IS A MAJOR SOURCE FOR CO, NOX, PM-10, AND A NON-MAJOR SOURCE FOR SO2, VOC, AND HAP. THE FACILITY IS A CONGLOMERATE OF HOTELS AND CASINOS LOCATED IN A CONTIGUOUS AREA, WHICH AIR QUALITY IS NON-ATTAINMENT FOR CO, OZONE, AND PM-10, AND ATTAINMENT FOR THE OTHER CRITERIA AIR POLLUTANTS. | THE FACILITY IS A CONGLOMERATE OF TEN BUSINESS ENTITIES, WHICH ARE: (1) MGM GRAND, (2) NEW YORK-NEW YORK, (3) MANDALAY BAY, (4) LUXOR, (5) EXCALIBUR, (6) BELLAGIO, AND (7) CITY CENTER, (8) SIGNATURE (THE RESIDENCES), (9) MONTE CARLO, AND (10) FOUR SEASONS. ALL OF THESE ENTITIES ARE IN A CONTIGUOUS PROPERTY AND HAD BEEN PERMITTED INDIVIDUALLY PRIOR TO THE ACQUISITION PROCESS BEGINNING FROM 2005. THE FACILITY BECAME A MAJOR STATIONARY SOURCE FOR CO WHEN THE ATC FOR MODIFICATION #8 WAS ISSUED ON MARCH 30, 2006. MODIFICATION #8 CONSISTED OF CONSTRUCTING THE NEW CITY CENTER, WHICH COMMENCED OPERATION IN DECEMBER 2009. ALL EMISSION UNITS PERMITTED ON OR AFTER MARCH 30, 2006 ARE CONSIDERED NEW FOR THIS REPORT. | BOILERS - UNITS CC001, CC002, AND CC003 AT CITY CENTER | 11.31 | NATURAL GAS | 41.64 | MMBTU/H | THE THREE UNITS ARE IDENTICAL NEBRASKA BOILERS, EACH OF WHICH IS RATED AT 41.64 MMBTU/HR. EACH UNIT IS ALLOWED TO OPERATE 24 HOURS/DAY AND UP TO 5,800 HOURS/ YEAR. THE EMISSION LIMITS REPORTED HEREIN ARE BASED ON THE ATC PERMIT FOR MODIFICATION #8 DATED MARCH 30, 2006. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | LIMITING THE FUEL TO NATURAL GAS ONLY. | 0.0007 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT |  | 0 | N | 0.72 | LB/D |  | 0.0007 | LB/MMBTU |  | 0 | 0 | N |  | EMISSION LIMIT 2 APPLIES TO EACH OF THE THREE UNITS.
TX-0650 | DIRECT REDUCED IRON AND HOT BRIQUETTING FACILITY | VOESTALPINE TEXAS LLC | SAN PATRICIO | TX |  | USA | MATTHIAS PASTL | 361-452-0746 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Dois Webb, Phone: 512-239-1575 e-mail: dois.webb@tceq.texas.gov | 108113/PSDTX1344 | 3312 | 331111 | UNKNOWN | 02/05/2013 &nbsp;ACT | 03/18/2014 &nbsp;ACT | 2014-03-27 | 2016-07-29 | A |  | Converts iron ore pellets into iron briquettes |  | GAS REFORMER | 11.31 | NATURAL GAS | 1591 | MMBTU/H |  | Sulfur Dioxide (SO2) | EPA/OAR Mthd 6 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | EMISSION LIMIT AND FUEL SULFUR CONTENT LIMIT | 0.002 | LB/MMBTU |  | BACT-PSD | NSPS , NESHAP , MACT , SIP | N | 0 | U | 2000 | GR/MMSCF | MAX FUEL SULFUR CONTENT | 0 |  |  | 0 | 0 | N
PA-0260 | DELTA POWER PLANT | CONECTIV MID MERIT LLC | YORK | PA | 197146066 | USA | ALBERT KIRBY | 3024515090 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083 | 4911 | 221122 | 110010966785 | &nbsp; | 01/03/2008 &nbsp;ACT | 2008-06-30 | 2008-08-25 | A |  | 1100 MEGAWATT COMBINED CYCLE POWER PLANT |  | GAS FIRED TURBINES (6) (SIMPLE CYCLE) | 11.31 | NG | 11240 | GAL/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | A |  | 0.003 | LB/MMBTU | HOURLY BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
PA-0260 | DELTA POWER PLANT | CONECTIV MID MERIT LLC | YORK | PA | 197146066 | USA | ALBERT KIRBY | 3024515090 |  | 3 | PA001 | PENNSYLVANIA DEPT OF ENVIRONMENTAL PROTECTION, BUREAU OF AIR QUALITY | MR. ROBERT COOK | (717)772-3974 | rwcook@pa.gov |  | 67-05083 | 4911 | 221122 | 110010966785 | &nbsp; | 01/03/2008 &nbsp;ACT | 2008-06-30 | 2008-08-25 | A |  | 1100 MEGAWATT COMBINED CYCLE POWER PLANT |  | GAS FIRED TURBINES (60 (COMBINED CYCLE) | 11.31 | NG | 11240 | GAL/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.003 | LB/MMBTU | HOURLY BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0650 | DIRECT REDUCED IRON AND HOT BRIQUETTING FACILITY | VOESTALPINE TEXAS LLC | SAN PATRICIO | TX |  | USA | MATTHIAS PASTL | 361-452-0746 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Dois Webb, Phone: 512-239-1575 e-mail: dois.webb@tceq.texas.gov | 108113/PSDTX1344 | 3312 | 331111 | UNKNOWN | 02/05/2013 &nbsp;ACT | 03/18/2014 &nbsp;ACT | 2014-03-27 | 2016-07-29 | A |  | Converts iron ore pellets into iron briquettes |  | REACTOR FURNACE TOP EXHAUST TO HOT PRESSURE RELIEF FLARE | 11.31 | NATURAL GAS | 458 | SCF/HR |  | Sulfur Dioxide (SO2) | EPA/OAR Mthd 6 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 0.02 | LB/H |  | BACT-PSD | NSPS , NESHAP , MACT , SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0248 | DIRECT REDUCTION IRON PLANT | CONSOLIDATED ENVIRONMENTAL MANAGEMENT INC - NUCOR | ST JAMES PARISH | LA | 70723 | USA | STEVE ROWLAN | (704) 366-7000 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | KERMIT WITTENBURG, KERMIT.WITTENBURG@LA.GOV | PSD-LA-751 | 3312 | 331111 | 110037583442 | 10/31/2010 &nbsp;ACT | 01/27/2011 &nbsp;ACT | 2011-06-28 | 2011-12-08 | B |  | THE DRI PROCESS REDUCES THE IRON OXIDE CONTENT OF IRON ORE PELLETS INTO IRON METAL THROUGH DIRECT CONTACT WITH A REDUCING GAS. THE EFFECTIVENESS OF THIS REDUCTION PROCESS IS CALLED METALLIZATION, AND THE PROCESS EQUIPMENT WILL BE DESIGNED TO ACHIEVE A METALLIZATION RATE OF AT LEAST 92% OF THE OXIDES WITHIN THE ORE. THE REDUCTION WILL TAKE PLACE IN A COUNTERCURRENT VERTICAL SHAFT FURNACE, WHERE REDUCING GAS PASSES UP THROUGH IRON OXIDE PELLETS, WHICH FEED THROUGH THE FURNACE BY GRAVITY. THE MAJOR ELEMENTS OF THE DRI PROCESS INCLUDE THE FOLLOWING: (1) IRON OXIDE PREPARATION; (2) REDUCING GAS PREPARATION; (3) DRI REACTOR SHAFT FURNACE; (4) SPENT REDUCING GAS PREPARATION FOR REUSE, (5) DRI PRODUCT HANDLING; AND (6) ANCILLARY OPERATIONS, INCLUDING A PACKAGE BOILER, TWO COOLING TOWERS, AND A FLARE FOR EMERGENCY SITUATIONS. | ON 1/27/11, LDEQ ISSUED TO NUCOR TITLE V (TV) AND PSD PERMITS AUTHORIZING TWO DRI UNITS (MIDREX DESIGN). ON 9/29/11, NUCOR REQUESTED APPROVAL TO CONVERT ONE UNIT TO A DESIGN DEVELOPED BY TENOVA HYL. THE ONLY SIGNIFICANT DIFFERENCE BETWEEN THE MIDREX AND HYL DESIGNS IS THE POINT IN THE PROCESS WHERE NATURAL GAS IS REFORMED INTO CO & H2. LDEQ APPROVED NUCORâ€™S APPLICATION AND MODIFIED THE TV PERMIT ON 3/8/12. HOWEVER, LDEQ CONCLUDED THAT ITS INITIAL BACT DETERMINATIONS REMAINED APPROPRIATE AND DID NOT MODIFY THE PSD PERMIT. LDEQ SUBSEQUENTLY DECIDED TO REOPEN PSD-LA-751 FOR THE LIMITED PURPOSE OF CONFIRMING LDEQâ€™S INITIAL ASSESSMENT. LDEQ REQUIRED NUCOR TO PROVIDE AN ANALYSIS DEMONSTRATING THAT 1.) BACT FOR THE HYL EQUIPMENT IS NOT MORE STRINGENT THAN THAT PROVIDED BY PSD-LA-751, AND 2.) USE OF HYL EQUIPMENT IN ONE UNIT OF THE DRI FACILITY DOES NOT MATERIALLY CHANGE THE ORIGINAL AIR QUALITY ANALYSIS. LDEQ AGAIN CONCLUDED THAT NO CHANGES TO THE EXISTING BACT DETERMINATIONS WERE WARRANTED AND THAT THE HYL DESIGN DOES NOT RESULT IN ADVERSE AIR QUALITY IMPACTS. THEREFORE, LDEQ REVISED PSD-LA-751 ON 11/16/12 ONLY TO CLARIFY THAT IT COVERS THE HYL (I.E., IN SITU REFORMING) EQUIPMENT. MORE SPECIFICALLY, PSD-LA-751(M-1) REFLECTED THE FOLLOWING CHANGES: 1. REPLACEMENT OF THE DRI UNIT NO. 1 REFORMER (DRI-108) WITH A PROCESS HEATER. 2. REVISION OF THE PM10/PM2.5 BACT LIMIT FOR DRI-108 FROM 0.0027 GR/DSCF TO 0.006 LB/MM BTU TO ACCOUNT FOR BOTH FILTERABLE AND CONDENSABLE PM. 3. DELETION OF THE DRI UNIT NO. 1 UPPER SEAL GAS VENT. 4. REMOVAL OF SEAL GAS EMISSIONS FROM THE DRI UNIT NO. 1 FURNACE DUST COLLECTION. 5. LOWERING OF THE FIRING RATE OF THE DRI UNIT NO. 1 PACKAGE BOILER FROM 290 TO 100 MM BTU/HR. 6. REVISION OF THE EMISSIONS LIMITATIONS FOR THE DRI UNIT NO. 1 HOT FLARE TO REFLECT THAT IT WILL NOW BE UTILIZED FOR ONLY SU/SD OPERATIONS INSTEAD OF INTERMITTENTLY DURING NORMAL OPERATIONS. | DRI-109 - DRI Unit #1 Package Boiler Flue Stack | 11.31 | Natural Gas | 1760 | Billion Btu/yr | The package boilers provide steam to each DRI unit. The steam is primarily used to heat the reboiler in the acid gas absorption system, as well as for utility purposes. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Emissions of SO2 are usually attributable to the sulfur contained within the fuel being combusted. Therefore the use of a low sulfur fuel can drastically reduce emissions of SO2 when compared to other potential fuels. | 0.09 | LB/H |  | BACT-PSD |  | N | 0 | U | 0.33 | T/YR |  | 0 |  |  | 0 | 0 | N |  | Sulfur dioxide: Purchase natural gas with a sulfur content less than 2000 grains per million standard cubic feet of gas. Sulfur content shall be monitored and recorded monthly and shall be based on either the natural gas analysis provided by the supplier or direct sampling by the facility
LA-0248 | DIRECT REDUCTION IRON PLANT | CONSOLIDATED ENVIRONMENTAL MANAGEMENT INC - NUCOR | ST JAMES PARISH | LA | 70723 | USA | STEVE ROWLAN | (704) 366-7000 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | KERMIT WITTENBURG, KERMIT.WITTENBURG@LA.GOV | PSD-LA-751 | 3312 | 331111 | 110037583442 | 10/31/2010 &nbsp;ACT | 01/27/2011 &nbsp;ACT | 2011-06-28 | 2011-12-08 | B |  | THE DRI PROCESS REDUCES THE IRON OXIDE CONTENT OF IRON ORE PELLETS INTO IRON METAL THROUGH DIRECT CONTACT WITH A REDUCING GAS. THE EFFECTIVENESS OF THIS REDUCTION PROCESS IS CALLED METALLIZATION, AND THE PROCESS EQUIPMENT WILL BE DESIGNED TO ACHIEVE A METALLIZATION RATE OF AT LEAST 92% OF THE OXIDES WITHIN THE ORE. THE REDUCTION WILL TAKE PLACE IN A COUNTERCURRENT VERTICAL SHAFT FURNACE, WHERE REDUCING GAS PASSES UP THROUGH IRON OXIDE PELLETS, WHICH FEED THROUGH THE FURNACE BY GRAVITY. THE MAJOR ELEMENTS OF THE DRI PROCESS INCLUDE THE FOLLOWING: (1) IRON OXIDE PREPARATION; (2) REDUCING GAS PREPARATION; (3) DRI REACTOR SHAFT FURNACE; (4) SPENT REDUCING GAS PREPARATION FOR REUSE, (5) DRI PRODUCT HANDLING; AND (6) ANCILLARY OPERATIONS, INCLUDING A PACKAGE BOILER, TWO COOLING TOWERS, AND A FLARE FOR EMERGENCY SITUATIONS. | ON 1/27/11, LDEQ ISSUED TO NUCOR TITLE V (TV) AND PSD PERMITS AUTHORIZING TWO DRI UNITS (MIDREX DESIGN). ON 9/29/11, NUCOR REQUESTED APPROVAL TO CONVERT ONE UNIT TO A DESIGN DEVELOPED BY TENOVA HYL. THE ONLY SIGNIFICANT DIFFERENCE BETWEEN THE MIDREX AND HYL DESIGNS IS THE POINT IN THE PROCESS WHERE NATURAL GAS IS REFORMED INTO CO & H2. LDEQ APPROVED NUCORâ€™S APPLICATION AND MODIFIED THE TV PERMIT ON 3/8/12. HOWEVER, LDEQ CONCLUDED THAT ITS INITIAL BACT DETERMINATIONS REMAINED APPROPRIATE AND DID NOT MODIFY THE PSD PERMIT. LDEQ SUBSEQUENTLY DECIDED TO REOPEN PSD-LA-751 FOR THE LIMITED PURPOSE OF CONFIRMING LDEQâ€™S INITIAL ASSESSMENT. LDEQ REQUIRED NUCOR TO PROVIDE AN ANALYSIS DEMONSTRATING THAT 1.) BACT FOR THE HYL EQUIPMENT IS NOT MORE STRINGENT THAN THAT PROVIDED BY PSD-LA-751, AND 2.) USE OF HYL EQUIPMENT IN ONE UNIT OF THE DRI FACILITY DOES NOT MATERIALLY CHANGE THE ORIGINAL AIR QUALITY ANALYSIS. LDEQ AGAIN CONCLUDED THAT NO CHANGES TO THE EXISTING BACT DETERMINATIONS WERE WARRANTED AND THAT THE HYL DESIGN DOES NOT RESULT IN ADVERSE AIR QUALITY IMPACTS. THEREFORE, LDEQ REVISED PSD-LA-751 ON 11/16/12 ONLY TO CLARIFY THAT IT COVERS THE HYL (I.E., IN SITU REFORMING) EQUIPMENT. MORE SPECIFICALLY, PSD-LA-751(M-1) REFLECTED THE FOLLOWING CHANGES: 1. REPLACEMENT OF THE DRI UNIT NO. 1 REFORMER (DRI-108) WITH A PROCESS HEATER. 2. REVISION OF THE PM10/PM2.5 BACT LIMIT FOR DRI-108 FROM 0.0027 GR/DSCF TO 0.006 LB/MM BTU TO ACCOUNT FOR BOTH FILTERABLE AND CONDENSABLE PM. 3. DELETION OF THE DRI UNIT NO. 1 UPPER SEAL GAS VENT. 4. REMOVAL OF SEAL GAS EMISSIONS FROM THE DRI UNIT NO. 1 FURNACE DUST COLLECTION. 5. LOWERING OF THE FIRING RATE OF THE DRI UNIT NO. 1 PACKAGE BOILER FROM 290 TO 100 MM BTU/HR. 6. REVISION OF THE EMISSIONS LIMITATIONS FOR THE DRI UNIT NO. 1 HOT FLARE TO REFLECT THAT IT WILL NOW BE UTILIZED FOR ONLY SU/SD OPERATIONS INSTEAD OF INTERMITTENTLY DURING NORMAL OPERATIONS. | DRI-209 - DRI Unit #2 Package Boiler Flue Stack | 11.31 | Natural Gas | 1760 | Billion Btu/yr | The package boilers provide steam to each DRI unit. The steam is primarily used to heat the reboiler in the acid gas absorption system, as well as for utility purposes. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Emissions of SO2 are usually attributable to the sulfur contained within the fuel being combusted. Therefore the use of a low sulfur fuel can drastically reduce emissions of SO2 when compared to other potential fuels. | 0.09 | LB/H |  | BACT-PSD |  | N | 0 | U | 0.33 | T/YR |  | 0 |  |  | 0 | 0 | N |  | Sulfur dioxide: Purchase natural gas with a sulfur content less than 2000 grains per million standard cubic feet of gas. Sulfur content shall be monitored and recorded monthly and shall be based on either the natural gas analysis provided by the supplier or direct sampling by the facility
LA-0231 | LAKE CHARLES GASIFICATION FACILITY | LAKE CHARLES COGENERATION, LLC | CALCASIEU | LA | 70665 | USA | DOUG BARBA | 7139634635 | INTERPOWERLLC@AOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: MR. DAN NGUYEN - 225-219-3180 | PSD-LA-742 | 2869 | 325110 | UNKNOWN | 09/24/2008 &nbsp;ACT | 06/22/2009 &nbsp;ACT | 2009-07-10 | 2010-05-17 | A |  | A FACILITY TO CONVERT APPROXIMATELY 7400 TONS/DAY OF PETROLEUM COKE TO NATURAL GAS AND SULFURIC ACID. PERMIT PSD-LA-742(M1), DECEMBER 30, 2010, ALLOWS THE FACILITY TO PRODUCE 2.3 MILLION TONS OF METHANOL, INSTEAD OF NATURAL GAS. | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS. PERMIT PSD-LA-742(M1) WAS ISSUED DECEMBER 30, 2010 TO REVISE THE PROCESS DESIGN. THE FACILITY WILL PRODUCE H2SO4 AND METHANOL, INSTEAD OF NATURAL GAS. EXISTING BACT WILL NOT BE CHANGED. NO NEW BACT WILL BE ADDED. PERMIT PSD-LA-742(M2) DATED JUNE 29, 2012 1) REVISES THE PROCESS DESIGN TO PRODUCE HYDROGEN, 2) INCORPORATE PM 2.5 AND CO2E, AND 3)CHANGE NAME TO LAKE CHARLES CLEAN ENERGY. NO NEW BACT WILL BE ADDED. | AUXILIARY BOILER | 11.31 | NATURAL GAS | 938.3 | MMBTU/H |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | FUELED BY NATURAL GAS OR SUBSTITUTE NATURAL GAS (SNG) | 0.28 | LB/H | MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
KY-0106 | RIVERSIDE GENERATING CO LLC | RIVERSIDE GENERATING CO LLC | LAWRENCE | KY | 41129 | USA | STEVEN HOLBROOK | 6066861311 |  | 4 | KY001 | KENTUCKY DEP, DIV FOR AIR QUALITY | MR. RICK SHEWEKAH, MGR | (502)564-3999 | Sreenivas.Kesaraju@ky.gov |  | V-15-035 | 4911 | 221112 | 110012574071 | 09/20/2012 &nbsp;ACT | 09/30/2016 &nbsp;ACT | 2017-04-24 | 2017-04-28 | C |  | Riverside currently operates a simple cycle power plant consists of five (5) Siemens 501 FD2 turbines which began commercial operations in 2001 (Units 1-3) and 2002 (Units 4-5). The five Existing Natural Gas-Fired Turbines (EU 01 - 05) have the capacity to generate 180 MW each. This application is for the conversion of the simple cycle gas turbine electric generation units to combined-cycle gas turbine (CCGT) units for a new total generating capacity of approximately 1,700 MW. |  | Five Combined Cycle Generation Turbines (CCGT) with Duct burners and HRSG | 11.31 | Natural Gas | 1700 | MW | Five natural gas-fired turbines for electric generation, rated 2,076 MMBtu/hr each. New Project: Five Combined Cycle Generation Turbines (CCGT) (EU 01B-05B) - Five New Natural Gas-Fired Duct Burners for Five New Heat Recovery Steam Generators (HRSG) providing heat for Two New Steam Turbine Generators (STG) System (1) â€“ Three CTG/HRSG combined cycles to one STG System (2) â€“ Two CTG/HRSG combined cycles to one STG Maximum Rated Capacity: EU 01B-05B Duct Burners for HRSGs, 660 MMBtu/hr each STG, 3x1 â€“ 500MW, 2x1 â€“ 350 MW Construction Commenced: EU01B-05B proposed 2016 | Sulfur Dioxide (SO2) | EPA/OAR Mthd 6 | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | The use of pipeline quality natural gas with a sulfur content of less than or equal to 1.0 grain/100 dscf | 7.82 | LB/HR | 1-HOUR AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0245 | HYDROGEN PLANT | VALERO REFINING - NEW ORLEANS, LLC | ST. CHARLES | LA | 70079 | USA | ROBERT MARTIN | (985)764-8611 | ROB.MARTIN@VALERO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen - 225-219-3395 | PSD-LA-750 | 2911 | 324110 | Not Available | 08/18/2010 &nbsp;ACT | 12/15/2010 &nbsp;ACT | 2011-03-29 | 2011-07-06 | B |  | A plant to produce hydrogen by steam reforming natural gas. | Application Accepted Received Date = Date of completeness Determination | SMR Heaters (EQT0400 and EQT0401) | 11.31 | Fuel Gas | 1055 | MMBTU/H | Two identical units | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | Limit maximum H2S concentration in fuels to 60 ppmv (annual average) | 16.7 | LB/H | HOURLY MAXIMUM (EACH UNITS) | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0167 | MAGNETATION LLC | MAGNETATION LLC | WHITE | IN | 47980 | USA | MICHAEL TWITE | 2182593795 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: KRISTEN WILLOUGHBY 317-233-3031 KWILLOUGHBY@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 181-32081-00054 | 1011 | 212210 | 110055584363 | 07/02/2012 &nbsp;ACT | 04/16/2013 &nbsp;ACT | 2013-08-16 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32081F.PDF | IRON ORE CONCENTRATE PELLETIZING PLANT |  | FURNACE WINDBOX EXHAUST (WBE) | 11.31 | NATURAL | 436 | MMBTU/H | IDENTIFIED AS EU014 USING ONE (1) GAS SUSPENSION ABSORBER (GAS) (CE015) AND ONE (1) WBE BAGHOUSE (CE016) EXHAUSTING TO STACK SV013B, FURNACE WINDBOX EXHAUST (WBE) IS PART OF ONE (1) INDURATION MACHINE, CONISTING OF ONE (1) NATURAL GAS FIRED PELLET HARDENING FURNACE. WITH A MAXIMUM HEAT INPUT CAPACITY OF 436 MMBTU PER HOUR AND A MAXIMUM THROUGHPUT RATE OF 450 TONS PER HOUR OF IRON OXIDE PELLETS. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | A | GSA DRY SCRUBBER AND BAGHOUSE CE016 | 19.61 | LB/H | 3 HOURS | BACT-PSD |  | U | 95 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LIMIT ONE: 5.0 PPMV WET AT 15% O2 NOTE: 0.048 LB SO2/TON PELLETS * 450 TONS/HR = 21.6 LB/HR SO2
IN-0167 | MAGNETATION LLC | MAGNETATION LLC | WHITE | IN | 47980 | USA | MICHAEL TWITE | 2182593795 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: KRISTEN WILLOUGHBY 317-233-3031 KWILLOUGHBY@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 181-32081-00054 | 1011 | 212210 | 110055584363 | 07/02/2012 &nbsp;ACT | 04/16/2013 &nbsp;ACT | 2013-08-16 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32081F.PDF | IRON ORE CONCENTRATE PELLETIZING PLANT |  | FURNACE HOOD EXHAUST | 11.31 | NATURAL GAS | 436 | MMBTU/H | IDENTIFIED AS EU013, USING BAGHOUSE CE013, EXHAUSTS TO STACK SV013A, ONE (1) FURNACE HOOD EXHAUST IS PART OF ONE (1) INDURATION MACHINE. CONSISTING OF ONE (1) NATRUAL GAS FIRED PELLET HARDENING FURNACE, WITH A MAXIMUM HEAT INPUT CAPACITY OF 436 MMBTU PER HOUR AND A MAXIMUM THROUGHPUT RATE OF 450 TONS PER HOUR OF IRON OXIDE PELLETS. | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 21.68 | LB/H | 3 HOURS | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N |  | LIMIT ONE: 7.1 PPMV WET AT 20% O2 NOTE: 0.089 LB SO2/TON PELLETS * 450 TONS/HR = 40.1 LB/HR SO2
TX-0583 | MOUNTAIN CREEK STEAM ELECTRIC STATION | EXTEX LAPORTE LIMITED PARTNERSHIP | DALLAS | TX | 75211 | USA | GEROME RANDLE | (817) 446-2578 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | PSDTX1100 | 4911 | 221112 | 110015679443 | 07/19/2007 &nbsp;ACT | 01/12/2011 &nbsp;ACT | 2011-08-25 | 2011-09-14 | A |  | Construction Of Simple Cycle Gas Turbines 1 &amp; 2 |  | Simple Cycle Gas Turbines 1 &amp; 2 | 11.31 | Natural Gas | 0 |  |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | N |  | 64 | LB/H |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Pipeline quality natural gas only
LA-0238 | ALLIANCE REFINERY | CONOCOPHILLIPS COMPANY | PLAQUEMINES | LA | 70037 | USA | CHRIS CHANDLER | 5046567711 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: CORBET MATHIS - PHONE: 225-219-3181 | PSD-LA-75(M3) | 2911 | 324110 | 2207500003 | 01/22/2008 &nbsp;ACT | 07/10/2009 &nbsp;ACT | 2009-09-11 | 2012-05-18 | C |  | A PETROLEUM REFINERY IN BELLE CHASSE, LA. | PSD-LA-75 (OCTOBER 22, 1978): TO EXPAND THE FCCU CAPACITY FROM 78,000 TO 89,000 BPD. PSD-LA-75(M3): INCLUDING STARTUP SHUTDOWN EMISSIONS, RECONCILE SO2 AND CO EMISSIONS FROM HEATER AND BOILERS | CO BOILERS (2) | 11.31 | REFINERY GAS | 831.3 | MMBTU/H EACH |  | Sulfur Dioxide (SO2) | Unspecified | (InOrganic Compounds,Oxides of Sulfur (SOx)) | 2025884 | P | COMPLY WITH 40 CFR 60 SUBPART J | 1286 | LB/H | HOURLY MAXIMUM | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N