## All Pollutants_Large Boilers 11
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
LA-0323 | MONSANTO LULING PLANT | MONSANTO COMPANY | ST. CHARLES PARISH | LA | 70070 | USA | ENRIQUE WEHLEN | 9857858211 | ENRIGUE.WEHLEN@MONSANTO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-890 | 2879 | 325320 | 110067118274 | 09/21/2015 &nbsp;ACT | 01/09/2017 &nbsp;ACT | 2017-09-26 | 2018-05-11 | D | http://edms.deq.louisiana.gov/app/doc/view.aspx?doc=10460194&ob=yes | Chemical Manufacture | Dicamba Manufacturing Facility expansion project. | No. 9 Boiler - Natural Gas Fired | 11.31 | Natural Gas | 325 | MMBTU/h |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices and energy efficient operation | 0.167 | LB/LB | ANNUAL AVERAGE | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Units are lb of CO2e/lb of steam generated.
LA-0323 | MONSANTO LULING PLANT | MONSANTO COMPANY | ST. CHARLES PARISH | LA | 70070 | USA | ENRIQUE WEHLEN | 9857858211 | ENRIGUE.WEHLEN@MONSANTO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-890 | 2879 | 325320 | 110067118274 | 09/21/2015 &nbsp;ACT | 01/09/2017 &nbsp;ACT | 2017-09-26 | 2018-05-11 | D | http://edms.deq.louisiana.gov/app/doc/view.aspx?doc=10460194&ob=yes | Chemical Manufacture | Dicamba Manufacturing Facility expansion project. | No. 10 Boiler - Natural Gas Fired | 11.31 | Natural Gas | 325 | MMBTU/h |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Good combustion practices and energy efficient operation | 0.167 | LB/LB | ANNUAL AVERAGE | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Units are lb of CO2e/lb of steam generated.
LA-0311 | DONALDSONVILLE NITROGEN COMPLEX | CF INDUSTRIES NITROGEN, LLC | ASCENSION | LA | 70346 | USA | VALERIE KAZLAUSKAS | (225) 473-5585 | VKAZLAUSKAS@CFINDUSTRIES.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-772 | 2873 | 325311 | Not Found | 12/20/2012 &nbsp;ACT | 07/15/2013 &nbsp;ACT | 2017-03-10 | 2017-04-28 | B |  |  | Permit addresses the addition of the following new process units: No. 6 Ammonia Plant (1,460,000 TPY) No. 5 Urea Plant (1,405,250 TPY) No. 4 Nitric Acid Plant (657,000 TPY) No. 3 Urea Ammonium Nitrate Plant (1,788,500 TPY) | No. 6 Ammonia Plant Reformer (1-13, EQT 155) | 11.39 | Natural Gas | 2244.24 | MM Btu/hr | Reformer also fired with purge gas. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of natural gas as fuel and energy efficiency measures, including extended preheating of the hydrocarbon/steam feed, preheating of combustion air, energy efficient convection coil design, use of an improved CO2 removal system, use of smallest available catalyst particles in the ammonia converters, indirect cooling of the ammonia synthesis reactor, and hydrogen recovery from the purge gas of the ammonia synthesis loop. | 1.854 | LB/TON NH3 | ANNUAL AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit represents full range of operating conditions (&lsquo;&lsquo;routine&lsquo;&lsquo; and startup/shutdown operations).
AK-0083 | KENAI NITROGEN OPERATIONS | AGRIUM U.S. INC. | USA | AK | 99611 | USA | TED HARTMAN | 913 302 7469 | TED.HARTMAN@AGRIUM.COM | 10 | AK001 | ALASKA DEPT OF ENVIRONMENTAL CONS | MR. JIM PLOSAY | (907) 465-5103 | JOHN.KUTERBACH@ALASKA.GOV |  | AQ0083CPT06 | 2873 | 325311 | 110030488620 | 11/25/2014 &nbsp;ACT | 01/06/2015 &nbsp;ACT | 2015-01-29 | 2016-02-19 | A | http://dec.alaska.gov/Applications/Air/airtoolsweb/Home/ViewAttachment/16672291/KQZafTqmYd8SVnZ3RUWQfQ2 | The Kenai Nitrogen Operations Facility is located at Mile 21 of the Kenai Spur Highway, near Kenai Alaska. It is classified as a nitrogenous fertilizer manufacturing facility under Standard Industrial Classification code 2873 and under North American Industrial Classification code 325311. The facility will produce ammonia and urea for bulk sale. There are two ammonia and two urea plants at Agriumâ€™s KNO facility. This permit authorizes the restart of one ammonia and one urea plant (plants 4 and 5). The ammonia plant converts natural gas with added steam and air to produce ammonia (NH3) and carbon dioxide (CO2). Feedstocks for the urea plant include CO2 and NH3. The utility plant generates the power and steam needed to operate the ammonia and urea plants. Final products are loaded at the Product Loading Wharf for shipment. |  | Primary Reformer Furnace | 11.31 | Natural Gas, Process Gas | 1350 | MMBTU/H | Natural Gas-, Process Gas-Fired 1,350 MMBtu/hr Primary Reformer Furnace. Installed in 1976. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 59.61 | TONS/MMCF | 3-HR AVG | BACT-PSD |  | U | 0 | U | 700000 | TONS/YEAR |  | 0 |  |  | 0 | 0 | N
TX-0744 | C3 PETROCHEMICALS, PDH CHOCOLATE BAYOU PLANT | C3 PETROCHEMICALS LLC | BRAZORIA | TX | 77512-0711 | USA | RAY LEWIS | 281-228-4400 | RCLEWI1@ASCENDMATERIALS.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Bonnie Braganza, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, Tx 75202 | PSD-TX-1342-GHG | 2869 | 325110 | 110063953208 | 05/09/2014 &nbsp;ACT | 06/12/2014 &nbsp;ACT | 2015-05-29 | 2016-07-06 | B | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | C3P seeks authority to construct a new PDH plant for the production of propylene. The plant will use propane as its primary raw material. As part of the plant, C3P proposes to construct two parallel trains, each consisting of a charge heater, three interheaters, four reactors, feed exchangers, and a catalyst regeneration tower. The project will also require construction of feed driers, pretreatment units, separation units, a pressure swing adsorption unit, a cooling tower, and a ground flare, along with piping, compression, treatment and storage. | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions. See: CN604259192; RN106592579 | Boiler equipped with SCR and ultra-low NOx burners | 11.31 | Pipeline Nat Gas or Process Gas | 615 | MMBTU/H | Boiler is equipped with ultra low NOx burners using flue gas recirculation and fuel. Permittee is required to use insulation to minimize heat loss and maintain energy efficiency of the boilers. Economizer will be used to preheat boiler feedwater. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 82 | % THERMAL EFFICIENCY | 12-MONTH ROLLING TOTAL INCLUDES MSS | BACT-PSD |  | U | 82 | U | 330055 | TPY CO2E | 12-MONTH ROLLING TOTAL INCLUDES MSS | 0 |  |  | 0 | 0 | N |  | Permittee required to install, operate, and maintain an O2 analyzer on the boiler flue gas at a location downstream of the radiant sections of the boilers. Excess O2 shall be controlled to less than 3% when the operating load is 75% or greater to ensure efficiency on a 12-month rolling average basis. The oxygen analyzer shall continuously monitor and record the excess oxygen concentration in the combustion gases. Each boiler shall not exceed a one-hour maximum firing rate of 615 MMBtu/hr. The stack exhaust temperature, fuel temperature, ambient temperature and excess oxygen will be continuously monitored and averaged on a monthly basis to be used to calculate the thermal efficiency of each boiler. Thermal efficiency will be calculated using equation G-1 from API method 560 (4th ed.) Annex G. In accordance with 40 CFR 75.13(c) the permittee will determine the hourly CO2 conc and mass emissions with a flow monitoring system; a continuous O2 conc monitor, fuel F and Fc factors; and where O2 conc is measured on a dry basis, either a continuous moisture monitoring system or fuel specific default moisture percentage and by using the methods and procedures specified in 40 CFR Part 75.
TX-0744 | C3 PETROCHEMICALS, PDH CHOCOLATE BAYOU PLANT | C3 PETROCHEMICALS LLC | BRAZORIA | TX | 77512-0711 | USA | RAY LEWIS | 281-228-4400 | RCLEWI1@ASCENDMATERIALS.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Bonnie Braganza, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, Tx 75202 | PSD-TX-1342-GHG | 2869 | 325110 | 110063953208 | 05/09/2014 &nbsp;ACT | 06/12/2014 &nbsp;ACT | 2015-05-29 | 2016-07-06 | B | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | C3P seeks authority to construct a new PDH plant for the production of propylene. The plant will use propane as its primary raw material. As part of the plant, C3P proposes to construct two parallel trains, each consisting of a charge heater, three interheaters, four reactors, feed exchangers, and a catalyst regeneration tower. The project will also require construction of feed driers, pretreatment units, separation units, a pressure swing adsorption unit, a cooling tower, and a ground flare, along with piping, compression, treatment and storage. | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions. See: CN604259192; RN106592579 | Process Heaters | 11.31 |  | 0 |  |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 87 | % THERM EFF | 12-MONTH ROLLING TOTAL /TRAIN WITH MSS | BACT-PSD |  | U | 87 | U | 230308 | TPY CO2E | 12-MONTH ROLLING TOTAL /TRAIN WITH MSS | 0 |  |  | 0 | 0 | N |  | Additional BACT limit for excess oxygen to be limited to 3% or less. Pipeline Natural Gas only. The sum of the four heaters in the reactor train shall not exceed the one-hour maximum firing rate of 435 MMBtu/hr per reactor train. Oxygen analyzers are required to be used to monitor and record the excess oxygen concentration in the combustion gases. Heaters are required to be continuously monitored for exhaust temperature and stack oxygen. The thermal efficiency is calculated monthly by totalizing the fuel to the four heaters in each reactor train to determine heat input and the heat added to the process in each heater combined with the steam production to determine heat recovery. Thermal efficiency is calculated using equation G-1, API method 560 (4th ed) Annex G.
OK-0162 | ENID NITROGEN PLANT | KOCH NITROGEN CO LLC | GARFIELD | OK | 73701 | USA | MIKE KLEIS | 580-249-4830 | KLEISM@KOCHIND.COM | 6 | OK001 | OKLAHOMA DEPARTMENT OF ENVIRONMENTAL QUALITY | MR. LEE WARDEN | (405)702-4182 | LEE.WARDEN@DEQ.OK.GOV |  | 2011-441-C(M-2)PSD | 2873 | 325311 | 047-00008 | 03/20/2014 &nbsp;ACT | 05/29/2014 &nbsp;ACT | 2014-06-19 | 2016-05-04 | D |  | Koch Nitrogen Company (KNC) operates an ammonia products and nitrogen fertilizer plant (SIC 2873) located approximately five (5) miles east of Enid, Oklahoma. | Project includes enlarging two existing reformers, adding one (1) 450 MMBTUH gas-fired boiler, and construction of a new urea plant. | Boiler | 11.31 | Natural Gas | 450 | MMBTUH |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Efficient Design, Air Preheaters | 117 | LB/MMBTU |  | BACT-PSD | N/A | N | 0 | N | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0739 | AIR LIQUIDE, BAYOU COGENERATION PLANT | AIR LIQUIDE LARGE INDUSTRIES U.S., L.P. | HARRIS | TX | 77507 | USA | ASWATH KALAPPA | 713-402-2396 | ASWATH.KALAPPA@AIRLIQUIDE.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Aimee Wilson, US EPA Region 6, Air Permitting Section (6PD-R) 1445 Ross Avenue,Dallas, TX 75202 | PSD-TX-612-GHG | 4931 | 221112 | 110000462758 | 08/29/2013 &nbsp;ACT | 11/21/2013 &nbsp;ACT | 2015-05-28 | 2016-07-06 | D | http://yosemite.epa.gov/r6/Apermit.nsf/AirP#A | The redevelopment project at the Bayou Cogeneration Plant consists of replacing components of the power block and the boilers at the existing facility. | The Texas Commission on Environmental Quality (TCEQ) reviewed and issued the associated permitting action for the non-GHG emissions. CN600300693; RN100233998 | Boiler equipped with SCR | 11.31 | Pipeline Nat Gas and 90/10 blend | 550 | MMBTU/H | Startup begins at 60% loading and is limited to 240 minutes per event. Shutdown is limited to 60 minutes per event. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 117 | LB CO2/MMBTU | 12-MONTH ROLLING AVERAGE INCLUDES MSS | BACT-PSD |  | U | 0 | U | 485588 | TPY CO2E | 12-MONTH TOTAL, ROLLING MONTHLY | 0 |  |  | 0 | 0 | N |  | Fuel is limited to pipeline quality natural gas or a maximum 90/10 ratio of pipeline quality natural gas blended with off-gas based on annual average. CO2 CEMS and flow meters required. Emission limits include MSS. Each startup is limited to 240 min per event and each shutdown is limited to 60 minutes per event. Performance testing is required in accordance with 40 CFR 60.8 and Method 3a or 3b. Testing is not required for CH4 and N2O; however, the emissions are calculated to determine CO2e.
AL-0271 | GEORGIA PACIFIC BRETON LLC | GEORGIA PACIFIC LLC | ESCAMBIA | AL | 36427 | USA | ROBERTO FLORES | 251-867-8358 | ROBERTO.FLORES@GAPAC.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 502-0001-X049 | 2631 | 322130 | Unknown | 04/18/2014 &nbsp;ACT | 06/11/2014 &nbsp;ACT | 2014-07-11 | 2016-05-04 | D |  | Kraft Pulp &amp; Paper mdu | NAICS Code: 322130 | No.4 Power Boiler | 11.31 | Natural Gas | 425 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 117.1 | LB/MMBTU |  | BACT-PSD |  | U | 0 | N | 219214 | T/YR |  | 0 |  |  | 0 | 0 | N |  | Energy Efficient Practices
LA-0311 | DONALDSONVILLE NITROGEN COMPLEX | CF INDUSTRIES NITROGEN, LLC | ASCENSION | LA | 70346 | USA | VALERIE KAZLAUSKAS | (225) 473-5585 | VKAZLAUSKAS@CFINDUSTRIES.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-772 | 2873 | 325311 | Not Found | 12/20/2012 &nbsp;ACT | 07/15/2013 &nbsp;ACT | 2017-03-10 | 2017-04-28 | B |  |  | Permit addresses the addition of the following new process units: No. 6 Ammonia Plant (1,460,000 TPY) No. 5 Urea Plant (1,405,250 TPY) No. 4 Nitric Acid Plant (657,000 TPY) No. 3 Urea Ammonium Nitrate Plant (1,788,500 TPY) | No. 6 Ammonia Plant Boiler (15-13) and No. 5 Urea Boiler (23-13) (EQTs 165 &amp; 175) | 11.31 | Natural Gas | 612.4 | MM Btu/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Use of natural gas as fuel and energy efficiency measures, including annual tuning; use of economizers; optimization of combustion; instrumentation and controls (temperature sensors, oxygen trim systems); heating incoming combustion air with an air preheater; insulating boilers surfaces; reducing air leakages; employing a condensate return/recovery system; reducing slagging and fouling of heat transfer surfaces; a steam trap/valve maintenance program; good operating and maintenance practices (monitoring air-to-fuel ratio, regular inspections); and pursuing ANSI or ISO certification. | 191.7 | LB/1000 LB STEAM | ANNUAL AVERAGE | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Limit represents full range of operating conditions (&lsquo;&lsquo;routine&lsquo;&lsquo; and startup/shutdown operations).
TX-0741 | APEX BETHEL ENERGY CENTER | APEX BETHEL ENERGY CENTER, LLC | ANDERSON | TX | 75861 | USA | STEPHEN NAEVE | 713-963-8104 | STEPHEN.NAEVE@APEXCAES.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Bonnie Braganza; US EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, Texas 75202 | PSD-TX-104511-GHG | 4911 | 221112 | 110033246878 | 12/26/2014 &nbsp;ACT | 03/13/2014 &nbsp;ACT | 2015-05-29 | 2016-07-06 | A | http://yosemite.epa.gov/r6/Apermit.nsf/AirP |  | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emission associated with this project. See: RN10022223 | Gas Expansion Turbines, Trains A and B | 11.31 | Natural Gas | 42222262 | Btu/kWh (HHV, gross) | APEX has a total of 2 trains. The turbine trains have an estimated heat rate of 4,390 Btu/kWh at max load and 4773 Btu/kWh at low load (HHV). | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 558 | LB CO2/MWH | 365-DAY ROLLING AVERAGE INCLUDES MSS | BACT-PSD |  | U | 0 | U | 458769 | TPY CO2E | 12-MONTH ROLLING AVERAGE | 0 |  |  | 0 | 0 | N |  | Additional BACT limits: Maximum heat input to one train is 695.1 MMBtu/hr. Combustion Efficiency of 4773 Btu/kWh for all combustors on a 365-day rolling average; Good maintenance practices according to the vendor's recommendation attached to the permit; Insulation and maintenance of insulation on all combustors and recuperators for minimizing heat loss; process controls and instrumentation to optimize fuel/air ratios and minimize fuel gas use. Emission limits include MSS. Startup is limited to 30 min per event and shutdown is limited to 3.3 min per event. Planned startups shall not exceed 365 events per year per turbine train and shutdowns shall not exceed 365 per year per turbine train. CO2 CEMS is also required to be installed. To demonstrate compliance, the energy efficiency of the turbines is calculated to determine the 12-month rolling average. Performance testing is required initially and every five years for CO2 and the calculation of CH4, N2O and CO2e. Turbine is required to be tested at or above 90%, 50% and 10% of maximum load operations for the atm conditions which exist during testing. Each turbine train is required to install a recuperator to preheat the air entering the expander train.
TX-0742 | APEX MATAGORDA ENERGY CENTER | APEX MATAGORDA ENERGY CENTER, LLC | MATAGORDA | TX | 77414 | USA | STEPHEN NAEVE | 713-963-8104 | STEPHEN.NAEVE@APEXCAES.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV | EPA Region 6 Permit Writer: Bonnie Braganza, EPA Region 6, Air Permitting Section (6PD-R), 1445 Ross Avenue, Dallas, Texas 75202 | PSD-TX-107055-GHG | 4911 | 221112 | 110056411654 | 02/05/2014 &nbsp;ACT | 04/14/2014 &nbsp;ACT | 2015-05-29 | 2016-07-06 | U | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | Compressed Air Energy Storage Power Plant to produce up to 317 MW of electrical power. | The Texas Commission on Environmental Quality is the permitting authority for the non-GHG emissions associated with this project. | Gas Expansion Turbines, Trains A and B | 11.31 | Natural Gas | 7807409 | MMBtu per year |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 558 | LB CO2/MWH | 12-MONTH TOTAL ROLLING MONTHLY AVERAGE | BACT-PSD |  | U | 0 | U | 458734 | TPY CO2E | 12-MONTH TOTAL, ROLLING MONTHLY | 0 |  |  | 0 | 0 | N |  | Additional BACT Limits: Combustion efficiency of 4773 Btu/kWh for all combustors on a 12-month rolling average; good maintenance practices according to the vendor's recommendation attached to the permit; Insulation and maintenance of insulation on all combustors and recuperators for minimizing heat loss; process controls and instrumentation to optimize fuel/air ratios and minimize fuel gas use; maximum heat input to the turbine will not exceed 695 MMBtu/hr. Emission limits included MSS. 365 startups/shutdowns for each turbine per year. Each startup is limited to 30 per event and each shutdown is limited to 3 min per event. CO2 CEMS and fuel monitoring required. Performance testing is required initially and every 5 years for CO2 and calculations are required for CH4, N2O, and CO2e.Testing is required to be done at or above 90% of maximum load and between 50% and 10% of load operations.
KY-0106 | RIVERSIDE GENERATING CO LLC | RIVERSIDE GENERATING CO LLC | LAWRENCE | KY | 41129 | USA | STEVEN HOLBROOK | 6066861311 |  | 4 | KY001 | KENTUCKY DEP, DIV FOR AIR QUALITY | MR. RICK SHEWEKAH, MGR | (502)564-3999 | Sreenivas.Kesaraju@ky.gov |  | V-15-035 | 4911 | 221112 | 110012574071 | 09/20/2012 &nbsp;ACT | 09/30/2016 &nbsp;ACT | 2017-04-24 | 2017-04-28 | C |  | Riverside currently operates a simple cycle power plant consists of five (5) Siemens 501 FD2 turbines which began commercial operations in 2001 (Units 1-3) and 2002 (Units 4-5). The five Existing Natural Gas-Fired Turbines (EU 01 - 05) have the capacity to generate 180 MW each. This application is for the conversion of the simple cycle gas turbine electric generation units to combined-cycle gas turbine (CCGT) units for a new total generating capacity of approximately 1,700 MW. |  | Five Combined Cycle Generation Turbines (CCGT) with Duct burners and HRSG | 11.31 | Natural Gas | 1700 | MW | Five natural gas-fired turbines for electric generation, rated 2,076 MMBtu/hr each. New Project: Five Combined Cycle Generation Turbines (CCGT) (EU 01B-05B) - Five New Natural Gas-Fired Duct Burners for Five New Heat Recovery Steam Generators (HRSG) providing heat for Two New Steam Turbine Generators (STG) System (1) â€“ Three CTG/HRSG combined cycles to one STG System (2) â€“ Two CTG/HRSG combined cycles to one STG Maximum Rated Capacity: EU 01B-05B Duct Burners for HRSGs, 660 MMBtu/hr each STG, 3x1 â€“ 500MW, 2x1 â€“ 350 MW Construction Commenced: EU01B-05B proposed 2016 | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | The use of pipeline quality natural gas with a sulfur content of less than or equal to 1.0 grain/100 dscf | 1069 | LB/MWH | WITH DUCT BURNERS | BACT-PSD |  | U | 0 | U | 1076 | LB/MWH | WITHOUT DUCT BURNERS | 0 |  |  | 0 | 0 | N
TX-0749 | GOLDEN SPREAD ELECTRIC COOPERATIVE, ANTELOPE STATION | GOLDEN SPREAD ELECTRIC COOPERATIVE INC. | HALE | TX | 79311 | USA | JEFF PIPPIN | 806-418-3010 | JPIPPIN@GSEC.COOP | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | EPA Region 6 Permit Writer: Melanie Magee, EPA Region 6 (6PD-R), Dallas, Tx, 75202 | PSD-TX-1358-GHG | 4911 | 221112 | 110043432737 | 04/29/2014 &nbsp;ACT | 06/02/2014 &nbsp;ACT | 2015-06-19 | 2016-07-06 | B | http://yosemite.epa.gov/r6/Apermit.nsf/AirP | GSEC proposes to construct a gas turbine to expand capacity at an existing power plant (Antelope Elk Energy Center) located near Abernathy, Texas in Hale County. GSEC expects the proposed project to provide power generation support to wind energy resources in a primarily peaking and intermediate power generation operation, maintaining grid stability and meeting load when weather conditions are not conducive to wind energy production. With this proposed project, GSEC plans to construct a natural gas-fired simple cycle turbine GE Model 7F 5 Series and associated equipment, a diesel-fired emergency generator, a gas-fired fuel gas heater, and circuit breakers (not to exceed 2,920 lbs SF6). For the purposes of this proposed permitting action, GHG emissions are permitted from the turbine, its auxiliary fuel gas heater, the diesel emergency generator engine, fugitive emissions from circuit breakers and natural gas piping, and maintenance, startup, and shut down emissions. | TCEQ is the permitting authority for the non-GHG emissions. See: CN602667787 and RN105862510 | Simple Cycle Combustion Turbine | 11.31 | Pipeline Natural Gas | 0 |  | 202 (maximum gross) MW GE 7F 5-Series. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 1304 | LB CO2/MW-HR (GROSS) | 4572 OPERATIONAL HR ROLLING WITH MSS | BACT-PSD |  | U | 0 | U | 539094 | TPY CO2E | 12-MONTH ROLLING WITH MSS | 0 |  |  | 0 | 0 | N |  | BACT applies during all periods of turbine operation, including startup and shutdown. EPA is proposed an emission limit of 1,304 lb CO2/MWhr gross output on a 4,572 rolling operational hour basis. The turbine is limited to 4,572 hours of operation per year, including 635 startup and 635 shutdown events, on a 12-month rolling basis. -Startups are limited to no more than 30 minutes per event, and shutdowns are limited to no more than 24 minutes per event. - No more than 635 startup and 635 shutdown events may occur on a 12-month rolling basis. The fuel use limit for the combustion turbine that corresponds to the 4,572 hour of operation per 12-month rolling basis is 8,873,053 MMBtu (HHV). An initial stack test demonstration will be required for CO2 emissions from the combustion turbine.
*LA-0312 | ST. JAMES METHANOL PLANT | SOUTH LOUISIANA METHANOL LP | ST. JAMES | LA |  | USA | BRIAN JONES | (512) 394-7346 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Christopher Smith, (225) 219-3439 | PSD-LA-780(M-1) | 2869 | 325998 | Not Found | 09/30/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-03-10 | 2017-12-27 | A |  | New MeOH plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | New methanol plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | B2-13-SUSD - Boiler 2 Startup/Shutdown (EQT0006) | 11.31 | Natural Gas | 515 | MMBTU/hr | Max in any 24 hr period is 10776 MM BTU/day Operating hours limit: 144 hrs/yr | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Follow manufacturerâ€™s procedures for start-up and shutdown | 4339 | TPY |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0312 | ST. JAMES METHANOL PLANT | SOUTH LOUISIANA METHANOL LP | ST. JAMES | LA |  | USA | BRIAN JONES | (512) 394-7346 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Christopher Smith, (225) 219-3439 | PSD-LA-780(M-1) | 2869 | 325998 | Not Found | 09/30/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-03-10 | 2017-12-27 | A |  | New MeOH plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | New methanol plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | B1-13-SUSD - Boiler 1 Startup/Shutdown (EQT0005) | 11.31 | Natural Gas | 515 | MMBTU/hr | Max in any 24 hr period is 10776 MM BTU/day Operating hours limit: 144 hrs/yr | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Follow manufacturerâ€™s procedures for start-up and shutdown | 4339 | TPY |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Auxiliary Boiler | 11.31 | natural gas | 472.4 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Other - recordkeeping | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 51748 | TONS/YR | ROLLING 12 MONTH TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*ND-0033 | GRAND FORKS FERTILIZER PLANT | NORTHERN PLAINS NITROGEN | GRAND FORKS | ND | 58203 | USA | LARRY MACKIE |  | LARRYMACKIE@GMAIL.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV |  | PTC15052 | 2873 | 325311 |  | 01/20/2015 &nbsp;ACT | 08/10/2015 &nbsp;ACT | 2015-08-24 | 2015-08-24 | A | http://www.ndhealth.gov/AQ/ActivePermits.aspx | Fertilizer manufacturing plant designed to produce both feedstock and saleable products in the following nominal capacities: 2425 tpd ammonia, 2540 tpd ammonium nitrate solution, 300 tpd DEF, 3000 tpd urea solution, 3000 tpd granular urea, 2000 tpd nitric acid, 5620 tpd UAN, 441 tpd ammonium thiosulfate and 1080 tpd APP |  | Boilers | 11.31 | Natural gas | 187.5 | MMBTU/H | Facility includes 3 boilers of identical size (187.5 MM Btu/hr each) | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Fuel Efficiency Techniques | 59675 | TONS/YEAR CO2E | 12-MONTH ROLLING TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0108 | IOWA STATE UNIVERSITY POWER PLANT | IOWA STATE UNIVERSITY | STORY | IA | 50011 | USA | LINDSEY WANDERSCHEID | 515-291-0129 |  | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV |  | 13-137 | 8221 | 611310 | 110022692111 | 04/23/2013 &nbsp;ACT | 11/07/2013 &nbsp;ACT | 2015-01-16 | 2016-05-05 | D | https://programs.iowadnr.gov/airqualityconstructionpermits/Pages/ConstructionPermit/SearchResult.aspx | Steam and electrical generation for university campus |  | Boiler | 11.31 | natural gas | 213.6 | MMBTU/H | fuel oil backup for 200 hr/yr | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 113552 | TONS | 12-MONTH ROLLING TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
MN-0088 | SOUTHERN MINNESOTA BEET SUGAR COOPERATIVE | SOUTHERN MINNESOTA BEET SUGAR COOPERATIVE | RENVILLE | MN | 56284 | USA | LOUIS KNIEPER | 3203298305 | LOUIS.KNIEPER@SMBSC.COM | 5 | MN001 | MINNESOTA POLL CTRL AGCY, AIR QUAL DIV | MR. RICHARD CORDES | (651)757-2291 | RICHARD.CORDES@STATE.MN.US |  | 12900014-008 | 2063 | 311313 | 110000594811 | 09/20/2012 &nbsp;ACT | 05/22/2013 &nbsp;ACT | 2014-08-13 | 2016-05-05 | A |  | SOUTHERN MINNESOTA BEET SUGAR COOPERATIVE (SMBSC) PLANS TO INSTALL A NEW NATURAL GAS?FIRED BOILER (BOILER NO. 5) TO GENERATE STEAM TO DRIVE AN EXISTING ELECTRICITY GENERATOR. SMBSC MAY ALSO USE THE REDUCED PRESSURE STEAM FROM THE ELECTRICITY GENERATOR FOR OPERATIONS IN THE FACTORY. BOILER NO. 5 WILL HAVE A MAXIMUM RATE HEAT INPUT CAPACITY OF 257.3 MMBTU/HR AND WILL BE EQUIPPED WITH LOW?NOX BURNERS. THE NEW BOILER WILL ALLOW INCREASED THROUGHPUT OF SEVERAL EMISSION UNITS ABOVE HISTORICAL USAGE LEVELS, LEADING TO INCREASED EMISSIONS. SMBSC PROCESSES SUGAR FROM SUGAR BEETS FOR USE IN MANY CONSUMER FOOD PRODUCTS. THE ORIGINAL FACILITY WAS BUILT IN 1974. THE MAJOR SOURCES OF AIR EMISSIONS AT SMBSC CAN BE DIVIDED INTO TWO CATEGORIES: COMBUSTION SOURCES AND PRODUCT HANDLING SOURCES. COMBUSTION SOURCES INCLUDE THREE BOILERS AND TWO LIME KILNS. THE LARGEST BOILER IS CONTROLLED BY AN ELECTROSTATIC PRECIPITATOR AND THE LIME KILNS ARE UNCONTROLLED (ALTHOUGH THE COMBUSTION GAS IS USUALLY BUBBLED THROUGH THE CARBONATORS). PRODUCT HANDLING SOURCES INCLUDE SUGAR HANDLING AND CONVEYING EQUIPMENT ALONG WITH OTHER PRODUCT/RAW MATERIAL HANDLING EQUIPMENT. THE MAJORITY OF THE PRODUCT HANDLING SOURCES IS CONTROLLED BY BAGHOUSES. TWO UNITS ARE CONTROLLED BY SCRUBBERS. THE MAJOR SOURCE OF FUGITIVE EMISSIONS AT THE FACILITY IS TRUCK TRAFFIC. CO2E - 117,800 PM2.5 - 8.9 PM10 - 10 LEAD - 0.0 | CO2E - 117,800 PM2.5 - 8.9 PM10 - 10 LEAD - 0.0 | NATURAL GAS-FIRED BOILER | 11.31 | NATURAL GAS | 257.3 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | LIMITED TO NATURAL GAS BY DESIGN. REQUIRED TO BE EQUIPPED WITH AN ECONOMIZER AND AN OXYGEN TRIM SYSTEM. | 117800 | T/YR | 12-MONTH ROLLING | BACT-PSD | NSPS , OPERATING PERMIT | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | A TUNE-UP IS REQUIRED EVERY FIVE YEARS.
TX-0634 | LONE STAR NGL, MONT BELVIEU GAS PLANT | ENERGY TRANSFER PARTNERS, LP | CHAMBERS | TX | 77580 | USA | CLINT COWAN | 2104037670 | CLINT.COWAN@ENERGYTRANSFER.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV |  | PSD-TX-93813-GHG | 1321 | 211112 | Not Available | 12/07/2011 &nbsp;ACT | 10/12/2012 &nbsp;ACT | 2013-09-04 | 2014-01-07 | D |  |  | The facility will modify the existing fractionation (FRAC I) train and construct a second fractionation (FRAC II) train at the Mont Belvieu Gas Plant in Chambers County, Texas. The FRAC I and FRAC II trains are identical. The first stage in each fractionation train (FRAC J and FRAC II) is an amine unit. Both fractionation trains (FRAC I and FRAC IT) will employ a hot oil system that will provide heat to the process. | FRAC I and II Hot Oil Heaters | 11.31 | Natural Gas | 270 | MMBTU/H | 003-HOHTR and 013-HOHTR Each Fractionation train has one hot oil heater rated at 270 million British thermal units per hour (MMBtu/hr) (FRAC I- 003-HOHTR and FRAC II -013-HOHTR) and a molecular sieve regenerator heater rated at 46 MMBtu (FRAC I - 003- RGNHTR and FRAC II - 013-RGNHTR). Both process heaters, in each fractionation train (FRAC I and FRAC II),will be ducted to a common stack that will be equipped with Selective Catalytic Reduction (SCR) technology (003-SCR and 013-SCR, respectively). | Carbon Dioxide Equivalent (CO2e) | Other - 40 CFR Part 98, Subpart A, Table A-1 | (Greenhouse Gasses (GHG)) | CO2e | N |  | 138078 | T/YR | 12-MONTH ROLLING BASIS | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ND-0032 | SPIRITWOOD NITROGEN PLANT | CHS, INC. | STUTSMAN | ND | 58481 | USA | AJIT VENKATRAMAN |  | AJIT.VENKATRAMAN@CHSINC.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV |  | PTC14027 | 2873 | 325311 | Not Found | 09/19/2013 &nbsp;ACT | 06/20/2014 &nbsp;ACT | 2014-10-24 | 2017-06-28 | A | http://www.ndhealth.gov/EHS/FOIA/AQPermits/AQPermitConstruction.aspx | Fertilizer manufacturing plant to manufacture nitrogen-based products ammonia, urea, urea ammonium nitrate (UAN) and diesel exhaust fluid. The facility will produce both feedstock and saleable products in the following capacities: 2,425 tpd ammonia; 3,000 tpd urea solution; 3,000 tpd granular urea; 835 tpd nitric acid and 2,000 tpd UAN. |  | Package boiler | 11.31 | Natural gas | 280 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 143501 | TONS | 12-MONTH ROLLING TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
NE-0054 | CARGILL, INCORPORATED | CARGILL, INCORPORATED | WASHINGTON | NE | 68008 | USA | MICHELLE BUCKLIN | 4024714204 | MICHELLE_BUCKLIN@CARGILL.COM | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | 12-042 | 2046 | 311221 | Not Found | 11/09/2012 &nbsp;ACT | 09/12/2013 &nbsp;ACT | 2012-10-24 | 2017-06-28 | B |  |  |  | Boiler K | 11.31 | natural gas | 300 | mmbtu/h |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | good combustion practices | 153743 | TON/YEAR | 12-CONSECUTIVE MONTH ROLLING SUM | BACT-PSD |  | U | 0 | U | 178 | LB/1,000 LB STEAM | 12-CONSECUTIVE MONTH ROLLING AVERAGE | 0 |  |  | 0 | 0 | N |  | The 178 lbs / 1,000 lbs steam emission limit is only applicable to CO2, not CO2e.
*LA-0312 | ST. JAMES METHANOL PLANT | SOUTH LOUISIANA METHANOL LP | ST. JAMES | LA |  | USA | BRIAN JONES | (512) 394-7346 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Christopher Smith, (225) 219-3439 | PSD-LA-780(M-1) | 2869 | 325998 | Not Found | 09/30/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-03-10 | 2017-12-27 | A |  | New MeOH plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | New methanol plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | B1-13 - Boiler 1 (EQT0003) | 11.31 | Natural Gas | 350 | MM BTU/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy Efficiency Measures: | 179511 | TON/YEAR |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.05 | TON CO2E/TON MEOH |  | 0 |  |  | 0 | 0 | N |  | 1.05 Ton CO2e/Metric Ton of MeOH produced
*LA-0312 | ST. JAMES METHANOL PLANT | SOUTH LOUISIANA METHANOL LP | ST. JAMES | LA |  | USA | BRIAN JONES | (512) 394-7346 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Christopher Smith, (225) 219-3439 | PSD-LA-780(M-1) | 2869 | 325998 | Not Found | 09/30/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-03-10 | 2017-12-27 | A |  | New MeOH plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | New methanol plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | B2-13 - Boiler 2 (EQT0004) | 11.31 | Natural Gas | 350 | MM BTU/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures | 179511 | TPY |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 1.05 | TON CO2E/TON MEOH |  | 0 |  |  | 0 | 0 | N |  | 1.05 Ton CO2e/Metric Ton of MeOH produced
TX-0806 | PORT ARTHUR ETHANE SIDE CRACKER | TOTAL PETROCHEMICALS AND REFINING USA INC. | JEFFERSON | TX |  | USA | DON CLAUSON | 281-476-3811 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Daniel Guthrie, (512) 239-1319, Daniel.Guthrie@tceq.texas.gov | GHGPSDTX114, 122353, PSDTX1426 | 2869 | 325110 | 110059190021 | 05/19/2016 &nbsp;ACT | 07/22/2016 &nbsp;ACT | 2016-07-21 | 2017-11-16 | B |  | Ethylene Production |  | Pyrolysis Furnaces (7) | 11.31 | natural gas | 4000000000 | SCF/YR | information per furnace | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Low carbon fuel, good combustion practices | 192399 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emissions information per furnace
IA-0106 | CF INDUSTRIES NITROGEN, LLC - PORT NEAL NITROGEN COMPLEX | CF INDUSTRIES NITROGEN, LLC | WOODBURY | IA | 51054 | USA | MIKE MAAS | 712-233-6222 | MMAAS@CFINDUSTRIES.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | Christopher A. Roling, PE Environmental Engineer Senior Iowa DNR - Air Quality Bureau 7900 Hickman Rd, Suite 1 Windsor Heights, IA 50324 (515) 242-6002 chris.roling@dnr.iowa.gov | PN 13-037 | 2873 | 325311 | 110000414089 | 02/01/2013 &nbsp;ACT | 07/12/2013 &nbsp;ACT | 2013-07-16 | 2016-05-04 | B |  | Nitrogenous fertilizer manufacturing including ammonia, urea, and urea-ammonium nitrate (UAN) solutions. |  | Boilers | 11.31 | natural gas | 456 | MMBTU/H | There are two (2) identical boilers | Carbon Dioxide Equivalent (CO2e) | Other - calculation based on mass emissions and GWP | (Greenhouse Gasses (GHG)) | CO2e | P | proper operation and use of natural gas | 234168 | TONS/YR | ROLLING TWELVE (12) MONTH TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0640 | EQUISTAR CHEMICALS, LP LA PORTE COMPLEX | EQUISTAR CHEMICALS, LP | HARRIS | TX | 77571-9810 | USA | FOURTNEY F. RUTH | 713 336 5475 | COURTNEY.RUTH@LYONDELLBASELL.COM | 6 | OT007 | EPA REGION VI | MS. ASHLEY MOHR | (214) 665-7289 | MOHR.ASHLEY@EPA.GOV |  | PSD-TX-752-GHG | 2869 | 325110 |  | 06/29/2012 &nbsp;ACT | 03/14/2013 &nbsp;ACT | 2013-11-20 | 2014-03-28 | D |  | The proposed modification will add two new cracking furnaces and associated equipment to the existing Olefin unit (QE-1) at the La Porte Complex in La Porte, Texas. The Olefins unit (QE-1) receives hydrocarbon feedstock where it is fed into pyrolysis furnaces. The pyrolysis furnaces, whjcb are fired on natural gas and/or process gas, heat the feedstock to a high temperature where it cracks and reforms as alkenes or olefins. The modification increases the plant nominal ethylene production capacity from 875,000 tpy to 1,280,000 tpy. This equates to approximately 405,000 tons per year nominal capacity to produce ethylene. The plant aiso produces other products at varying capacities, but ethylene is the predominant product. |  | Cracking Furnaces | 11.31 | Natural Gas and/or proces gas | 600 | MM BTU/HR | Two Cracking Furnaces (Combustion Units). Each furnace has a maxi mum rated capacit) of 600 MMBtu/hr, and will be equipped with a Selective Catalytic Reduction (SCR) system. FIN:QE1010B and QE1011B | Carbon Dioxide Equivalent (CO2e) | Other - 40 CFR Part 98, Subpart A, Table A-1 | (Greenhouse Gasses (GHG)) | CO2e | A | Selective Ctalytic Redction (SCR) system | 281766 | T/R | 12 MONTH ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | Emision Rate is for each of the two furnances.
*LA-0306 | TOPCHEM POLLOCK, LLC | TOPCHEM POLLOCK, LLC | GRANT | LA | 71467 | USA | RAIMONDAS PETREIKIS |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mrs. Mei Wu, (225) 219-3428 | PSD-LA-815 | 2873 | 325311 | 110000450681 | 03/31/2016 &nbsp;ACT | 12/20/2016 &nbsp;ACT | 2017-03-08 | 2017-12-29 | A |  | Ammonia Production Plant | Application Accepted Date reflects date of administrative completeness CO2e emissions from the entire facility are limited to 1.01 tons per metric ton of ammonia produced (annual average). To demonstrate compliance with this limit, the permittee shall record the ammonia production monthly. CO2e emissions shall be recorded in accordance with the Mandatory Reporting of Greenhouse Rule (40 CFR 98). All records shall be maintained onsite for at least five years and be available for inspection by LDEQ. | Primary Reformer Stack RS-16-1 (EQT029) | 11.31 | Natural gas | 337 | MM BTU/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measure | 363287 | T/YR | ANNUAL MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 111.72 kg/MM BTU of CO2, 0.001 kg/MM BTU of CH4, and 0.0001 kg/MM BTU of N2O
WY-0076 | ROCK SPRINGS FERTILIZER COMPLEX | SIMPLOT PHOSPHATES, LLC | SWEETWATER | WY | 82901 | USA | DARIN HOWE | 3073821519 | DARIN.HOWE@SIMPLOT.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | MD-14824 | 2874 | 325312 | 110040924033 | 11/13/2013 &nbsp;ACT | 07/01/2014 &nbsp;ACT | 2014-07-01 | 2016-01-08 | B |  | Phosphate fertilizer Plant | Installation of an anhydrous ammonia plant with a nominal production capacity of 600 short tons per day (t/day) | Reformer/PSA Unit | 11.31 | natural gas | 384 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | energy efficiency | 398296 | T/YR | 12-MONTH ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0669 | APEX MATAGORDA ENERGY CENTER | APEX MATAGORDA ENERGY CENTER, LLC | MATAGORDA COUNTY | TX | 77027 | USA | STEPHEN NAEVE | 7139638104 | STEPHEN.NAEVE@APEXCAES.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | EPA REgion 6 Bonnie Braganza | PSD-TX-107055-GHG |  | 221119 |  | &nbsp; | 04/14/2014 &nbsp;ACT | 2015-02-12 | 2016-07-07 | A |  | The project proposes to construct a bulk energy storage system that will use compressed air energy storage (CAES) to produce up to 317 MW of electrical power. | the facility will consist of two expansion turbine generating trains each rated at 158.34 MW. GHG pollutants occur primarily from the exhaust emissions from the natural gas combustion turbine trains with minor emissions from fugitive sources and an emergency generator engine. | Combined Gas Expansion Turbine train A and B | 11.31 |  | 8600 | scf/hr |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | N |  | 456296 | TONS PER YEAR |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ND-0032 | SPIRITWOOD NITROGEN PLANT | CHS, INC. | STUTSMAN | ND | 58481 | USA | AJIT VENKATRAMAN |  | AJIT.VENKATRAMAN@CHSINC.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV |  | PTC14027 | 2873 | 325311 | Not Found | 09/19/2013 &nbsp;ACT | 06/20/2014 &nbsp;ACT | 2014-10-24 | 2017-06-28 | A | http://www.ndhealth.gov/EHS/FOIA/AQPermits/AQPermitConstruction.aspx | Fertilizer manufacturing plant to manufacture nitrogen-based products ammonia, urea, urea ammonium nitrate (UAN) and diesel exhaust fluid. The facility will produce both feedstock and saleable products in the following capacities: 2,425 tpd ammonia; 3,000 tpd urea solution; 3,000 tpd granular urea; 835 tpd nitric acid and 2,000 tpd UAN. |  | Primary reformer | 11.31 | Natural gas | 788 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy efficiency measures | 509665 | TONS | 12-MONTH ROLLING TOTAL | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*ND-0033 | GRAND FORKS FERTILIZER PLANT | NORTHERN PLAINS NITROGEN | GRAND FORKS | ND | 58203 | USA | LARRY MACKIE |  | LARRYMACKIE@GMAIL.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV |  | PTC15052 | 2873 | 325311 |  | 01/20/2015 &nbsp;ACT | 08/10/2015 &nbsp;ACT | 2015-08-24 | 2015-08-24 | A | http://www.ndhealth.gov/AQ/ActivePermits.aspx | Fertilizer manufacturing plant designed to produce both feedstock and saleable products in the following nominal capacities: 2425 tpd ammonia, 2540 tpd ammonium nitrate solution, 300 tpd DEF, 3000 tpd urea solution, 3000 tpd granular urea, 2000 tpd nitric acid, 5620 tpd UAN, 441 tpd ammonium thiosulfate and 1080 tpd APP |  | Ammonia Plant Primary Reformer | 11.31 | Natural gas | 1006 | MMBTU/H |  | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Energy Efficiency Measures | 515778 | TONS/YEAR CO2E | 12-MONTH ROLLING TOTAL | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0774 | BISHOP FACILITY | TICONA POLYMERS, INC. | NUECES | TX |  | USA | WILLIAM CHIDESTER | (361) 584-6614 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Daniel Guthrie (512) 239-1319 daniel.guthrie@tceq.texas.gov | 123216, PSDTX1438 AND GHGPSDTX | 2869 | 325199 | 110031352649 | 08/28/2015 &nbsp;ACT | 11/12/2015 &nbsp;ACT | 2015-11-09 | 2016-07-06 | B |  | Methanol Synthesis Plant |  | Reformer | 11.31 | natural gas | 1190 | MMBTU/H | Primary reformer for methanol production process which utilizes steam methane and auto-thermal reforming technologies. | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Firing of pipeline quality natural gas and high hydrogen process gas. CO2eq (CH4, N2O, and CO2) emissions are controlled through heat integration and best management practices. | 533629 | TPY |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0814 | AMMONIA AND UREA PLANT | AGRIUM US, INC | HUTCHINSON | TX |  | USA | JOSH REGAN | (806) 468-0605 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ramiro Cruz, (512)239-1302, Ramiro.Cruz@tceq.texas.gov | 19778 AND GHGPSDTX155 | 2873 | 325311 | Not Found | 11/04/2016 &nbsp;ACT | 01/05/2017 &nbsp;ACT | 2017-01-17 | 2017-11-16 | C |  | Anhydrous Ammonia and Urea Manufacturing Plant |  | Reformer Furnace 101-B | 11.31 | NATURAL GAS | 9636000 | MMBTU/YR | 1100 MMBTU/HR | Carbon Dioxide Equivalent (CO2e) | Unspecified | (Greenhouse Gasses (GHG)) | CO2e | P | Agrium uses good engineering practices to minimize CO2 e emissions. | 564019 | T/YR |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*TX-0644 | EQUISTAR CHEMICALS, LP - CHANNELVIEW NORTH PLANT | EQUISTAR CHEMICALS, LP (EQUISTAR) | HARRIS | TX | 77530 | USA | MICHAEL VANDERSNICK | 281-860-5050 | VANDERSNICK@LYONDELLBASELL.COM | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov |  | PSD-TX-1280-GHG | 2869 |  |  | 08/14/2012 &nbsp;ACT | 02/14/2013 &nbsp;ACT | 2014-02-05 | 2016-10-13 | D |  | Equistar is proposing to restart the methanol unit (MeOH Restart Project) at the Channelview North Plant. As part of the MeOH Restart Project, Equistar is proposing to transfer the existing equipment from Highly Purified Isobutylene (HPIB) production back to MeOH production. |  | Reformer Furnace (Combustion Unit). | 11.31 | Natural gas or high hydrogen fuel gas | 1615 | MMBTU/H | The furnace has a maximum design heat input rate of l,615MMbtu/hr, and will be equipped with a Selective Catalytic Reduction (SCR) system and low NOx burners. | Carbon Dioxide Equivalent (CO2e) | Other - Eq. C-5 in 40 CFR Part 98 Subpart C | (Greenhouse Gasses (GHG)) | CO2e | A | Selective Catalytic Reduction (SCR) system and low NOx burners. | 826600 | T/YR | 365 ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT requirements: Furnace Gas Exhaust Temperature 320 F . Maintain Thermal Efficiency of 90%. See permit condition IV.A.l.o.through q.