## All Pollutants_Large Boilers 11
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
AL-0251 | HILLABEE ENERGY CENTER | CER GENERATION | TALLAPOOSA | AL |  | USA | TONY DIEMEL | 4136150637 | TONY.W.DIEMEL@CONSTELLATION.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US | AMY GRAHAM (334) 271-7867 | 310-0022-X001 | 4911 | 221119 | not found | 07/09/2008 &nbsp;ACT | 09/24/2008 &nbsp;ACT | 2011-03-22 | 2015-02-09 | A |  | ENERGY PLANT |  | FUEL HEATER | 11.31 | NATURAL GAS | 11640000 | BTU |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNER | 0.013 | LB/MMBTU |  | BACT-PSD |  | U | 0 | N | 1.6 | LB/H |  | 0 |  |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT IP04 | 11.31 | NATURAL GAS | 16.7 | MMBTU/H | UNIT IP04 IS A KEWANEE BOILER AT IMPERIAL PALACE. UNIT IP04 IS IDENTICAL TO UNIT IP05. EITHER BOILER IS ALLOWED TO OPERATE UP TO 8,760 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER | 0.049 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 40.2 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0049 | LB/MMBTU |  | 0 | 0 | N
AL-0271 | GEORGIA PACIFIC BRETON LLC | GEORGIA PACIFIC LLC | ESCAMBIA | AL | 36427 | USA | ROBERTO FLORES | 251-867-8358 | ROBERTO.FLORES@GAPAC.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 502-0001-X049 | 2631 | 322130 | Unknown | 04/18/2014 &nbsp;ACT | 06/11/2014 &nbsp;ACT | 2014-07-11 | 2016-05-04 | D |  | Kraft Pulp &amp; Paper mdu | NAICS Code: 322130 | No.4 Power Boiler | 11.31 | Natural Gas | 425 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burner with FGR | 0.02 | LB/MMBTU |  | BACT-PSD | MACT | U | 50 | N | 8.5 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Low NOx Burner with FGR
TX-0650 | DIRECT REDUCED IRON AND HOT BRIQUETTING FACILITY | VOESTALPINE TEXAS LLC | SAN PATRICIO | TX |  | USA | MATTHIAS PASTL | 361-452-0746 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Dois Webb, Phone: 512-239-1575 e-mail: dois.webb@tceq.texas.gov | 108113/PSDTX1344 | 3312 | 331111 | UNKNOWN | 02/05/2013 &nbsp;ACT | 03/18/2014 &nbsp;ACT | 2014-03-27 | 2016-07-29 | A |  | Converts iron ore pellets into iron briquettes |  | GAS REFORMER | 11.31 | NATURAL GAS | 1591 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNERS | 0.058 | LB/MMBTU |  | BACT-PSD | NSPS , NESHAP , MACT , SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AR-0094 | JOHN W. TURK JR. POWER PLANT | SOUTHWEST ELECTRIC POWER COMPANY | FULTON | AR | 71838 | USA | KRIS GAUS | 214771113 | KPGAIS@AEP.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2123-AOP-R0 | 4911 | 221112 | UNKNOWN | 07/08/2008 &nbsp;ACT | 11/05/2008 &nbsp;ACT | 2009-01-09 | 2010-04-09 | A |  | 600 MW POWDER RIVER BASIN SUB-BITUMINOUS PULVERIZED COAL FIRED POWER PLANT | PSD AND 112(G) PERMIT DECISION | AUXILIARY BOILER | 11.31 | NATURAL GAS | 555 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNERS | 0.11 | LB/MMBTU | 30 DAY ROLLING AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Auxiliary Boiler | 11.31 | natural gas | 472.4 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners (LNB) and Flue Gas Recirculation (FGR) | 0.0125 | LB/MMBTU | ROLLING 30 DAY AVERAGE | BACT-PSD |  | U | 0 | U | 5.52 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
WY-0074 | GREEN RIVER SODA ASH PLANT | SOLVAY CHEMICALS | SWEETWATER | WY | 82935 | USA | TIM BROWN | 3078726570 | TIM.BROWN@SOLVAY.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | MD-13083 | 1474 | 212391 | 110007899248 | 08/06/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2013-11-18 | 2016-05-04 | B |  | Trona Mine and Refinery | Installation of a 254 million British thermal unit per hour (MMBtu/hr) natural gas fired package boiler to provide steam and heat to the facilities production processes, installation of a clear liquor heat exchanger, and other minor operational and equipment changes to debottleneck production. | Natural Gas Package Boiler | 11.31 | Natural Gas | 254 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | low NOx burners and flue gas recirculation | 0.011 | LB/MMBTU | 30-DAY ROLLING | BACT-PSD | NSPS , NESHAP | N | 0 | U | 2.8 | LB/H | 30-DAY ROLLING | 0 |  |  | 8802 | 8802 | N | 2013
NE-0054 | CARGILL, INCORPORATED | CARGILL, INCORPORATED | WASHINGTON | NE | 68008 | USA | MICHELLE BUCKLIN | 4024714204 | MICHELLE_BUCKLIN@CARGILL.COM | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | 12-042 | 2046 | 311221 | Not Found | 11/09/2012 &nbsp;ACT | 09/12/2013 &nbsp;ACT | 2012-10-24 | 2017-06-28 | B |  |  |  | Boiler K | 11.31 | natural gas | 300 | mmbtu/h |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNERS AND INDUCED FLUE GAS RECIRCULATION | 0.04 | LB/MMBTU | 30-DAY ROLLING AVERAGE | BACT-PSD | NSPS | U | 0 | U | 12 | LB/H | 3-HOUR ROLLING AVERAGE | 0 |  |  | 0 | 0 | N
IN-0167 | MAGNETATION LLC | MAGNETATION LLC | WHITE | IN | 47980 | USA | MICHAEL TWITE | 2182593795 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: KRISTEN WILLOUGHBY 317-233-3031 KWILLOUGHBY@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 181-32081-00054 | 1011 | 212210 | 110055584363 | 07/02/2012 &nbsp;ACT | 04/16/2013 &nbsp;ACT | 2013-08-16 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32081F.PDF | IRON ORE CONCENTRATE PELLETIZING PLANT |  | FURNACE WINDBOX EXHAUST (WBE) | 11.31 | NATURAL | 436 | MMBTU/H | IDENTIFIED AS EU014 USING ONE (1) GAS SUSPENSION ABSORBER (GAS) (CE015) AND ONE (1) WBE BAGHOUSE (CE016) EXHAUSTING TO STACK SV013B, FURNACE WINDBOX EXHAUST (WBE) IS PART OF ONE (1) INDURATION MACHINE, CONISTING OF ONE (1) NATURAL GAS FIRED PELLET HARDENING FURNACE. WITH A MAXIMUM HEAT INPUT CAPACITY OF 436 MMBTU PER HOUR AND A MAXIMUM THROUGHPUT RATE OF 450 TONS PER HOUR OF IRON OXIDE PELLETS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX LE NATURAL GAS BURNERS | 0.25 | LB/MMBTU | 3 HOURS | BACT-PSD |  | U | 0 | U | 109 | LB/H | 3 HOURS | 0 |  |  | 0 | 0 | N |  | LIMIT TWO: COMBINED EMISSIONS FROM SV013A AND SV013B. NOTE: 0.249 LB NOX/MMBTU * 436 MMBTU/HR = 109 LB/HR NOX
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT HA08 | 11.31 | NATURAL GAS | 8.37 | MMBTU/H | THE EMISSION UNIT IS A CLEAVER BROOKS BOILER AT HARRAH'S LAS VEGAS. UNIT HA08 IS IDENTICAL TO HA09 AND HA10. THE SAME SET OF EMISSION LIMITS APPLIES TO EACH OF THE THREE BOILERS. THE THREE BOILERS ARE SUBJECT TO THE LIMIT OF TOTAL ANNUAL OPERATING TIME FOR 20,000 HOURS PER YEAR. THERE ARE NO BOILERS AT HARRAH'S LAS VEGAS, WHICH HAS A THROUGHPUT CAPACITY IN EXCESS OF 10 MMBTU/HR. NO BACT DETERMINATIONS FOR ANY EMISSION UNITS AT BILL'S GAMBLIN' HALL & SALON ARE REPORTED HEREIN BECAUSE ALL OF THEM HAVE A VERY SMALL POTENTIAL TO EMIT FOR ANY POLLUTANT. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOX BURNER | 0.0146 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 12 | PPMVD | CORRECTED AT 3% OXYGEN | 0.0146 | LB/MMBTU |  | 0 | 0 | N
IN-0234 | GRAIN PROCESSING CORPORATION | GRAIN PROCESSING CORPORATION | DAVIESS | IN | 47501 | USA | WENDY BOUVIER | 8122572759 | WENDY.BOUVIER@GRAINPROCESSING.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | MADHURIMA MOULIK 317-233-0868 JASON KRAWCZYK, SECTION CHIEF IDEM OFFICE OF AIR QUALITY 100 N. SENATE AVENUE 317-234-5174 | 027-35177-00046 | 2046 | 311221 | 110041204265 | 11/26/2014 &nbsp;ACT | 12/08/2015 &nbsp;ACT | 2016-02-25 | 2016-07-06 | B | HTTP:PERMITS.AIR.IDEM.IN.GOV/35177F.PDF | THIS FACILITY IS A STATIONARY CORN WET MILLING PLANT. |  | BOILER 1 | 11.31 | NATURAL GAS | 271 | MMBTU/H | NATURAL GAS FIRED, ALSO CAPACBLE OF BURNING ALCOHOL. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW-NOX BURNER AND FLUE GAS RECIRCULATION SYSTEM | 0.05 | LB/MMBTU | NORMAL OPERATION | BACT-PSD |  | N | 0 | U | 0.2 | LB/MMBTU | DURING SSM | 0 |  |  | 0 | 0 | N |  | NOX EMISSIONS SHALL NOT 13.6 LB/HR DURING NORMAL OPERATION AND 54.2 LB/HR DURING START-UP, SHUTDOWN AND MALFUNCTION.
IN-0234 | GRAIN PROCESSING CORPORATION | GRAIN PROCESSING CORPORATION | DAVIESS | IN | 47501 | USA | WENDY BOUVIER | 8122572759 | WENDY.BOUVIER@GRAINPROCESSING.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | MADHURIMA MOULIK 317-233-0868 JASON KRAWCZYK, SECTION CHIEF IDEM OFFICE OF AIR QUALITY 100 N. SENATE AVENUE 317-234-5174 | 027-35177-00046 | 2046 | 311221 | 110041204265 | 11/26/2014 &nbsp;ACT | 12/08/2015 &nbsp;ACT | 2016-02-25 | 2016-07-06 | B | HTTP:PERMITS.AIR.IDEM.IN.GOV/35177F.PDF | THIS FACILITY IS A STATIONARY CORN WET MILLING PLANT. |  | BOILER 2 | 11.31 | NATURAL GAS | 271 | MMBTU/H | NATURAL GAS BOILER WITH CAPABILITY OF BURNING ALCOHOL | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW-NOX BURNERS AND FLUE GAS RECIRCULATION | 0.05 | LB/MMBTU | NORMAL OPERATION | BACT-PSD |  | N | 0 |  | 0.2 | LB/MMBTU | DURING SSM | 0 |  |  | 0 | 0 | N |  | 13.6 LB/HR DURING NORMAL OPERATION, 54.2 LB/HR DURING START-UP SHUTDOWN AND MALFUNCTION
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Boiler | 11.31 | natural gas | 864 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | low-nox burners, scr (or equivalent) | 0.012 | LB/MMBTU | 30-DAY AVERAGE ROLLED DAILY | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0167 | MAGNETATION LLC | MAGNETATION LLC | WHITE | IN | 47980 | USA | MICHAEL TWITE | 2182593795 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: KRISTEN WILLOUGHBY 317-233-3031 KWILLOUGHBY@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 181-32081-00054 | 1011 | 212210 | 110055584363 | 07/02/2012 &nbsp;ACT | 04/16/2013 &nbsp;ACT | 2013-08-16 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32081F.PDF | IRON ORE CONCENTRATE PELLETIZING PLANT |  | FURNACE HOOD EXHAUST | 11.31 | NATURAL GAS | 436 | MMBTU/H | IDENTIFIED AS EU013, USING BAGHOUSE CE013, EXHAUSTS TO STACK SV013A, ONE (1) FURNACE HOOD EXHAUST IS PART OF ONE (1) INDURATION MACHINE. CONSISTING OF ONE (1) NATRUAL GAS FIRED PELLET HARDENING FURNACE, WITH A MAXIMUM HEAT INPUT CAPACITY OF 436 MMBTU PER HOUR AND A MAXIMUM THROUGHPUT RATE OF 450 TONS PER HOUR OF IRON OXIDE PELLETS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOX LE NATURAL GAS BURNERS | 0.25 | LB/MMBTU | 3 HOURS | BACT-PSD |  | U | 0 | U | 109 | LB/H | 3 HOURS | 0 |  |  | 0 | 0 | N |  | LIMIT TWO: COMBINED EMISSIONS FROM SV013A AND SV013B
LA-0317 | METHANEX - GEISMAR METHANOL PLANT | METHANEX USA, LLC | ASCENSION | LA | 70734 | USA | GLYNN FONTENOT | 225-402-0301 | GFONTENOT@METHANEX.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: Dr. Qingming Zhang (225)-219-3457 | PSD-LA-761(M4) | 2869 | 325199 | 110046528227 | 09/09/2016 &nbsp;ACT | 12/22/2016 &nbsp;ACT | 2017-03-15 | 2017-04-28 | A |  | methanol plant (Unit I and Unit II) to produce 6000 metric tons of methanol by steam reforming natural gas | psd-la-761, issued 11/07/12, for relocation Unit I (3000 mt/yr) from punta arenas (chile); psd-la-761(M1), issued 07/12/13, for relocation Unit II (3000 mt/yr); psd-la-761(M2) (issued 01/15/16), psd-la-761(M3) (issued 01/14/16), and psd-la-761(M4) (issued 12/22/16) are for miscellaneous reconciliation | Steam methane reformers (I-H-101, II-H-101) | 11.31 | natural gas | 2364 | mm btu/hr |  | Nitrogen Oxides (NOx) | EPA/OAR Cond. Test Mthd 022 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 0.007 | LB/MM BTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT = LAER (Permit 0180-00210-V4, dated 12/22/2016)
TX-0656 | GAS TO GASOLINE PLANT | NATGASOLINE | JEFFERSON | TX |  | USA | KEVIN STRUVE |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Cheryl Covone 512-239-1248 | PSDTX1340 AND 107764 | 2911 | 325199 | 110064577006 | 01/16/2013 &nbsp;ACT | 05/16/2014 &nbsp;ACT | 2014-05-20 | 2016-05-12 | A |  | Chemical Plant |  | Boiler | 11.31 | natural gas and fuel gas | 950 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 0.01 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0305 | LAKE CHARLES METHANOL FACILITY | LAKE CHARLES METHANOL, LLC | CALCASIEU PARISH | LA | 70669 | USA | JOHN MCDANIEL | 318-308-0322 | JMCDANIEL@LAKECHARLESMETHANOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Dan Nguyen - (225)219-3395 | PSD-LA-803(M1) | 2869 | 325199 | 110067180366 | 06/16/2016 &nbsp;ACT | 06/30/2016 &nbsp;ACT | 2017-03-07 | 2017-04-28 | A |  | Proposed facility to produce methanol, H2, H2SO4, CO2, Argon and electricity from Pet Coke | PSD-LA-803 was issued 2/24/2016. The facility has not commence construction when Permit PSD-LA-803(M1) was issued. | Auxiliary Boilers and Superheaters | 11.31 | Natural Gas | 0 |  | Supplement fuel: fuel gas Boilers: 225 MM BTU/hr each | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 0.015 | LBS/MM BTU | 30 ROLLING AVG., EXCEPT SCR SU OR MAINT. | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ND-0032 | SPIRITWOOD NITROGEN PLANT | CHS, INC. | STUTSMAN | ND | 58481 | USA | AJIT VENKATRAMAN |  | AJIT.VENKATRAMAN@CHSINC.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV |  | PTC14027 | 2873 | 325311 | Not Found | 09/19/2013 &nbsp;ACT | 06/20/2014 &nbsp;ACT | 2014-10-24 | 2017-06-28 | A | http://www.ndhealth.gov/EHS/FOIA/AQPermits/AQPermitConstruction.aspx | Fertilizer manufacturing plant to manufacture nitrogen-based products ammonia, urea, urea ammonium nitrate (UAN) and diesel exhaust fluid. The facility will produce both feedstock and saleable products in the following capacities: 2,425 tpd ammonia; 3,000 tpd urea solution; 3,000 tpd granular urea; 835 tpd nitric acid and 2,000 tpd UAN. |  | Primary reformer | 11.31 | Natural gas | 788 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR & Low NOx burners | 0.02 | LB/MMBTU | 30 DAY ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CT-0156 | MONTVILLE POWER LLC | NRG ENERGY |  | CT | 6382 | USA | ROBERT SPOONER | 860-982-0459 | ROBERT.SPOONER@NRGENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | JAMES GRILLO (860) 424-4152 | 107-0056 | 4911 | 221119 | 900700108 | 05/11/2009 &nbsp;ACT | 04/06/2010 &nbsp;ACT | 2010-04-13 | 2013-05-30 | D |  | 43 MW STOKER FIRED BIOMASS; 82 MW TANGENTIALLY FIRED NATURAL GAS/ULS DISTILLATE UTILITY BOILER (7% ANNUAL CAPACITY FACTOR) |  | 82 MW Utility Boiler | 11.31 | Natural Gas | 995 | MMBTU/H | 7% annual capacity factor for distillate and natural gas firing. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR (Regenerative) | 0.06 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0245 | HYDROGEN PLANT | VALERO REFINING - NEW ORLEANS, LLC | ST. CHARLES | LA | 70079 | USA | ROBERT MARTIN | (985)764-8611 | ROB.MARTIN@VALERO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen - 225-219-3395 | PSD-LA-750 | 2911 | 324110 | Not Available | 08/18/2010 &nbsp;ACT | 12/15/2010 &nbsp;ACT | 2011-03-29 | 2011-07-06 | B |  | A plant to produce hydrogen by steam reforming natural gas. | Application Accepted Received Date = Date of completeness Determination | SMR Heaters (EQT0400 and EQT0401) | 11.31 | Fuel Gas | 1055 | MMBTU/H | Two identical units | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR and Ultra low NOX burner | 0.015 | LB/MMBTU | ANNUAL AVERAGE | BACT-PSD |  | U | 0 | U | 15.83 | LB/H | HOURLY MAXIMUM (EACH UNIT) | 0 |  |  | 0 | 0 | N
LA-0264 | NORCO HYDROGEN PLANT | AIR PRODUCTS AND CHEMICALS, INC. | ST. CHARLES | LA | 70079 | USA | DAN DILLER | 5042541590 | DILLERDJ@AIRPRODUCTS.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen | PSD-LA-750(M1) | 2813 | 325120 | 110000597140 | 02/29/2012 &nbsp;ACT | 09/04/2012 &nbsp;ACT | 2012-11-29 | 2013-09-06 | A |  | A new hydrogen plant (SMR) which was previously propoposed by Valero (LA-0245) |  | Reformer | 11.31 | fuel gas | 1320 | MMBTU/H | Supplement fuel: natural gas | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR and Ultra low NOX burner | 0.015 | LB/MMBTU | ANNUAL AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0.015 | LB/MMBTU | ANNUAL AVERAGE | 0 | 0 | N
TX-0659 | DEER PARK PLANT | ROHM AND HAAS TEXAS INC | HARRIS | TX |  | USA | HARRY ENGELHARDT | 281-228-8100 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX1320, 2165 | 2869 | 325188 | UNKNOWN | 10/12/2012 &nbsp;ACT | 12/20/2013 &nbsp;ACT | 2014-06-05 | 2016-07-29 | C |  |  |  | Boiler | 11.31 | Natural gas | 515 | MMBTU/H | Two (2) 515 MMBtu/hr boilers firing natural gas with refinery gas as a secondary fuel | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective catalytic reduction | 0.01 | LB/MMBTU | 1-HR | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0704 | UTILITY PLANT | M & G RESINS USA LLC | NUECES | TX |  | USA | MAURO FENOGLIO | (281) 874-8074 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 108819 PSDTX1354 | 4911 | 221112 | unknown | 02/22/2013 &nbsp;ACT | 12/02/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | In support of the new PET (polyethylene terephthalate) unit and new PTA (terephthalic acid) plant proposed by M&amp;G Resins USA LLC, the company also proposes a Utility Plant that will consist of either one of two options. All steam generated from the Utility Plant will be used as process steam. There is no steam driven electrical generator. |  | (2) boilers | 11.31 | natural gas | 450 | MMBTU/H | Auxiliary Boilers A1 and A2 are rated at 450 MMBtu/hr each. Auxiliary Boiler A1 and A2 were represented by the applicant to potentially operate 8,760 hours per year each. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 0.01 | LB/MMBTU | 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0704 | UTILITY PLANT | M & G RESINS USA LLC | NUECES | TX |  | USA | MAURO FENOGLIO | (281) 874-8074 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 108819 PSDTX1354 | 4911 | 221112 | unknown | 02/22/2013 &nbsp;ACT | 12/02/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | In support of the new PET (polyethylene terephthalate) unit and new PTA (terephthalic acid) plant proposed by M&amp;G Resins USA LLC, the company also proposes a Utility Plant that will consist of either one of two options. All steam generated from the Utility Plant will be used as process steam. There is no steam driven electrical generator. |  | boiler | 11.31 | natural gas | 250 | MMBTU/H | Auxiliary Boiler B is rated at 250 MMBtu/hr. Auxiliary Boiler B was represented by the applicant to potentially operate 8,760 hours per year. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 0.01 | LB/MMBTU | 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0707 | CHEMICAL MANUFACTURING FACILITY | ROHM AND HAAS TEXAS INCORPORATED | HARRIS | TX |  | USA | HARRY ENGLEHARDT | (281) 228-8100 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | 2165 PSDTX1320 | 2865 | 325110 | 110043790163 | 10/12/2012 &nbsp;ACT | 12/20/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | RH is proposing to install two 515 million British thermal unit per hour (MMBtu/hr) gas-fired boilers to produce additional steam for the RH Texas Deer Park Plant manufacturing facilities and give the plant the ability to perform planned maintenance on other steam producing equipment at the site without sacrificing peak steam production. The boilers will be authorized to fire natural gas and N-area absorber off-gas (off-gas). Each boiler will be equipped with a Selective Catalytic Reduction (SCR) system and Continuous Emission Monitoring System (CEMS). |  | (2) boilers | 11.31 | natural gas | 515 | MMBTU/H | RH is proposing to install two 515 million British thermal unit per hour (MMBtu/hr) gas-fired boilers. The boilers will be authorized to fire natural gas and N-area absorber off-gas (off-gas). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 0.01 | LB/MMBTU | 1 HOUR | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 10 ppm ammonia slip limit
*ND-0033 | GRAND FORKS FERTILIZER PLANT | NORTHERN PLAINS NITROGEN | GRAND FORKS | ND | 58203 | USA | LARRY MACKIE |  | LARRYMACKIE@GMAIL.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV |  | PTC15052 | 2873 | 325311 |  | 01/20/2015 &nbsp;ACT | 08/10/2015 &nbsp;ACT | 2015-08-24 | 2015-08-24 | A | http://www.ndhealth.gov/AQ/ActivePermits.aspx | Fertilizer manufacturing plant designed to produce both feedstock and saleable products in the following nominal capacities: 2425 tpd ammonia, 2540 tpd ammonium nitrate solution, 300 tpd DEF, 3000 tpd urea solution, 3000 tpd granular urea, 2000 tpd nitric acid, 5620 tpd UAN, 441 tpd ammonium thiosulfate and 1080 tpd APP |  | Ammonia Plant Primary Reformer | 11.31 | Natural gas | 1006 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction & Low NOx burners | 0.012 | LB/MM BTU | 30 DAY ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0815 | PORT ARTHUR ETHANE SIDE CRACKER | TOTAL PETROCHEMICALS & REFINING USA, INC. | JEFFERSON | TX |  | USA | DOROTHY BARTOL | (409) 963-6800 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Daniel Guthrie, (512) 239-1319, Daniel.Guthrie@tceq.texas.gov | 122353, PSDTX1426, GHGPSDTX114 | 2869 | 325110 | Not Found | 11/17/2016 &nbsp;ACT | 01/17/2017 &nbsp;ACT | 2017-01-18 | 2017-11-16 | B |  | Ethylene Production |  | Pyrolysis Furnaces | 11.31 | NATURAL GAS | 1000 | kT / YR | 7 furnaces | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction & Low NOx burners | 0.01 | LB/MMBTU |  | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0248 | DIRECT REDUCTION IRON PLANT | CONSOLIDATED ENVIRONMENTAL MANAGEMENT INC - NUCOR | ST JAMES PARISH | LA | 70723 | USA | STEVE ROWLAN | (704) 366-7000 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | KERMIT WITTENBURG, KERMIT.WITTENBURG@LA.GOV | PSD-LA-751 | 3312 | 331111 | 110037583442 | 10/31/2010 &nbsp;ACT | 01/27/2011 &nbsp;ACT | 2011-06-28 | 2011-12-08 | B |  | THE DRI PROCESS REDUCES THE IRON OXIDE CONTENT OF IRON ORE PELLETS INTO IRON METAL THROUGH DIRECT CONTACT WITH A REDUCING GAS. THE EFFECTIVENESS OF THIS REDUCTION PROCESS IS CALLED METALLIZATION, AND THE PROCESS EQUIPMENT WILL BE DESIGNED TO ACHIEVE A METALLIZATION RATE OF AT LEAST 92% OF THE OXIDES WITHIN THE ORE. THE REDUCTION WILL TAKE PLACE IN A COUNTERCURRENT VERTICAL SHAFT FURNACE, WHERE REDUCING GAS PASSES UP THROUGH IRON OXIDE PELLETS, WHICH FEED THROUGH THE FURNACE BY GRAVITY. THE MAJOR ELEMENTS OF THE DRI PROCESS INCLUDE THE FOLLOWING: (1) IRON OXIDE PREPARATION; (2) REDUCING GAS PREPARATION; (3) DRI REACTOR SHAFT FURNACE; (4) SPENT REDUCING GAS PREPARATION FOR REUSE, (5) DRI PRODUCT HANDLING; AND (6) ANCILLARY OPERATIONS, INCLUDING A PACKAGE BOILER, TWO COOLING TOWERS, AND A FLARE FOR EMERGENCY SITUATIONS. | ON 1/27/11, LDEQ ISSUED TO NUCOR TITLE V (TV) AND PSD PERMITS AUTHORIZING TWO DRI UNITS (MIDREX DESIGN). ON 9/29/11, NUCOR REQUESTED APPROVAL TO CONVERT ONE UNIT TO A DESIGN DEVELOPED BY TENOVA HYL. THE ONLY SIGNIFICANT DIFFERENCE BETWEEN THE MIDREX AND HYL DESIGNS IS THE POINT IN THE PROCESS WHERE NATURAL GAS IS REFORMED INTO CO & H2. LDEQ APPROVED NUCORâ€™S APPLICATION AND MODIFIED THE TV PERMIT ON 3/8/12. HOWEVER, LDEQ CONCLUDED THAT ITS INITIAL BACT DETERMINATIONS REMAINED APPROPRIATE AND DID NOT MODIFY THE PSD PERMIT. LDEQ SUBSEQUENTLY DECIDED TO REOPEN PSD-LA-751 FOR THE LIMITED PURPOSE OF CONFIRMING LDEQâ€™S INITIAL ASSESSMENT. LDEQ REQUIRED NUCOR TO PROVIDE AN ANALYSIS DEMONSTRATING THAT 1.) BACT FOR THE HYL EQUIPMENT IS NOT MORE STRINGENT THAN THAT PROVIDED BY PSD-LA-751, AND 2.) USE OF HYL EQUIPMENT IN ONE UNIT OF THE DRI FACILITY DOES NOT MATERIALLY CHANGE THE ORIGINAL AIR QUALITY ANALYSIS. LDEQ AGAIN CONCLUDED THAT NO CHANGES TO THE EXISTING BACT DETERMINATIONS WERE WARRANTED AND THAT THE HYL DESIGN DOES NOT RESULT IN ADVERSE AIR QUALITY IMPACTS. THEREFORE, LDEQ REVISED PSD-LA-751 ON 11/16/12 ONLY TO CLARIFY THAT IT COVERS THE HYL (I.E., IN SITU REFORMING) EQUIPMENT. MORE SPECIFICALLY, PSD-LA-751(M-1) REFLECTED THE FOLLOWING CHANGES: 1. REPLACEMENT OF THE DRI UNIT NO. 1 REFORMER (DRI-108) WITH A PROCESS HEATER. 2. REVISION OF THE PM10/PM2.5 BACT LIMIT FOR DRI-108 FROM 0.0027 GR/DSCF TO 0.006 LB/MM BTU TO ACCOUNT FOR BOTH FILTERABLE AND CONDENSABLE PM. 3. DELETION OF THE DRI UNIT NO. 1 UPPER SEAL GAS VENT. 4. REMOVAL OF SEAL GAS EMISSIONS FROM THE DRI UNIT NO. 1 FURNACE DUST COLLECTION. 5. LOWERING OF THE FIRING RATE OF THE DRI UNIT NO. 1 PACKAGE BOILER FROM 290 TO 100 MM BTU/HR. 6. REVISION OF THE EMISSIONS LIMITATIONS FOR THE DRI UNIT NO. 1 HOT FLARE TO REFLECT THAT IT WILL NOW BE UTILIZED FOR ONLY SU/SD OPERATIONS INSTEAD OF INTERMITTENTLY DURING NORMAL OPERATIONS. | DRI-109 - DRI Unit #1 Package Boiler Flue Stack | 11.31 | Natural Gas | 1760 | Billion Btu/yr | The package boilers provide steam to each DRI unit. The steam is primarily used to heat the reboiler in the acid gas absorption system, as well as for utility purposes. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | selective catalytic reduction & low-NOx burner | 0.0032 | LB/MMBTU |  | BACT-PSD | NSPS | N | 90 | N | 3.41 | T/YR |  | 0.0032 | LB/MMBTU |  | 0 | 0 | N
LA-0248 | DIRECT REDUCTION IRON PLANT | CONSOLIDATED ENVIRONMENTAL MANAGEMENT INC - NUCOR | ST JAMES PARISH | LA | 70723 | USA | STEVE ROWLAN | (704) 366-7000 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | KERMIT WITTENBURG, KERMIT.WITTENBURG@LA.GOV | PSD-LA-751 | 3312 | 331111 | 110037583442 | 10/31/2010 &nbsp;ACT | 01/27/2011 &nbsp;ACT | 2011-06-28 | 2011-12-08 | B |  | THE DRI PROCESS REDUCES THE IRON OXIDE CONTENT OF IRON ORE PELLETS INTO IRON METAL THROUGH DIRECT CONTACT WITH A REDUCING GAS. THE EFFECTIVENESS OF THIS REDUCTION PROCESS IS CALLED METALLIZATION, AND THE PROCESS EQUIPMENT WILL BE DESIGNED TO ACHIEVE A METALLIZATION RATE OF AT LEAST 92% OF THE OXIDES WITHIN THE ORE. THE REDUCTION WILL TAKE PLACE IN A COUNTERCURRENT VERTICAL SHAFT FURNACE, WHERE REDUCING GAS PASSES UP THROUGH IRON OXIDE PELLETS, WHICH FEED THROUGH THE FURNACE BY GRAVITY. THE MAJOR ELEMENTS OF THE DRI PROCESS INCLUDE THE FOLLOWING: (1) IRON OXIDE PREPARATION; (2) REDUCING GAS PREPARATION; (3) DRI REACTOR SHAFT FURNACE; (4) SPENT REDUCING GAS PREPARATION FOR REUSE, (5) DRI PRODUCT HANDLING; AND (6) ANCILLARY OPERATIONS, INCLUDING A PACKAGE BOILER, TWO COOLING TOWERS, AND A FLARE FOR EMERGENCY SITUATIONS. | ON 1/27/11, LDEQ ISSUED TO NUCOR TITLE V (TV) AND PSD PERMITS AUTHORIZING TWO DRI UNITS (MIDREX DESIGN). ON 9/29/11, NUCOR REQUESTED APPROVAL TO CONVERT ONE UNIT TO A DESIGN DEVELOPED BY TENOVA HYL. THE ONLY SIGNIFICANT DIFFERENCE BETWEEN THE MIDREX AND HYL DESIGNS IS THE POINT IN THE PROCESS WHERE NATURAL GAS IS REFORMED INTO CO & H2. LDEQ APPROVED NUCORâ€™S APPLICATION AND MODIFIED THE TV PERMIT ON 3/8/12. HOWEVER, LDEQ CONCLUDED THAT ITS INITIAL BACT DETERMINATIONS REMAINED APPROPRIATE AND DID NOT MODIFY THE PSD PERMIT. LDEQ SUBSEQUENTLY DECIDED TO REOPEN PSD-LA-751 FOR THE LIMITED PURPOSE OF CONFIRMING LDEQâ€™S INITIAL ASSESSMENT. LDEQ REQUIRED NUCOR TO PROVIDE AN ANALYSIS DEMONSTRATING THAT 1.) BACT FOR THE HYL EQUIPMENT IS NOT MORE STRINGENT THAN THAT PROVIDED BY PSD-LA-751, AND 2.) USE OF HYL EQUIPMENT IN ONE UNIT OF THE DRI FACILITY DOES NOT MATERIALLY CHANGE THE ORIGINAL AIR QUALITY ANALYSIS. LDEQ AGAIN CONCLUDED THAT NO CHANGES TO THE EXISTING BACT DETERMINATIONS WERE WARRANTED AND THAT THE HYL DESIGN DOES NOT RESULT IN ADVERSE AIR QUALITY IMPACTS. THEREFORE, LDEQ REVISED PSD-LA-751 ON 11/16/12 ONLY TO CLARIFY THAT IT COVERS THE HYL (I.E., IN SITU REFORMING) EQUIPMENT. MORE SPECIFICALLY, PSD-LA-751(M-1) REFLECTED THE FOLLOWING CHANGES: 1. REPLACEMENT OF THE DRI UNIT NO. 1 REFORMER (DRI-108) WITH A PROCESS HEATER. 2. REVISION OF THE PM10/PM2.5 BACT LIMIT FOR DRI-108 FROM 0.0027 GR/DSCF TO 0.006 LB/MM BTU TO ACCOUNT FOR BOTH FILTERABLE AND CONDENSABLE PM. 3. DELETION OF THE DRI UNIT NO. 1 UPPER SEAL GAS VENT. 4. REMOVAL OF SEAL GAS EMISSIONS FROM THE DRI UNIT NO. 1 FURNACE DUST COLLECTION. 5. LOWERING OF THE FIRING RATE OF THE DRI UNIT NO. 1 PACKAGE BOILER FROM 290 TO 100 MM BTU/HR. 6. REVISION OF THE EMISSIONS LIMITATIONS FOR THE DRI UNIT NO. 1 HOT FLARE TO REFLECT THAT IT WILL NOW BE UTILIZED FOR ONLY SU/SD OPERATIONS INSTEAD OF INTERMITTENTLY DURING NORMAL OPERATIONS. | DRI-209 - DRI Unit #2 Package Boiler Flue Stack | 11.31 | Natural Gas | 1760 | Billion Btu/yr | The package boilers provide steam to each DRI unit. The steam is primarily used to heat the reboiler in the acid gas absorption system, as well as for utility purposes. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | selective catalytic reduction & low-NOx burner | 0.0032 | LB/MMBTU |  | BACT-PSD | NSPS | N | 90 | N | 3.41 | T/YR |  | 0.0032 | LB/MMBTU |  | 0 | 0 | N
TX-0698 | BAYPORT COMPLEX | AIR LIQUIDE LARGE INDUSTRIES U.S., L.P. | HARRIS | TX |  | USA | JASON MILLER | (281) 474-8243 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 | 9346 PSDTX612M2 | 4931 | 325120 | 110000462758 | 07/27/2012 &nbsp;ACT | 09/05/2013 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | Air Liquid currently operates a cogeneration facility in Pasadena, Texas (Bayou Cogeneration Plant). The permit amendment submitted by Air Liquide will authorize a redevelopment project of its cogeneration plant. The proposed project will involve the replacement of four existing gas-fired turbines (GE 7EA) with similar gas-fired turbines (GE 7EA), the addition of three new gas-fired boilers rated at 550 MMBtu/hr and the removal of three existing gas-fired boilers rated at 443 MMBtu/hr. |  | (3) gas-fired boilers | 11.31 | natural gas | 550 | MMBTU/H | (3) 550 MMBtu/hr gas-fired boilers | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction (SCR) | 0.01 | LB/MMBTU | 3 HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 10 ppm ammonia slip limit
*FL-0330 | PORT DOLPHIN ENERGY LLC |  | HILLSBOROUGH | FL | 33616 | USA |  |  |  | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | DPA-EPA-R4001 | 4923 | 213112 | 110029520141 | &nbsp; | 12/01/2011 &nbsp;ACT | 2012-02-03 | 2018-03-23 | A |  | Port Dolphin is a deepwater port designed to moor liquefied natural gas shuttle and regasification vessels 28 miles off the cost of Florida. |  | Boilers (4 - 278 mmbtu/hr each) | 11.31 | natural gas | 0 |  |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction (SCR) | 0.012 | LB/MMBTU | 3-HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Utility Boiler 1 | 11.31 | Natural Gas | 656 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction (SCR) | 0.2 | LB/MMBTU | 30-DAY ROLLING AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 17.25 | T/YR | ANNUAL MAXIMUM | 0.2 | LB/MMBTU | 30-DAY ROLLING AVERAGE | 0 | 0 | N |  | BACT Limit = 0.006 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Utility Boiler 2 | 11.31 | Natural Gas | 656 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction (SCR) | 0.2 | LB/MMBTU | 30-DAY ROLLING AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 17.25 | T/YR | ANNUAL MAXIMUM | 0.2 | LB/MMBTU | 30-DAY ROLLING AVERAGE | 0 | 0 | N |  | BACT Limit = 0.006 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Utility Boiler 3 | 11.31 | Natural Gas | 656 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction (SCR) | 0.2 | LB/MMBTU | 30-DAY ROLLING AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 17.25 | T/YR | ANNUAL MAXIMUM | 0.2 | LB/MMBTU | 30-DAY ROLLING AVERAGE | 0 | 0 | N |  | BACT Limit = 0.006 LB/MMBTU (12-Month Rolling Average)
TX-0774 | BISHOP FACILITY | TICONA POLYMERS, INC. | NUECES | TX |  | USA | WILLIAM CHIDESTER | (361) 584-6614 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Daniel Guthrie (512) 239-1319 daniel.guthrie@tceq.texas.gov | 123216, PSDTX1438 AND GHGPSDTX | 2869 | 325199 | 110031352649 | 08/28/2015 &nbsp;ACT | 11/12/2015 &nbsp;ACT | 2015-11-09 | 2016-07-06 | B |  | Methanol Synthesis Plant |  | Reformer | 11.31 | natural gas | 1190 | MMBTU/H | Primary reformer for methanol production process which utilizes steam methane and auto-thermal reforming technologies. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | selective catalytic reduction Good combustion practices, firing of high hydrogen process gas and | 0.01 | LB/MMBTU | 12-MO AVERAGE | BACT-PSD |  | N | 0 | U | 0.015 | LB/MMBTU | 24-HR AVERAGE | 0 |  |  | 0 | 0 | N
*LA-0312 | ST. JAMES METHANOL PLANT | SOUTH LOUISIANA METHANOL LP | ST. JAMES | LA |  | USA | BRIAN JONES | (512) 394-7346 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Christopher Smith, (225) 219-3439 | PSD-LA-780(M-1) | 2869 | 325998 | Not Found | 09/30/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-03-10 | 2017-12-27 | A |  | New MeOH plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | New methanol plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | B2-13 - Boiler 2 (EQT0004) | 11.31 | Natural Gas | 350 | MM BTU/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Selective Catalytic Reduction, Low NOx Burners, & Good Combustion Practices | 0.01 | LB/MMBTU | 12-MONTH AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.01 | LB/MMBTU | 12-MONTH AVERAGE | 0 |  |  | 0 | 0 | N |  | NOX emissions will be monitored by a CEMS required by NSPS Subpart Db.
*LA-0312 | ST. JAMES METHANOL PLANT | SOUTH LOUISIANA METHANOL LP | ST. JAMES | LA |  | USA | BRIAN JONES | (512) 394-7346 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Christopher Smith, (225) 219-3439 | PSD-LA-780(M-1) | 2869 | 325998 | Not Found | 09/30/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-03-10 | 2017-12-27 | A |  | New MeOH plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | New methanol plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | B1-13 - Boiler 1 (EQT0003) | 11.31 | Natural Gas | 350 | MM BTU/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Selective Catalytic Reduction, Low NOx Burners, & Good Combustion Practices | 0.01 | LB/MMMTU | 12 MONTH AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.01 | LB/MMMTU | 12 MONTH AVERAGE | 0 |  |  | 0 | 0 | N |  | NOX emissions will be monitored with a CEMS required by NSPS Subpart Db.
IN-0166 | INDIANA GASIFICATION, LLC | INDIANA GASIFICATION, LLC | SPENCER | IN | 47635 | USA | MARK LUBBERS | 3174905078 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | T147-30464-00060 | 4925 | 221210 | 110045439888 | 04/20/2011 &nbsp;ACT | 06/27/2012 &nbsp;ACT | 2013-08-16 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/30464F.PDF | THE PERMITTEE OWNS AND OPERATES A STATIONARY SUBSTITUTE NATURAL GAS (SNG) AND LIQUEFIED CARBON DIOXIDE (CO2) PRODUCTION PLANT ALSO SIC: 2819 NAICS: 211112 | ALSO SIC: 2819 NAICS: 211112 | TWO (2) AUXILIARY BOILERS | 11.31 | NATURAL GAS | 408 | MMBTU/H, EACH | IDENTIFIED AS EU-005A AND EU-005B. ALSO COMBUSTS SUBSTITIUTE NATURAL GAS (SNG) | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | ULTRA LOW NOX BURNER WITH FGR | 0.0125 | LB/MMBTU | 24 HR | BACT-PSD |  | N | 60 |  | 0 |  |  | 0 |  |  | 80900 | 0 | N | 2012 | EL1AVG. TIME/CONDITIONS: 24-HOUR BLOCK DAILY AVERAGE. SCR NOT COST EFFECTIVE.
LA-0323 | MONSANTO LULING PLANT | MONSANTO COMPANY | ST. CHARLES PARISH | LA | 70070 | USA | ENRIQUE WEHLEN | 9857858211 | ENRIGUE.WEHLEN@MONSANTO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-890 | 2879 | 325320 | 110067118274 | 09/21/2015 &nbsp;ACT | 01/09/2017 &nbsp;ACT | 2017-09-26 | 2018-05-11 | D | http://edms.deq.louisiana.gov/app/doc/view.aspx?doc=10460194&ob=yes | Chemical Manufacture | Dicamba Manufacturing Facility expansion project. | No. 9 Boiler - Natural Gas Fired | 11.31 | Natural Gas | 325 | MMBTU/h |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Ultra Low NOx Burners | 0.035 | LB/MMBTU | ANNUAL AVERAGE | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0323 | MONSANTO LULING PLANT | MONSANTO COMPANY | ST. CHARLES PARISH | LA | 70070 | USA | ENRIQUE WEHLEN | 9857858211 | ENRIGUE.WEHLEN@MONSANTO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-890 | 2879 | 325320 | 110067118274 | 09/21/2015 &nbsp;ACT | 01/09/2017 &nbsp;ACT | 2017-09-26 | 2018-05-11 | D | http://edms.deq.louisiana.gov/app/doc/view.aspx?doc=10460194&ob=yes | Chemical Manufacture | Dicamba Manufacturing Facility expansion project. | No. 10 Boiler - Natural Gas Fired | 11.31 | Natural Gas | 325 | MMBTU/h |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Ultra Low NOx Burners | 0.035 | LB/MMBTU | ANNUAL AVERAGE | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0231 | LAKE CHARLES GASIFICATION FACILITY | LAKE CHARLES COGENERATION, LLC | CALCASIEU | LA | 70665 | USA | DOUG BARBA | 7139634635 | INTERPOWERLLC@AOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: MR. DAN NGUYEN - 225-219-3180 | PSD-LA-742 | 2869 | 325110 | UNKNOWN | 09/24/2008 &nbsp;ACT | 06/22/2009 &nbsp;ACT | 2009-07-10 | 2010-05-17 | A |  | A FACILITY TO CONVERT APPROXIMATELY 7400 TONS/DAY OF PETROLEUM COKE TO NATURAL GAS AND SULFURIC ACID. PERMIT PSD-LA-742(M1), DECEMBER 30, 2010, ALLOWS THE FACILITY TO PRODUCE 2.3 MILLION TONS OF METHANOL, INSTEAD OF NATURAL GAS. | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS. PERMIT PSD-LA-742(M1) WAS ISSUED DECEMBER 30, 2010 TO REVISE THE PROCESS DESIGN. THE FACILITY WILL PRODUCE H2SO4 AND METHANOL, INSTEAD OF NATURAL GAS. EXISTING BACT WILL NOT BE CHANGED. NO NEW BACT WILL BE ADDED. PERMIT PSD-LA-742(M2) DATED JUNE 29, 2012 1) REVISES THE PROCESS DESIGN TO PRODUCE HYDROGEN, 2) INCORPORATE PM 2.5 AND CO2E, AND 3)CHANGE NAME TO LAKE CHARLES CLEAN ENERGY. NO NEW BACT WILL BE ADDED. | AUXILIARY BOILER | 11.31 | NATURAL GAS | 938.3 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | ULTRA LOW NOX BURNERS | 0.035 | lb/MMBtu | MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.035 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N
LA-0320 | ST. CHARLES REFINERY | VALERO REFINING COMPANY - NEW ORLEANS LLC | ST. CHARLES | LA | 70079 | USA | ANDRE MARQUETTE | 985-764-8611 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-619(M11) | 2911 | 324199 | 110000448659 | 11/22/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2017-03-24 | 2017-04-28 | B |  | An existing petroleum refinery. Several tanks for the BTX Unit and the Marine Vapor Recovery No. 2 will be constructed. |  | Cat Naphtha Hydrotreater | 11.31 | Fuel gas | 0 |  |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Ultra Low NOx burners (ULNB) | 0.03 | LB/MM BTU | THREE ONE HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0.04 | LB/MM BTU | (WITH AIR PREHEATED) | 0 |  |  | 0 | 0 | N
LA-0231 | LAKE CHARLES GASIFICATION FACILITY | LAKE CHARLES COGENERATION, LLC | CALCASIEU | LA | 70665 | USA | DOUG BARBA | 7139634635 | INTERPOWERLLC@AOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: MR. DAN NGUYEN - 225-219-3180 | PSD-LA-742 | 2869 | 325110 | UNKNOWN | 09/24/2008 &nbsp;ACT | 06/22/2009 &nbsp;ACT | 2009-07-10 | 2010-05-17 | A |  | A FACILITY TO CONVERT APPROXIMATELY 7400 TONS/DAY OF PETROLEUM COKE TO NATURAL GAS AND SULFURIC ACID. PERMIT PSD-LA-742(M1), DECEMBER 30, 2010, ALLOWS THE FACILITY TO PRODUCE 2.3 MILLION TONS OF METHANOL, INSTEAD OF NATURAL GAS. | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS. PERMIT PSD-LA-742(M1) WAS ISSUED DECEMBER 30, 2010 TO REVISE THE PROCESS DESIGN. THE FACILITY WILL PRODUCE H2SO4 AND METHANOL, INSTEAD OF NATURAL GAS. EXISTING BACT WILL NOT BE CHANGED. NO NEW BACT WILL BE ADDED. PERMIT PSD-LA-742(M2) DATED JUNE 29, 2012 1) REVISES THE PROCESS DESIGN TO PRODUCE HYDROGEN, 2) INCORPORATE PM 2.5 AND CO2E, AND 3)CHANGE NAME TO LAKE CHARLES CLEAN ENERGY. NO NEW BACT WILL BE ADDED. | STEAM SUPERHEATERS (A &amp; B) | 11.31 | SUBSTITUTE NATURAL GAS | 415 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | ULTRA LOW NOX BURNERS (ULNB) | 0.035 | lb/MMBtu | TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0.035 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N
*ND-0033 | GRAND FORKS FERTILIZER PLANT | NORTHERN PLAINS NITROGEN | GRAND FORKS | ND | 58203 | USA | LARRY MACKIE |  | LARRYMACKIE@GMAIL.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV |  | PTC15052 | 2873 | 325311 |  | 01/20/2015 &nbsp;ACT | 08/10/2015 &nbsp;ACT | 2015-08-24 | 2015-08-24 | A | http://www.ndhealth.gov/AQ/ActivePermits.aspx | Fertilizer manufacturing plant designed to produce both feedstock and saleable products in the following nominal capacities: 2425 tpd ammonia, 2540 tpd ammonium nitrate solution, 300 tpd DEF, 3000 tpd urea solution, 3000 tpd granular urea, 2000 tpd nitric acid, 5620 tpd UAN, 441 tpd ammonium thiosulfate and 1080 tpd APP |  | Boilers | 11.31 | Natural gas | 187.5 | MMBTU/H | Facility includes 3 boilers of identical size (187.5 MM Btu/hr each) | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Ultra Low NOx Burners and Flue Gas Recirculation | 0.018 | LB/MM BTU | 30 DAY ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ND-0032 | SPIRITWOOD NITROGEN PLANT | CHS, INC. | STUTSMAN | ND | 58481 | USA | AJIT VENKATRAMAN |  | AJIT.VENKATRAMAN@CHSINC.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV |  | PTC14027 | 2873 | 325311 | Not Found | 09/19/2013 &nbsp;ACT | 06/20/2014 &nbsp;ACT | 2014-10-24 | 2017-06-28 | A | http://www.ndhealth.gov/EHS/FOIA/AQPermits/AQPermitConstruction.aspx | Fertilizer manufacturing plant to manufacture nitrogen-based products ammonia, urea, urea ammonium nitrate (UAN) and diesel exhaust fluid. The facility will produce both feedstock and saleable products in the following capacities: 2,425 tpd ammonia; 3,000 tpd urea solution; 3,000 tpd granular urea; 835 tpd nitric acid and 2,000 tpd UAN. |  | Package boiler | 11.31 | Natural gas | 280 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | ultra low NOx burners and flue gas recirculation | 0.018 | LB/MMBTU | 30 DAY ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AL-0276 | MOUNT VERNON MILL | THYSSENKRUP STEEL USA, LLC | MOBILE | AL | 36513 | USA | JORDAN COLLINS | 251-289-3833 | JORDAN.COLLINS@ARCELORMITTAL.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-0095-X001 | 3312 | 331221 | Unknown | 08/03/2009 &nbsp;ACT | 03/25/2010 &nbsp;ACT | 2015-02-27 | 2016-05-05 | C |  | The carbon steel mill would receive slabs primarily by barge. These carbon steel slabs would be heated and rolled to from a long strip in the hot strip mill. After rolling, the coils would be prepared for sale or would proceed to the picklin lines. After pickling, if needed, the strips would be cold-rolled for sale or would be further processed in the galvanizing lines. |  | Walking Beam Furnaces | 11.31 | Natural Gas | 845 | MMBTU/H | Throughput Capacity/Size: 845 mmbtu/hr (51-53) | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | ultra-low NOx burners and low NOx burners | 0.085 | LB/MMBTU |  | BACT-PSD |  | U | 0 | N | 71.82 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Combustion of ultra-low NOx burners and low NOx burners
FL-0344 | OKEELANTA COGENERATION PLANT | NEW HOPE POWER COMPANY | PALM BEACH | FL | 33493 | USA | MATTHEW CAPONE |  | MATTHEW_CAPONE@FLORIDACRYSTALS.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0990332-021-AC | 4911 | 221119 | 110012338684 | 05/03/2013 &nbsp;ACT | 08/27/2013 &nbsp;ACT | 2015-01-08 | 2016-05-05 | B | http://arm-permit2k.dep.state.fl.us/nontv/0990332.021.AC.F.ZIP | Cogeneration facility, fired with bagasse, wood, and natural gas. Four boilers, total electrical generating capacity of 140 MW. Also generates steam for co-located sugar refinery and sugar mill. | Technical evaluation available at http://arm-permit2k.dep.state.fl.us/nontv/0990332.021.AC.D.ZIP Adding fourth boiler to facility, fired by natural gas. Existing boilers were primarily fired with bagasse and wood. GHG BACT permit for this additional boiler processed/issued by EPA Region 4. | Natural Gas Boiler | 11.31 | Natural gas | 589 | MMBTU/H | Natural gas boiler, up to 48 hr/yr of oil permitted. 1-hr max 589 MMBtu/hr 24-hr max 536 MMBtu/hr Facility also includes three bagasse/wood-fired boilers, but this BACT determination applies only to this new natural gas boiler. | Nitrogen Oxides (NOx) | Other - NOx CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Ultra-low NOx burners with over-fire air | 0.035 | LB/MMBTU | 30-DAY ROLLING AVERAGE BY CEMS | BACT-PSD | NSPS | U | 0 | U | 18.8 | LB/H | 30-DAY ROLLING AVERAGE BY CEMS | 0 |  |  | 0 | 0 | N |  | Compliance by NOx CEMS, 30-day rolling average BACT more stringent than applicable NSPS (Da)
ID-0021 | MAGNIDA | MAGNOLIA NITROGEN IDAHO LLC | POWER | ID | 83211 | USA | TOM HORNYAK | 303-905-2675 | THORNYAK@MAGNIDA.COM | 10 | ID001 | IDAHO DEPT OF ENVIRONMENTAL QUALITY | MR. BILL ROGERS | (208)373-0437 | WILLIAM.ROGERS@DEQ.IDAHO.GOV | DAN PITMAN, P.E., PERMIT WRITER | P-2013.0030 | 2873 | 325311 | Not Found | 12/02/2013 &nbsp;ACT | 04/21/2014 &nbsp;ACT | 2017-05-19 | 2017-09-11 | A | NO LONGER AVAILABLE ON-LINE AS THE PERMIT IS EXPIRED | MAGNOLIA NITROGEN IDAHO LLC (MAGNIDA) IS PROPOSING TO CONSTRUCT A NEW COMPLEX FOR MANUFACTURING NITROGEN-BASED FERTILIZERS FROM NATURAL GAS. THE FACILITY WILL PRODUCE AMMONIA, GRANULATED UREA, UREA AMMONIUM NITRATE (UAN), AND DEISEL EXHAUST FLUID (DEF) FOR COMMERCIAL USE. | THIS PERMIT EXPIRED IN NOV. 2016; THE PROJECT WILL NOT BE PURSUED BY MAGNOLIA/MAGNIDA. There is one non-emissions BACT limit: Startup Heater Code 19.6 - has only a gas usage limit of 2.7 MMSCF per rolling 12-month period. | PACKAGE BOILER | 11.31 | Natural Gas | 275 | MMBtu/hr (HHV) | Provides heat throughout facility. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | N |  | 0.0125 | LB/MMBTU | PER MMBTU, 365-DAY AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | The emission limit condition of 365-day average includes periods of startup, shut down, and malfunction.

## LNB
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
WY-0074 | GREEN RIVER SODA ASH PLANT | SOLVAY CHEMICALS | SWEETWATER | WY | 82935 | USA | TIM BROWN | 3078726570 | TIM.BROWN@SOLVAY.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov |  | MD-13083 | 1474 | 212391 | 110007899248 | 08/06/2013 &nbsp;ACT | 11/18/2013 &nbsp;ACT | 2013-11-18 | 2016-05-04 | B |  | Trona Mine and Refinery | Installation of a 254 million British thermal unit per hour (MMBtu/hr) natural gas fired package boiler to provide steam and heat to the facilities production processes, installation of a clear liquor heat exchanger, and other minor operational and equipment changes to debottleneck production. | Natural Gas Package Boiler | 11.31 | Natural Gas | 254 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | low NOx burners and flue gas recirculation | 0.011 | LB/MMBTU | 30-DAY ROLLING | BACT-PSD | NSPS , NESHAP | N | 0 | U | 2.8 | LB/H | 30-DAY ROLLING | 0 |  |  | 8802 | 8802 | N | 2013
IL-0114 | CRONUS CHEMICALS, LLC | CRONUS CHEMICALS, LLC | DOUGLAS | IL | 60601 | USA | ERZIN ATAC | 312-863-8638 | ERZIN.ATAC@CRONUCHEM.COM | 5 | IL001 | ILLINOIS EPA, BUREAU OF AIR | MR. RAY PILAPIL | (217) 782-2113 | ray.pilapil@illinois.gov | Permit Writer: Bob Smet 217-785-9250 robert.smet@illinois.gov | 13060007 | 2873 | 325311 | 110055568522 | 02/14/2014 &nbsp;ACT | 09/05/2014 &nbsp;ACT | 2014-12-24 | 2016-05-05 | A | http://yosemite.epa.gov/r5/in_permt.nsf/6f1ebc583aad45448625763f0053e08e/02fa71769b748f8886257da2004e4f4f!OpenDocument | Plant will produce urea and ammonia, but ammonia production will be limited to a maximum of 3 months of the year (4,880 tpd urea and 2,789 tpd ammonia). |  | Boiler | 11.31 | natural gas | 864 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | low-nox burners, scr (or equivalent) | 0.012 | LB/MMBTU | 30-DAY AVERAGE ROLLED DAILY | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IA-0105 | IOWA FERTILIZER COMPANY | IOWA FERTILIZER COMPANY | LEE | IA | 52658 | USA | DAVE PEARSON | (319) 246-2308 | DAVE.PEARSON@IOWAFERTILIZERS.COM | 7 | IA001 | IOWA DEPARTMENT OF NATURAL RESOURCES AIR QUALITY | MR. GARY SMITH | (515) 725-9563 | GARY.SMITH@DNR.IOWA.GOV | CHRISTOPHER A. ROLING, PE ENVIRONMENTAL ENGINEER SENIOR (515) 725-9557 CHRIS.ROLING@DNR.IOWA.GOV | 12-219 | 2873 | 325311 | 110054890392 | 08/03/2012 &nbsp;ACT | 10/26/2012 &nbsp;ACT | 2012-11-01 | 2013-08-13 | A | https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp ,https://aqbweb.iowadnr.gov/airpermit/eepsdpermit.jsp | NITROGENEOUS FERTILIZER MANUFACTURING | THE PROJECT WAS AMENDED ON 3/13/14 DUE TO SOME DESIGN CHANGES WHICH INCLUDED ADDITIONAL EMISSION UNITS/POINTS. THE NEW PROJECT IS UNDER PROJECT NUMBER/PERMIT NUMBER 13-355 | Auxiliary Boiler | 11.31 | natural gas | 472.4 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burners (LNB) and Flue Gas Recirculation (FGR) | 0.0125 | LB/MMBTU | ROLLING 30 DAY AVERAGE | BACT-PSD |  | U | 0 | U | 5.52 | TONS/YR | ROLLING 12 MONTH TOTAL | 0 |  |  | 0 | 0 | N
IN-0166 | INDIANA GASIFICATION, LLC | INDIANA GASIFICATION, LLC | SPENCER | IN | 47635 | USA | MARK LUBBERS | 3174905078 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: JOSIAH BALOGUN 317-234-5257 JBALOGUN@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | T147-30464-00060 | 4925 | 221210 | 110045439888 | 04/20/2011 &nbsp;ACT | 06/27/2012 &nbsp;ACT | 2013-08-16 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/30464F.PDF | THE PERMITTEE OWNS AND OPERATES A STATIONARY SUBSTITUTE NATURAL GAS (SNG) AND LIQUEFIED CARBON DIOXIDE (CO2) PRODUCTION PLANT ALSO SIC: 2819 NAICS: 211112 | ALSO SIC: 2819 NAICS: 211112 | TWO (2) AUXILIARY BOILERS | 11.31 | NATURAL GAS | 408 | MMBTU/H, EACH | IDENTIFIED AS EU-005A AND EU-005B. ALSO COMBUSTS SUBSTITIUTE NATURAL GAS (SNG) | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | ULTRA LOW NOX BURNER WITH FGR | 0.0125 | LB/MMBTU | 24 HR | BACT-PSD |  | N | 60 |  | 0 |  |  | 0 |  |  | 80900 | 0 | N | 2012 | EL1AVG. TIME/CONDITIONS: 24-HOUR BLOCK DAILY AVERAGE. SCR NOT COST EFFECTIVE.
AL-0251 | HILLABEE ENERGY CENTER | CER GENERATION | TALLAPOOSA | AL |  | USA | TONY DIEMEL | 4136150637 | TONY.W.DIEMEL@CONSTELLATION.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US | AMY GRAHAM (334) 271-7867 | 310-0022-X001 | 4911 | 221119 | not found | 07/09/2008 &nbsp;ACT | 09/24/2008 &nbsp;ACT | 2011-03-22 | 2015-02-09 | A |  | ENERGY PLANT |  | FUEL HEATER | 11.31 | NATURAL GAS | 11640000 | BTU |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | LOW NOX BURNER | 0.013 | LB/MMBTU |  | BACT-PSD |  | U | 0 | N | 1.6 | LB/H |  | 0 |  |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT HA08 | 11.31 | NATURAL GAS | 8.37 | MMBTU/H | THE EMISSION UNIT IS A CLEAVER BROOKS BOILER AT HARRAH'S LAS VEGAS. UNIT HA08 IS IDENTICAL TO HA09 AND HA10. THE SAME SET OF EMISSION LIMITS APPLIES TO EACH OF THE THREE BOILERS. THE THREE BOILERS ARE SUBJECT TO THE LIMIT OF TOTAL ANNUAL OPERATING TIME FOR 20,000 HOURS PER YEAR. THERE ARE NO BOILERS AT HARRAH'S LAS VEGAS, WHICH HAS A THROUGHPUT CAPACITY IN EXCESS OF 10 MMBTU/HR. NO BACT DETERMINATIONS FOR ANY EMISSION UNITS AT BILL'S GAMBLIN' HALL & SALON ARE REPORTED HEREIN BECAUSE ALL OF THEM HAVE A VERY SMALL POTENTIAL TO EMIT FOR ANY POLLUTANT. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOX BURNER | 0.0146 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 12 | PPMVD | CORRECTED AT 3% OXYGEN | 0.0146 | LB/MMBTU |  | 0 | 0 | N
*ND-0033 | GRAND FORKS FERTILIZER PLANT | NORTHERN PLAINS NITROGEN | GRAND FORKS | ND | 58203 | USA | LARRY MACKIE |  | LARRYMACKIE@GMAIL.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV |  | PTC15052 | 2873 | 325311 |  | 01/20/2015 &nbsp;ACT | 08/10/2015 &nbsp;ACT | 2015-08-24 | 2015-08-24 | A | http://www.ndhealth.gov/AQ/ActivePermits.aspx | Fertilizer manufacturing plant designed to produce both feedstock and saleable products in the following nominal capacities: 2425 tpd ammonia, 2540 tpd ammonium nitrate solution, 300 tpd DEF, 3000 tpd urea solution, 3000 tpd granular urea, 2000 tpd nitric acid, 5620 tpd UAN, 441 tpd ammonium thiosulfate and 1080 tpd APP |  | Boilers | 11.31 | Natural gas | 187.5 | MMBTU/H | Facility includes 3 boilers of identical size (187.5 MM Btu/hr each) | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Ultra Low NOx Burners and Flue Gas Recirculation | 0.018 | LB/MM BTU | 30 DAY ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
ND-0032 | SPIRITWOOD NITROGEN PLANT | CHS, INC. | STUTSMAN | ND | 58481 | USA | AJIT VENKATRAMAN |  | AJIT.VENKATRAMAN@CHSINC.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV |  | PTC14027 | 2873 | 325311 | Not Found | 09/19/2013 &nbsp;ACT | 06/20/2014 &nbsp;ACT | 2014-10-24 | 2017-06-28 | A | http://www.ndhealth.gov/EHS/FOIA/AQPermits/AQPermitConstruction.aspx | Fertilizer manufacturing plant to manufacture nitrogen-based products ammonia, urea, urea ammonium nitrate (UAN) and diesel exhaust fluid. The facility will produce both feedstock and saleable products in the following capacities: 2,425 tpd ammonia; 3,000 tpd urea solution; 3,000 tpd granular urea; 835 tpd nitric acid and 2,000 tpd UAN. |  | Package boiler | 11.31 | Natural gas | 280 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | ultra low NOx burners and flue gas recirculation | 0.018 | LB/MMBTU | 30 DAY ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AL-0271 | GEORGIA PACIFIC BRETON LLC | GEORGIA PACIFIC LLC | ESCAMBIA | AL | 36427 | USA | ROBERTO FLORES | 251-867-8358 | ROBERTO.FLORES@GAPAC.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 502-0001-X049 | 2631 | 322130 | Unknown | 04/18/2014 &nbsp;ACT | 06/11/2014 &nbsp;ACT | 2014-07-11 | 2016-05-04 | D |  | Kraft Pulp &amp; Paper mdu | NAICS Code: 322130 | No.4 Power Boiler | 11.31 | Natural Gas | 425 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Low NOx Burner with FGR | 0.02 | LB/MMBTU |  | BACT-PSD | MACT | U | 50 | N | 8.5 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Low NOx Burner with FGR
LA-0320 | ST. CHARLES REFINERY | VALERO REFINING COMPANY - NEW ORLEANS LLC | ST. CHARLES | LA | 70079 | USA | ANDRE MARQUETTE | 985-764-8611 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: dan nguyen (225)219-3395 | PSD-LA-619(M11) | 2911 | 324199 | 110000448659 | 11/22/2013 &nbsp;ACT | 03/05/2014 &nbsp;ACT | 2017-03-24 | 2017-04-28 | B |  | An existing petroleum refinery. Several tanks for the BTX Unit and the Marine Vapor Recovery No. 2 will be constructed. |  | Cat Naphtha Hydrotreater | 11.31 | Fuel gas | 0 |  |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Ultra Low NOx burners (ULNB) | 0.03 | LB/MM BTU | THREE ONE HOUR TEST AVERAGE | BACT-PSD |  | U | 0 | U | 0.04 | LB/MM BTU | (WITH AIR PREHEATED) | 0 |  |  | 0 | 0 | N
LA-0323 | MONSANTO LULING PLANT | MONSANTO COMPANY | ST. CHARLES PARISH | LA | 70070 | USA | ENRIQUE WEHLEN | 9857858211 | ENRIGUE.WEHLEN@MONSANTO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-890 | 2879 | 325320 | 110067118274 | 09/21/2015 &nbsp;ACT | 01/09/2017 &nbsp;ACT | 2017-09-26 | 2018-05-11 | D | http://edms.deq.louisiana.gov/app/doc/view.aspx?doc=10460194&ob=yes | Chemical Manufacture | Dicamba Manufacturing Facility expansion project. | No. 9 Boiler - Natural Gas Fired | 11.31 | Natural Gas | 325 | MMBTU/h |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Ultra Low NOx Burners | 0.035 | LB/MMBTU | ANNUAL AVERAGE | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0323 | MONSANTO LULING PLANT | MONSANTO COMPANY | ST. CHARLES PARISH | LA | 70070 | USA | ENRIQUE WEHLEN | 9857858211 | ENRIGUE.WEHLEN@MONSANTO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-890 | 2879 | 325320 | 110067118274 | 09/21/2015 &nbsp;ACT | 01/09/2017 &nbsp;ACT | 2017-09-26 | 2018-05-11 | D | http://edms.deq.louisiana.gov/app/doc/view.aspx?doc=10460194&ob=yes | Chemical Manufacture | Dicamba Manufacturing Facility expansion project. | No. 10 Boiler - Natural Gas Fired | 11.31 | Natural Gas | 325 | MMBTU/h |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Ultra Low NOx Burners | 0.035 | LB/MMBTU | ANNUAL AVERAGE | BACT-PSD | NSPS , NESHAP | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0231 | LAKE CHARLES GASIFICATION FACILITY | LAKE CHARLES COGENERATION, LLC | CALCASIEU | LA | 70665 | USA | DOUG BARBA | 7139634635 | INTERPOWERLLC@AOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: MR. DAN NGUYEN - 225-219-3180 | PSD-LA-742 | 2869 | 325110 | UNKNOWN | 09/24/2008 &nbsp;ACT | 06/22/2009 &nbsp;ACT | 2009-07-10 | 2010-05-17 | A |  | A FACILITY TO CONVERT APPROXIMATELY 7400 TONS/DAY OF PETROLEUM COKE TO NATURAL GAS AND SULFURIC ACID. PERMIT PSD-LA-742(M1), DECEMBER 30, 2010, ALLOWS THE FACILITY TO PRODUCE 2.3 MILLION TONS OF METHANOL, INSTEAD OF NATURAL GAS. | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS. PERMIT PSD-LA-742(M1) WAS ISSUED DECEMBER 30, 2010 TO REVISE THE PROCESS DESIGN. THE FACILITY WILL PRODUCE H2SO4 AND METHANOL, INSTEAD OF NATURAL GAS. EXISTING BACT WILL NOT BE CHANGED. NO NEW BACT WILL BE ADDED. PERMIT PSD-LA-742(M2) DATED JUNE 29, 2012 1) REVISES THE PROCESS DESIGN TO PRODUCE HYDROGEN, 2) INCORPORATE PM 2.5 AND CO2E, AND 3)CHANGE NAME TO LAKE CHARLES CLEAN ENERGY. NO NEW BACT WILL BE ADDED. | AUXILIARY BOILER | 11.31 | NATURAL GAS | 938.3 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | ULTRA LOW NOX BURNERS | 0.035 | lb/MMBtu | MAXIMUM | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.035 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N
LA-0231 | LAKE CHARLES GASIFICATION FACILITY | LAKE CHARLES COGENERATION, LLC | CALCASIEU | LA | 70665 | USA | DOUG BARBA | 7139634635 | INTERPOWERLLC@AOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | PERMIT WRITER: MR. DAN NGUYEN - 225-219-3180 | PSD-LA-742 | 2869 | 325110 | UNKNOWN | 09/24/2008 &nbsp;ACT | 06/22/2009 &nbsp;ACT | 2009-07-10 | 2010-05-17 | A |  | A FACILITY TO CONVERT APPROXIMATELY 7400 TONS/DAY OF PETROLEUM COKE TO NATURAL GAS AND SULFURIC ACID. PERMIT PSD-LA-742(M1), DECEMBER 30, 2010, ALLOWS THE FACILITY TO PRODUCE 2.3 MILLION TONS OF METHANOL, INSTEAD OF NATURAL GAS. | APPLICATION ACCEPTED DATE REFLECTS DATE OF ADMINISTRATIVE COMPLETENESS. PERMIT PSD-LA-742(M1) WAS ISSUED DECEMBER 30, 2010 TO REVISE THE PROCESS DESIGN. THE FACILITY WILL PRODUCE H2SO4 AND METHANOL, INSTEAD OF NATURAL GAS. EXISTING BACT WILL NOT BE CHANGED. NO NEW BACT WILL BE ADDED. PERMIT PSD-LA-742(M2) DATED JUNE 29, 2012 1) REVISES THE PROCESS DESIGN TO PRODUCE HYDROGEN, 2) INCORPORATE PM 2.5 AND CO2E, AND 3)CHANGE NAME TO LAKE CHARLES CLEAN ENERGY. NO NEW BACT WILL BE ADDED. | STEAM SUPERHEATERS (A &amp; B) | 11.31 | SUBSTITUTE NATURAL GAS | 415 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | ULTRA LOW NOX BURNERS (ULNB) | 0.035 | lb/MMBtu | TOTAL | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0.035 | LB/MMBTU |  | 0 |  |  | 0 | 0 | N
FL-0344 | OKEELANTA COGENERATION PLANT | NEW HOPE POWER COMPANY | PALM BEACH | FL | 33493 | USA | MATTHEW CAPONE |  | MATTHEW_CAPONE@FLORIDACRYSTALS.COM | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | 0990332-021-AC | 4911 | 221119 | 110012338684 | 05/03/2013 &nbsp;ACT | 08/27/2013 &nbsp;ACT | 2015-01-08 | 2016-05-05 | B | http://arm-permit2k.dep.state.fl.us/nontv/0990332.021.AC.F.ZIP | Cogeneration facility, fired with bagasse, wood, and natural gas. Four boilers, total electrical generating capacity of 140 MW. Also generates steam for co-located sugar refinery and sugar mill. | Technical evaluation available at http://arm-permit2k.dep.state.fl.us/nontv/0990332.021.AC.D.ZIP Adding fourth boiler to facility, fired by natural gas. Existing boilers were primarily fired with bagasse and wood. GHG BACT permit for this additional boiler processed/issued by EPA Region 4. | Natural Gas Boiler | 11.31 | Natural gas | 589 | MMBTU/H | Natural gas boiler, up to 48 hr/yr of oil permitted. 1-hr max 589 MMBtu/hr 24-hr max 536 MMBtu/hr Facility also includes three bagasse/wood-fired boilers, but this BACT determination applies only to this new natural gas boiler. | Nitrogen Oxides (NOx) | Other - NOx CEMS | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Ultra-low NOx burners with over-fire air | 0.035 | LB/MMBTU | 30-DAY ROLLING AVERAGE BY CEMS | BACT-PSD | NSPS | U | 0 | U | 18.8 | LB/H | 30-DAY ROLLING AVERAGE BY CEMS | 0 |  |  | 0 | 0 | N |  | Compliance by NOx CEMS, 30-day rolling average BACT more stringent than applicable NSPS (Da)
NE-0054 | CARGILL, INCORPORATED | CARGILL, INCORPORATED | WASHINGTON | NE | 68008 | USA | MICHELLE BUCKLIN | 4024714204 | MICHELLE_BUCKLIN@CARGILL.COM | 7 | NE001 | NEBRASKA DEPT. OF ENVIRONMENTAL QUALITY | GARY BUTTERMORE. | (402) 471-2189 | ndeq.airquality@nebraska.gov |  | 12-042 | 2046 | 311221 | Not Found | 11/09/2012 &nbsp;ACT | 09/12/2013 &nbsp;ACT | 2012-10-24 | 2017-06-28 | B |  |  |  | Boiler K | 11.31 | natural gas | 300 | mmbtu/h |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNERS AND INDUCED FLUE GAS RECIRCULATION | 0.04 | LB/MMBTU | 30-DAY ROLLING AVERAGE | BACT-PSD | NSPS | U | 0 | U | 12 | LB/H | 3-HOUR ROLLING AVERAGE | 0 |  |  | 0 | 0 | N
NV-0049 | HARRAH'S OPERATING COMPANY, INC. | HARRAH'S OPERATING COMPANY, INC. | CLARK | NV | 891098969 | USA | TOM JENKIN | 7023675662 |  | 9 | NV002 | CLARK CO. DEPT. OF AIR QUALITY | MR. SANTOSH MATHEW | (702)455-5942 | Mathew@ClarkCountyNV.gov | RBLC COORDINATOR: DAVID C. LEE, TEL: (702) 455-1673 | 257 | 7011 | 721120 | UNKNOWN | 03/18/2009 &nbsp;EST | 08/20/2009 &nbsp;ACT | 2009-12-01 | 2009-12-01 | A |  | THE FACILITY CONSISTS OF SEVEN CONTIGUOUS HOTEL AND CASINO BUSINESSES OWNED AND OPERATED BY HARRAH'S OPERATING COMPANY, INC. BOILERS AND HEATERS ARE THE PRIMARY EMISSION UNITS. THE FACILITY IS A MAJOR SOURCE FOR NITROGEN OXIDES, A SYNTHETIC MINOR SOURCE FOR CARBON MONOXIDE, AND A MINOR SOURCE FOR ALL THE OTHER CRITERIA AIR POLLUTANTS. THE FACILITY IS LOCATED IN A NON-ATTAINMENT AREA FOR OZONE. | THE SEVEN INDIVIDUAL BUSINESSES THAT MAKE UP THIS CONSOLIDATED FACILITY ARE: HARRAH'S LAS VEGAS, FLAMINGO LAS VEGAS, BALLY'S LAS VEGAS, BILL'S GAMBLIN' HALL AND SALOON, CAESAR'S PALACE, PARIS CASINO RESORT, AND IMPERIAL PALACE. EACH ONE OF THEM HAD BEEN INDIVIDUALLY ISSUED A MINOR-SOURCE PERMIT PRIOR TO THE CONSOLIDATION IN 2005. EACH ONE OF THEM IS ADJACENT TO AT LEAST ONE OF THE OTHER BUSINESSES. THIS REPORT IS BASED ON THE AUTHORITY TO CONSTRUCT (ATC) PERMIT FOR MODIFICATION #12, REVISION #1 AND ITS TECHNICAL SUPPORT DOCUMENT. THE ATC PERMITS FOR MODIFICATIONS #13 AND #14 FOCUS NARROWLY ON ADDING SMALL EMISSION UNITS AT CAESARS PALACE AND PARIS CASINO RESORT RESPECTIVELY WITHOUT A COMPREHENSIVE ACCOUNT OF ALL THE EMISSION UNITS FOR THE MAJOR STATIONARY SOURCE. A PART 70 PERMIT HAS BEEN PROPOSED FOR PUBLIC NOTICE. DUE TO THE LARGE NUMBER OF EMISSION UNITS. THOSE WITH A POTENTIAL TO EMIT LESS THAN ONE TON PER YEAR FOR ANY POLLUTANT MAY BE SKIPPED. | BOILER - UNIT IP04 | 11.31 | NATURAL GAS | 16.7 | MMBTU/H | UNIT IP04 IS A KEWANEE BOILER AT IMPERIAL PALACE. UNIT IP04 IS IDENTICAL TO UNIT IP05. EITHER BOILER IS ALLOWED TO OPERATE UP TO 8,760 HOURS PER YEAR. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNER | 0.049 | LB/MMBTU |  | BACT-PSD | SIP , OPERATING PERMIT | N | 0 | Y | 40.2 | PPMVD | CORRECTED TO 3% OXYGEN | 0.0049 | LB/MMBTU |  | 0 | 0 | N
IN-0234 | GRAIN PROCESSING CORPORATION | GRAIN PROCESSING CORPORATION | DAVIESS | IN | 47501 | USA | WENDY BOUVIER | 8122572759 | WENDY.BOUVIER@GRAINPROCESSING.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | MADHURIMA MOULIK 317-233-0868 JASON KRAWCZYK, SECTION CHIEF IDEM OFFICE OF AIR QUALITY 100 N. SENATE AVENUE 317-234-5174 | 027-35177-00046 | 2046 | 311221 | 110041204265 | 11/26/2014 &nbsp;ACT | 12/08/2015 &nbsp;ACT | 2016-02-25 | 2016-07-06 | B | HTTP:PERMITS.AIR.IDEM.IN.GOV/35177F.PDF | THIS FACILITY IS A STATIONARY CORN WET MILLING PLANT. |  | BOILER 1 | 11.31 | NATURAL GAS | 271 | MMBTU/H | NATURAL GAS FIRED, ALSO CAPACBLE OF BURNING ALCOHOL. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW-NOX BURNER AND FLUE GAS RECIRCULATION SYSTEM | 0.05 | LB/MMBTU | NORMAL OPERATION | BACT-PSD |  | N | 0 | U | 0.2 | LB/MMBTU | DURING SSM | 0 |  |  | 0 | 0 | N |  | NOX EMISSIONS SHALL NOT 13.6 LB/HR DURING NORMAL OPERATION AND 54.2 LB/HR DURING START-UP, SHUTDOWN AND MALFUNCTION.
IN-0234 | GRAIN PROCESSING CORPORATION | GRAIN PROCESSING CORPORATION | DAVIESS | IN | 47501 | USA | WENDY BOUVIER | 8122572759 | WENDY.BOUVIER@GRAINPROCESSING.COM | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | MADHURIMA MOULIK 317-233-0868 JASON KRAWCZYK, SECTION CHIEF IDEM OFFICE OF AIR QUALITY 100 N. SENATE AVENUE 317-234-5174 | 027-35177-00046 | 2046 | 311221 | 110041204265 | 11/26/2014 &nbsp;ACT | 12/08/2015 &nbsp;ACT | 2016-02-25 | 2016-07-06 | B | HTTP:PERMITS.AIR.IDEM.IN.GOV/35177F.PDF | THIS FACILITY IS A STATIONARY CORN WET MILLING PLANT. |  | BOILER 2 | 11.31 | NATURAL GAS | 271 | MMBTU/H | NATURAL GAS BOILER WITH CAPABILITY OF BURNING ALCOHOL | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | LOW-NOX BURNERS AND FLUE GAS RECIRCULATION | 0.05 | LB/MMBTU | NORMAL OPERATION | BACT-PSD |  | N | 0 |  | 0.2 | LB/MMBTU | DURING SSM | 0 |  |  | 0 | 0 | N |  | 13.6 LB/HR DURING NORMAL OPERATION, 54.2 LB/HR DURING START-UP SHUTDOWN AND MALFUNCTION
TX-0650 | DIRECT REDUCED IRON AND HOT BRIQUETTING FACILITY | VOESTALPINE TEXAS LLC | SAN PATRICIO | TX |  | USA | MATTHIAS PASTL | 361-452-0746 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Dois Webb, Phone: 512-239-1575 e-mail: dois.webb@tceq.texas.gov | 108113/PSDTX1344 | 3312 | 331111 | UNKNOWN | 02/05/2013 &nbsp;ACT | 03/18/2014 &nbsp;ACT | 2014-03-27 | 2016-07-29 | A |  | Converts iron ore pellets into iron briquettes |  | GAS REFORMER | 11.31 | NATURAL GAS | 1591 | MMBTU/H |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNERS | 0.058 | LB/MMBTU |  | BACT-PSD | NSPS , NESHAP , MACT , SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
AL-0276 | MOUNT VERNON MILL | THYSSENKRUP STEEL USA, LLC | MOBILE | AL | 36513 | USA | JORDAN COLLINS | 251-289-3833 | JORDAN.COLLINS@ARCELORMITTAL.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-0095-X001 | 3312 | 331221 | Unknown | 08/03/2009 &nbsp;ACT | 03/25/2010 &nbsp;ACT | 2015-02-27 | 2016-05-05 | C |  | The carbon steel mill would receive slabs primarily by barge. These carbon steel slabs would be heated and rolled to from a long strip in the hot strip mill. After rolling, the coils would be prepared for sale or would proceed to the picklin lines. After pickling, if needed, the strips would be cold-rolled for sale or would be further processed in the galvanizing lines. |  | Walking Beam Furnaces | 11.31 | Natural Gas | 845 | MMBTU/H | Throughput Capacity/Size: 845 mmbtu/hr (51-53) | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | ultra-low NOx burners and low NOx burners | 0.085 | LB/MMBTU |  | BACT-PSD |  | U | 0 | N | 71.82 | LB/H |  | 0 |  |  | 0 | 0 | N |  | Combustion of ultra-low NOx burners and low NOx burners
AR-0094 | JOHN W. TURK JR. POWER PLANT | SOUTHWEST ELECTRIC POWER COMPANY | FULTON | AR | 71838 | USA | KRIS GAUS | 214771113 | KPGAIS@AEP.COM | 6 | AR001 | ARKANSAS DEPT OF ENVIRONMENTAL QUALITY | MR. THOMAS RHEAUME | (501) 682-0762 | rheaume@adeq.state.ar.us |  | 2123-AOP-R0 | 4911 | 221112 | UNKNOWN | 07/08/2008 &nbsp;ACT | 11/05/2008 &nbsp;ACT | 2009-01-09 | 2010-04-09 | A |  | 600 MW POWDER RIVER BASIN SUB-BITUMINOUS PULVERIZED COAL FIRED POWER PLANT | PSD AND 112(G) PERMIT DECISION | AUXILIARY BOILER | 11.31 | NATURAL GAS | 555 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX BURNERS | 0.11 | LB/MMBTU | 30 DAY ROLLING AVERAGE | BACT-PSD |  |  | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0167 | MAGNETATION LLC | MAGNETATION LLC | WHITE | IN | 47980 | USA | MICHAEL TWITE | 2182593795 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: KRISTEN WILLOUGHBY 317-233-3031 KWILLOUGHBY@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 181-32081-00054 | 1011 | 212210 | 110055584363 | 07/02/2012 &nbsp;ACT | 04/16/2013 &nbsp;ACT | 2013-08-16 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32081F.PDF | IRON ORE CONCENTRATE PELLETIZING PLANT |  | FURNACE WINDBOX EXHAUST (WBE) | 11.31 | NATURAL | 436 | MMBTU/H | IDENTIFIED AS EU014 USING ONE (1) GAS SUSPENSION ABSORBER (GAS) (CE015) AND ONE (1) WBE BAGHOUSE (CE016) EXHAUSTING TO STACK SV013B, FURNACE WINDBOX EXHAUST (WBE) IS PART OF ONE (1) INDURATION MACHINE, CONISTING OF ONE (1) NATURAL GAS FIRED PELLET HARDENING FURNACE. WITH A MAXIMUM HEAT INPUT CAPACITY OF 436 MMBTU PER HOUR AND A MAXIMUM THROUGHPUT RATE OF 450 TONS PER HOUR OF IRON OXIDE PELLETS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW NOX LE NATURAL GAS BURNERS | 0.25 | LB/MMBTU | 3 HOURS | BACT-PSD |  | U | 0 | U | 109 | LB/H | 3 HOURS | 0 |  |  | 0 | 0 | N |  | LIMIT TWO: COMBINED EMISSIONS FROM SV013A AND SV013B. NOTE: 0.249 LB NOX/MMBTU * 436 MMBTU/HR = 109 LB/HR NOX
IN-0167 | MAGNETATION LLC | MAGNETATION LLC | WHITE | IN | 47980 | USA | MICHAEL TWITE | 2182593795 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: KRISTEN WILLOUGHBY 317-233-3031 KWILLOUGHBY@IDEM.IN.GOV SECTION CHIEF: MATT STUCKEY 317-233-0203 MSTUCKEY@IDEM.IN.GOV | 181-32081-00054 | 1011 | 212210 | 110055584363 | 07/02/2012 &nbsp;ACT | 04/16/2013 &nbsp;ACT | 2013-08-16 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/32081F.PDF | IRON ORE CONCENTRATE PELLETIZING PLANT |  | FURNACE HOOD EXHAUST | 11.31 | NATURAL GAS | 436 | MMBTU/H | IDENTIFIED AS EU013, USING BAGHOUSE CE013, EXHAUSTS TO STACK SV013A, ONE (1) FURNACE HOOD EXHAUST IS PART OF ONE (1) INDURATION MACHINE. CONSISTING OF ONE (1) NATRUAL GAS FIRED PELLET HARDENING FURNACE, WITH A MAXIMUM HEAT INPUT CAPACITY OF 436 MMBTU PER HOUR AND A MAXIMUM THROUGHPUT RATE OF 450 TONS PER HOUR OF IRON OXIDE PELLETS. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | LOW-NOX LE NATURAL GAS BURNERS | 0.25 | LB/MMBTU | 3 HOURS | BACT-PSD |  | U | 0 | U | 109 | LB/H | 3 HOURS | 0 |  |  | 0 | 0 | N |  | LIMIT TWO: COMBINED EMISSIONS FROM SV013A AND SV013B
[40 empty] | min | 0.011 | LB/MMBTU
[40 empty] | max | 0.25 | LB/MMBTU
[40 empty] | avg | 0.053275 | LB/MMBTU
[40 empty] | median | 0.035 | LB/MMBTU
[40 empty] | mode | 0.035 | LB/MMBTU

## SCR
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
LA-0248 | DIRECT REDUCTION IRON PLANT | CONSOLIDATED ENVIRONMENTAL MANAGEMENT INC - NUCOR | ST JAMES PARISH | LA | 70723 | USA | STEVE ROWLAN | (704) 366-7000 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | KERMIT WITTENBURG, KERMIT.WITTENBURG@LA.GOV | PSD-LA-751 | 3312 | 331111 | 110037583442 | 10/31/2010 &nbsp;ACT | 01/27/2011 &nbsp;ACT | 2011-06-28 | 2011-12-08 | B |  | THE DRI PROCESS REDUCES THE IRON OXIDE CONTENT OF IRON ORE PELLETS INTO IRON METAL THROUGH DIRECT CONTACT WITH A REDUCING GAS. THE EFFECTIVENESS OF THIS REDUCTION PROCESS IS CALLED METALLIZATION, AND THE PROCESS EQUIPMENT WILL BE DESIGNED TO ACHIEVE A METALLIZATION RATE OF AT LEAST 92% OF THE OXIDES WITHIN THE ORE. THE REDUCTION WILL TAKE PLACE IN A COUNTERCURRENT VERTICAL SHAFT FURNACE, WHERE REDUCING GAS PASSES UP THROUGH IRON OXIDE PELLETS, WHICH FEED THROUGH THE FURNACE BY GRAVITY. THE MAJOR ELEMENTS OF THE DRI PROCESS INCLUDE THE FOLLOWING: (1) IRON OXIDE PREPARATION; (2) REDUCING GAS PREPARATION; (3) DRI REACTOR SHAFT FURNACE; (4) SPENT REDUCING GAS PREPARATION FOR REUSE, (5) DRI PRODUCT HANDLING; AND (6) ANCILLARY OPERATIONS, INCLUDING A PACKAGE BOILER, TWO COOLING TOWERS, AND A FLARE FOR EMERGENCY SITUATIONS. | ON 1/27/11, LDEQ ISSUED TO NUCOR TITLE V (TV) AND PSD PERMITS AUTHORIZING TWO DRI UNITS (MIDREX DESIGN). ON 9/29/11, NUCOR REQUESTED APPROVAL TO CONVERT ONE UNIT TO A DESIGN DEVELOPED BY TENOVA HYL. THE ONLY SIGNIFICANT DIFFERENCE BETWEEN THE MIDREX AND HYL DESIGNS IS THE POINT IN THE PROCESS WHERE NATURAL GAS IS REFORMED INTO CO & H2. LDEQ APPROVED NUCORâ€™S APPLICATION AND MODIFIED THE TV PERMIT ON 3/8/12. HOWEVER, LDEQ CONCLUDED THAT ITS INITIAL BACT DETERMINATIONS REMAINED APPROPRIATE AND DID NOT MODIFY THE PSD PERMIT. LDEQ SUBSEQUENTLY DECIDED TO REOPEN PSD-LA-751 FOR THE LIMITED PURPOSE OF CONFIRMING LDEQâ€™S INITIAL ASSESSMENT. LDEQ REQUIRED NUCOR TO PROVIDE AN ANALYSIS DEMONSTRATING THAT 1.) BACT FOR THE HYL EQUIPMENT IS NOT MORE STRINGENT THAN THAT PROVIDED BY PSD-LA-751, AND 2.) USE OF HYL EQUIPMENT IN ONE UNIT OF THE DRI FACILITY DOES NOT MATERIALLY CHANGE THE ORIGINAL AIR QUALITY ANALYSIS. LDEQ AGAIN CONCLUDED THAT NO CHANGES TO THE EXISTING BACT DETERMINATIONS WERE WARRANTED AND THAT THE HYL DESIGN DOES NOT RESULT IN ADVERSE AIR QUALITY IMPACTS. THEREFORE, LDEQ REVISED PSD-LA-751 ON 11/16/12 ONLY TO CLARIFY THAT IT COVERS THE HYL (I.E., IN SITU REFORMING) EQUIPMENT. MORE SPECIFICALLY, PSD-LA-751(M-1) REFLECTED THE FOLLOWING CHANGES: 1. REPLACEMENT OF THE DRI UNIT NO. 1 REFORMER (DRI-108) WITH A PROCESS HEATER. 2. REVISION OF THE PM10/PM2.5 BACT LIMIT FOR DRI-108 FROM 0.0027 GR/DSCF TO 0.006 LB/MM BTU TO ACCOUNT FOR BOTH FILTERABLE AND CONDENSABLE PM. 3. DELETION OF THE DRI UNIT NO. 1 UPPER SEAL GAS VENT. 4. REMOVAL OF SEAL GAS EMISSIONS FROM THE DRI UNIT NO. 1 FURNACE DUST COLLECTION. 5. LOWERING OF THE FIRING RATE OF THE DRI UNIT NO. 1 PACKAGE BOILER FROM 290 TO 100 MM BTU/HR. 6. REVISION OF THE EMISSIONS LIMITATIONS FOR THE DRI UNIT NO. 1 HOT FLARE TO REFLECT THAT IT WILL NOW BE UTILIZED FOR ONLY SU/SD OPERATIONS INSTEAD OF INTERMITTENTLY DURING NORMAL OPERATIONS. | DRI-109 - DRI Unit #1 Package Boiler Flue Stack | 11.31 | Natural Gas | 1760 | Billion Btu/yr | The package boilers provide steam to each DRI unit. The steam is primarily used to heat the reboiler in the acid gas absorption system, as well as for utility purposes. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | selective catalytic reduction & low-NOx burner | 0.0032 | LB/MMBTU |  | BACT-PSD | NSPS | N | 90 | N | 3.41 | T/YR |  | 0.0032 | LB/MMBTU |  | 0 | 0 | N
LA-0248 | DIRECT REDUCTION IRON PLANT | CONSOLIDATED ENVIRONMENTAL MANAGEMENT INC - NUCOR | ST JAMES PARISH | LA | 70723 | USA | STEVE ROWLAN | (704) 366-7000 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | KERMIT WITTENBURG, KERMIT.WITTENBURG@LA.GOV | PSD-LA-751 | 3312 | 331111 | 110037583442 | 10/31/2010 &nbsp;ACT | 01/27/2011 &nbsp;ACT | 2011-06-28 | 2011-12-08 | B |  | THE DRI PROCESS REDUCES THE IRON OXIDE CONTENT OF IRON ORE PELLETS INTO IRON METAL THROUGH DIRECT CONTACT WITH A REDUCING GAS. THE EFFECTIVENESS OF THIS REDUCTION PROCESS IS CALLED METALLIZATION, AND THE PROCESS EQUIPMENT WILL BE DESIGNED TO ACHIEVE A METALLIZATION RATE OF AT LEAST 92% OF THE OXIDES WITHIN THE ORE. THE REDUCTION WILL TAKE PLACE IN A COUNTERCURRENT VERTICAL SHAFT FURNACE, WHERE REDUCING GAS PASSES UP THROUGH IRON OXIDE PELLETS, WHICH FEED THROUGH THE FURNACE BY GRAVITY. THE MAJOR ELEMENTS OF THE DRI PROCESS INCLUDE THE FOLLOWING: (1) IRON OXIDE PREPARATION; (2) REDUCING GAS PREPARATION; (3) DRI REACTOR SHAFT FURNACE; (4) SPENT REDUCING GAS PREPARATION FOR REUSE, (5) DRI PRODUCT HANDLING; AND (6) ANCILLARY OPERATIONS, INCLUDING A PACKAGE BOILER, TWO COOLING TOWERS, AND A FLARE FOR EMERGENCY SITUATIONS. | ON 1/27/11, LDEQ ISSUED TO NUCOR TITLE V (TV) AND PSD PERMITS AUTHORIZING TWO DRI UNITS (MIDREX DESIGN). ON 9/29/11, NUCOR REQUESTED APPROVAL TO CONVERT ONE UNIT TO A DESIGN DEVELOPED BY TENOVA HYL. THE ONLY SIGNIFICANT DIFFERENCE BETWEEN THE MIDREX AND HYL DESIGNS IS THE POINT IN THE PROCESS WHERE NATURAL GAS IS REFORMED INTO CO & H2. LDEQ APPROVED NUCORâ€™S APPLICATION AND MODIFIED THE TV PERMIT ON 3/8/12. HOWEVER, LDEQ CONCLUDED THAT ITS INITIAL BACT DETERMINATIONS REMAINED APPROPRIATE AND DID NOT MODIFY THE PSD PERMIT. LDEQ SUBSEQUENTLY DECIDED TO REOPEN PSD-LA-751 FOR THE LIMITED PURPOSE OF CONFIRMING LDEQâ€™S INITIAL ASSESSMENT. LDEQ REQUIRED NUCOR TO PROVIDE AN ANALYSIS DEMONSTRATING THAT 1.) BACT FOR THE HYL EQUIPMENT IS NOT MORE STRINGENT THAN THAT PROVIDED BY PSD-LA-751, AND 2.) USE OF HYL EQUIPMENT IN ONE UNIT OF THE DRI FACILITY DOES NOT MATERIALLY CHANGE THE ORIGINAL AIR QUALITY ANALYSIS. LDEQ AGAIN CONCLUDED THAT NO CHANGES TO THE EXISTING BACT DETERMINATIONS WERE WARRANTED AND THAT THE HYL DESIGN DOES NOT RESULT IN ADVERSE AIR QUALITY IMPACTS. THEREFORE, LDEQ REVISED PSD-LA-751 ON 11/16/12 ONLY TO CLARIFY THAT IT COVERS THE HYL (I.E., IN SITU REFORMING) EQUIPMENT. MORE SPECIFICALLY, PSD-LA-751(M-1) REFLECTED THE FOLLOWING CHANGES: 1. REPLACEMENT OF THE DRI UNIT NO. 1 REFORMER (DRI-108) WITH A PROCESS HEATER. 2. REVISION OF THE PM10/PM2.5 BACT LIMIT FOR DRI-108 FROM 0.0027 GR/DSCF TO 0.006 LB/MM BTU TO ACCOUNT FOR BOTH FILTERABLE AND CONDENSABLE PM. 3. DELETION OF THE DRI UNIT NO. 1 UPPER SEAL GAS VENT. 4. REMOVAL OF SEAL GAS EMISSIONS FROM THE DRI UNIT NO. 1 FURNACE DUST COLLECTION. 5. LOWERING OF THE FIRING RATE OF THE DRI UNIT NO. 1 PACKAGE BOILER FROM 290 TO 100 MM BTU/HR. 6. REVISION OF THE EMISSIONS LIMITATIONS FOR THE DRI UNIT NO. 1 HOT FLARE TO REFLECT THAT IT WILL NOW BE UTILIZED FOR ONLY SU/SD OPERATIONS INSTEAD OF INTERMITTENTLY DURING NORMAL OPERATIONS. | DRI-209 - DRI Unit #2 Package Boiler Flue Stack | 11.31 | Natural Gas | 1760 | Billion Btu/yr | The package boilers provide steam to each DRI unit. The steam is primarily used to heat the reboiler in the acid gas absorption system, as well as for utility purposes. | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | selective catalytic reduction & low-NOx burner | 0.0032 | LB/MMBTU |  | BACT-PSD | NSPS | N | 90 | N | 3.41 | T/YR |  | 0.0032 | LB/MMBTU |  | 0 | 0 | N
LA-0317 | METHANEX - GEISMAR METHANOL PLANT | METHANEX USA, LLC | ASCENSION | LA | 70734 | USA | GLYNN FONTENOT | 225-402-0301 | GFONTENOT@METHANEX.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | permit writer: Dr. Qingming Zhang (225)-219-3457 | PSD-LA-761(M4) | 2869 | 325199 | 110046528227 | 09/09/2016 &nbsp;ACT | 12/22/2016 &nbsp;ACT | 2017-03-15 | 2017-04-28 | A |  | methanol plant (Unit I and Unit II) to produce 6000 metric tons of methanol by steam reforming natural gas | psd-la-761, issued 11/07/12, for relocation Unit I (3000 mt/yr) from punta arenas (chile); psd-la-761(M1), issued 07/12/13, for relocation Unit II (3000 mt/yr); psd-la-761(M2) (issued 01/15/16), psd-la-761(M3) (issued 01/14/16), and psd-la-761(M4) (issued 12/22/16) are for miscellaneous reconciliation | Steam methane reformers (I-H-101, II-H-101) | 11.31 | natural gas | 2364 | mm btu/hr |  | Nitrogen Oxides (NOx) | EPA/OAR Cond. Test Mthd 022 | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 0.007 | LB/MM BTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | BACT = LAER (Permit 0180-00210-V4, dated 12/22/2016)
TX-0656 | GAS TO GASOLINE PLANT | NATGASOLINE | JEFFERSON | TX |  | USA | KEVIN STRUVE |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Cheryl Covone 512-239-1248 | PSDTX1340 AND 107764 | 2911 | 325199 | 110064577006 | 01/16/2013 &nbsp;ACT | 05/16/2014 &nbsp;ACT | 2014-05-20 | 2016-05-12 | A |  | Chemical Plant |  | Boiler | 11.31 | natural gas and fuel gas | 950 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 0.01 | LB/MMBTU |  | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0659 | DEER PARK PLANT | ROHM AND HAAS TEXAS INC | HARRIS | TX |  | USA | HARRY ENGELHARDT | 281-228-8100 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | PSDTX1320, 2165 | 2869 | 325188 | UNKNOWN | 10/12/2012 &nbsp;ACT | 12/20/2013 &nbsp;ACT | 2014-06-05 | 2016-07-29 | C |  |  |  | Boiler | 11.31 | Natural gas | 515 | MMBTU/H | Two (2) 515 MMBtu/hr boilers firing natural gas with refinery gas as a secondary fuel | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective catalytic reduction | 0.01 | LB/MMBTU | 1-HR | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0704 | UTILITY PLANT | M & G RESINS USA LLC | NUECES | TX |  | USA | MAURO FENOGLIO | (281) 874-8074 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 108819 PSDTX1354 | 4911 | 221112 | unknown | 02/22/2013 &nbsp;ACT | 12/02/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | In support of the new PET (polyethylene terephthalate) unit and new PTA (terephthalic acid) plant proposed by M&amp;G Resins USA LLC, the company also proposes a Utility Plant that will consist of either one of two options. All steam generated from the Utility Plant will be used as process steam. There is no steam driven electrical generator. |  | (2) boilers | 11.31 | natural gas | 450 | MMBTU/H | Auxiliary Boilers A1 and A2 are rated at 450 MMBtu/hr each. Auxiliary Boiler A1 and A2 were represented by the applicant to potentially operate 8,760 hours per year each. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 0.01 | LB/MMBTU | 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0704 | UTILITY PLANT | M & G RESINS USA LLC | NUECES | TX |  | USA | MAURO FENOGLIO | (281) 874-8074 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 108819 PSDTX1354 | 4911 | 221112 | unknown | 02/22/2013 &nbsp;ACT | 12/02/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | In support of the new PET (polyethylene terephthalate) unit and new PTA (terephthalic acid) plant proposed by M&amp;G Resins USA LLC, the company also proposes a Utility Plant that will consist of either one of two options. All steam generated from the Utility Plant will be used as process steam. There is no steam driven electrical generator. |  | boiler | 11.31 | natural gas | 250 | MMBTU/H | Auxiliary Boiler B is rated at 250 MMBtu/hr. Auxiliary Boiler B was represented by the applicant to potentially operate 8,760 hours per year. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 0.01 | LB/MMBTU | 3-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0707 | CHEMICAL MANUFACTURING FACILITY | ROHM AND HAAS TEXAS INCORPORATED | HARRIS | TX |  | USA | HARRY ENGLEHARDT | (281) 228-8100 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ruth.alvirez@tceq.texas.gov | 2165 PSDTX1320 | 2865 | 325110 | 110043790163 | 10/12/2012 &nbsp;ACT | 12/20/2013 &nbsp;ACT | 2015-03-20 | 2016-05-09 | B |  | RH is proposing to install two 515 million British thermal unit per hour (MMBtu/hr) gas-fired boilers to produce additional steam for the RH Texas Deer Park Plant manufacturing facilities and give the plant the ability to perform planned maintenance on other steam producing equipment at the site without sacrificing peak steam production. The boilers will be authorized to fire natural gas and N-area absorber off-gas (off-gas). Each boiler will be equipped with a Selective Catalytic Reduction (SCR) system and Continuous Emission Monitoring System (CEMS). |  | (2) boilers | 11.31 | natural gas | 515 | MMBTU/H | RH is proposing to install two 515 million British thermal unit per hour (MMBtu/hr) gas-fired boilers. The boilers will be authorized to fire natural gas and N-area absorber off-gas (off-gas). | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction | 0.01 | LB/MMBTU | 1 HOUR | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 10 ppm ammonia slip limit
TX-0815 | PORT ARTHUR ETHANE SIDE CRACKER | TOTAL PETROCHEMICALS & REFINING USA, INC. | JEFFERSON | TX |  | USA | DOROTHY BARTOL | (409) 963-6800 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Daniel Guthrie, (512) 239-1319, Daniel.Guthrie@tceq.texas.gov | 122353, PSDTX1426, GHGPSDTX114 | 2869 | 325110 | Not Found | 11/17/2016 &nbsp;ACT | 01/17/2017 &nbsp;ACT | 2017-01-18 | 2017-11-16 | B |  | Ethylene Production |  | Pyrolysis Furnaces | 11.31 | NATURAL GAS | 1000 | kT / YR | 7 furnaces | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction & Low NOx burners | 0.01 | LB/MMBTU |  | BACT-PSD | SIP | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0698 | BAYPORT COMPLEX | AIR LIQUIDE LARGE INDUSTRIES U.S., L.P. | HARRIS | TX |  | USA | JASON MILLER | (281) 474-8243 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Mr. Erik Hendrickson 512-239-1095 | 9346 PSDTX612M2 | 4931 | 325120 | 110000462758 | 07/27/2012 &nbsp;ACT | 09/05/2013 &nbsp;ACT | 2015-03-19 | 2016-05-09 | B |  | Air Liquid currently operates a cogeneration facility in Pasadena, Texas (Bayou Cogeneration Plant). The permit amendment submitted by Air Liquide will authorize a redevelopment project of its cogeneration plant. The proposed project will involve the replacement of four existing gas-fired turbines (GE 7EA) with similar gas-fired turbines (GE 7EA), the addition of three new gas-fired boilers rated at 550 MMBtu/hr and the removal of three existing gas-fired boilers rated at 443 MMBtu/hr. |  | (3) gas-fired boilers | 11.31 | natural gas | 550 | MMBTU/H | (3) 550 MMBtu/hr gas-fired boilers | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction (SCR) | 0.01 | LB/MMBTU | 3 HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N |  | 10 ppm ammonia slip limit
TX-0774 | BISHOP FACILITY | TICONA POLYMERS, INC. | NUECES | TX |  | USA | WILLIAM CHIDESTER | (361) 584-6614 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MS. ANNE INMAN | (512) 239-1267 | anne.inman@tceq.texas.gov | Daniel Guthrie (512) 239-1319 daniel.guthrie@tceq.texas.gov | 123216, PSDTX1438 AND GHGPSDTX | 2869 | 325199 | 110031352649 | 08/28/2015 &nbsp;ACT | 11/12/2015 &nbsp;ACT | 2015-11-09 | 2016-07-06 | B |  | Methanol Synthesis Plant |  | Reformer | 11.31 | natural gas | 1190 | MMBTU/H | Primary reformer for methanol production process which utilizes steam methane and auto-thermal reforming technologies. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | selective catalytic reduction Good combustion practices, firing of high hydrogen process gas and | 0.01 | LB/MMBTU | 12-MO AVERAGE | BACT-PSD |  | N | 0 | U | 0.015 | LB/MMBTU | 24-HR AVERAGE | 0 |  |  | 0 | 0 | N
*LA-0312 | ST. JAMES METHANOL PLANT | SOUTH LOUISIANA METHANOL LP | ST. JAMES | LA |  | USA | BRIAN JONES | (512) 394-7346 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Christopher Smith, (225) 219-3439 | PSD-LA-780(M-1) | 2869 | 325998 | Not Found | 09/30/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-03-10 | 2017-12-27 | A |  | New MeOH plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | New methanol plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | B2-13 - Boiler 2 (EQT0004) | 11.31 | Natural Gas | 350 | MM BTU/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Selective Catalytic Reduction, Low NOx Burners, & Good Combustion Practices | 0.01 | LB/MMBTU | 12-MONTH AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.01 | LB/MMBTU | 12-MONTH AVERAGE | 0 |  |  | 0 | 0 | N |  | NOX emissions will be monitored by a CEMS required by NSPS Subpart Db.
*LA-0312 | ST. JAMES METHANOL PLANT | SOUTH LOUISIANA METHANOL LP | ST. JAMES | LA |  | USA | BRIAN JONES | (512) 394-7346 |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Mr. Christopher Smith, (225) 219-3439 | PSD-LA-780(M-1) | 2869 | 325998 | Not Found | 09/30/2015 &nbsp;ACT | 06/30/2017 &nbsp;ACT | 2017-03-10 | 2017-12-27 | A |  | New MeOH plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | New methanol plant designed to produce 5,275 metric tons per day of refined methanol from natural gas and carbon dioxide (CO2) feedstock | B1-13 - Boiler 1 (EQT0003) | 11.31 | Natural Gas | 350 | MM BTU/hr |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | P | Selective Catalytic Reduction, Low NOx Burners, & Good Combustion Practices | 0.01 | LB/MMMTU | 12 MONTH AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 0.01 | LB/MMMTU | 12 MONTH AVERAGE | 0 |  |  | 0 | 0 | N |  | NOX emissions will be monitored with a CEMS required by NSPS Subpart Db.
*ND-0033 | GRAND FORKS FERTILIZER PLANT | NORTHERN PLAINS NITROGEN | GRAND FORKS | ND | 58203 | USA | LARRY MACKIE |  | LARRYMACKIE@GMAIL.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV |  | PTC15052 | 2873 | 325311 |  | 01/20/2015 &nbsp;ACT | 08/10/2015 &nbsp;ACT | 2015-08-24 | 2015-08-24 | A | http://www.ndhealth.gov/AQ/ActivePermits.aspx | Fertilizer manufacturing plant designed to produce both feedstock and saleable products in the following nominal capacities: 2425 tpd ammonia, 2540 tpd ammonium nitrate solution, 300 tpd DEF, 3000 tpd urea solution, 3000 tpd granular urea, 2000 tpd nitric acid, 5620 tpd UAN, 441 tpd ammonium thiosulfate and 1080 tpd APP |  | Ammonia Plant Primary Reformer | 11.31 | Natural gas | 1006 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction & Low NOx burners | 0.012 | LB/MM BTU | 30 DAY ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*FL-0330 | PORT DOLPHIN ENERGY LLC |  | HILLSBOROUGH | FL | 33616 | USA |  |  |  | 4 | FL001 | FLORIDA DEPT. OF ENVIRONMENTAL PROTECTION | MR. DAVID READ | (850) 717-9000 | David.Read@dep.state.fl.us |  | DPA-EPA-R4001 | 4923 | 213112 | 110029520141 | &nbsp; | 12/01/2011 &nbsp;ACT | 2012-02-03 | 2018-03-23 | A |  | Port Dolphin is a deepwater port designed to moor liquefied natural gas shuttle and regasification vessels 28 miles off the cost of Florida. |  | Boilers (4 - 278 mmbtu/hr each) | 11.31 | natural gas | 0 |  |  | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction (SCR) | 0.012 | LB/MMBTU | 3-HOUR ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0305 | LAKE CHARLES METHANOL FACILITY | LAKE CHARLES METHANOL, LLC | CALCASIEU PARISH | LA | 70669 | USA | JOHN MCDANIEL | 318-308-0322 | JMCDANIEL@LAKECHARLESMETHANOL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Dan Nguyen - (225)219-3395 | PSD-LA-803(M1) | 2869 | 325199 | 110067180366 | 06/16/2016 &nbsp;ACT | 06/30/2016 &nbsp;ACT | 2017-03-07 | 2017-04-28 | A |  | Proposed facility to produce methanol, H2, H2SO4, CO2, Argon and electricity from Pet Coke | PSD-LA-803 was issued 2/24/2016. The facility has not commence construction when Permit PSD-LA-803(M1) was issued. | Auxiliary Boilers and Superheaters | 11.31 | Natural Gas | 0 |  | Supplement fuel: fuel gas Boilers: 225 MM BTU/hr each | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR | 0.015 | LBS/MM BTU | 30 ROLLING AVG., EXCEPT SCR SU OR MAINT. | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0245 | HYDROGEN PLANT | VALERO REFINING - NEW ORLEANS, LLC | ST. CHARLES | LA | 70079 | USA | ROBERT MARTIN | (985)764-8611 | ROB.MARTIN@VALERO.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen - 225-219-3395 | PSD-LA-750 | 2911 | 324110 | Not Available | 08/18/2010 &nbsp;ACT | 12/15/2010 &nbsp;ACT | 2011-03-29 | 2011-07-06 | B |  | A plant to produce hydrogen by steam reforming natural gas. | Application Accepted Received Date = Date of completeness Determination | SMR Heaters (EQT0400 and EQT0401) | 11.31 | Fuel Gas | 1055 | MMBTU/H | Two identical units | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | B | SCR and Ultra low NOX burner | 0.015 | LB/MMBTU | ANNUAL AVERAGE | BACT-PSD |  | U | 0 | U | 15.83 | LB/H | HOURLY MAXIMUM (EACH UNIT) | 0 |  |  | 0 | 0 | N
LA-0264 | NORCO HYDROGEN PLANT | AIR PRODUCTS AND CHEMICALS, INC. | ST. CHARLES | LA | 70079 | USA | DAN DILLER | 5042541590 | DILLERDJ@AIRPRODUCTS.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit Writer: Dan Nguyen | PSD-LA-750(M1) | 2813 | 325120 | 110000597140 | 02/29/2012 &nbsp;ACT | 09/04/2012 &nbsp;ACT | 2012-11-29 | 2013-09-06 | A |  | A new hydrogen plant (SMR) which was previously propoposed by Valero (LA-0245) |  | Reformer | 11.31 | fuel gas | 1320 | MMBTU/H | Supplement fuel: natural gas | Nitrogen Oxides (NOx) | EPA/OAR Mthd 7E | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR and Ultra low NOX burner | 0.015 | LB/MMBTU | ANNUAL AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0.015 | LB/MMBTU | ANNUAL AVERAGE | 0 | 0 | N
ND-0032 | SPIRITWOOD NITROGEN PLANT | CHS, INC. | STUTSMAN | ND | 58481 | USA | AJIT VENKATRAMAN |  | AJIT.VENKATRAMAN@CHSINC.COM | 8 | ND001 | NORTH DAKOTA DEPARTMENT OF HEALTH | MR. CRAIG THORSTENSON | 701-328-5188 | CTHORSTENSON@ND.GOV |  | PTC14027 | 2873 | 325311 | Not Found | 09/19/2013 &nbsp;ACT | 06/20/2014 &nbsp;ACT | 2014-10-24 | 2017-06-28 | A | http://www.ndhealth.gov/EHS/FOIA/AQPermits/AQPermitConstruction.aspx | Fertilizer manufacturing plant to manufacture nitrogen-based products ammonia, urea, urea ammonium nitrate (UAN) and diesel exhaust fluid. The facility will produce both feedstock and saleable products in the following capacities: 2,425 tpd ammonia; 3,000 tpd urea solution; 3,000 tpd granular urea; 835 tpd nitric acid and 2,000 tpd UAN. |  | Primary reformer | 11.31 | Natural gas | 788 | MMBTU/H |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR & Low NOx burners | 0.02 | LB/MMBTU | 30 DAY ROLLING AVERAGE | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
CT-0156 | MONTVILLE POWER LLC | NRG ENERGY |  | CT | 6382 | USA | ROBERT SPOONER | 860-982-0459 | ROBERT.SPOONER@NRGENERGY.COM | 1 | CT001 | CONNECTICUT DEPT OF ENERGY & ENVIRONMENTAL PROTECTION | MR. GARY ROSE | (860)424-3468 | gary.rose@ct.gov | JAMES GRILLO (860) 424-4152 | 107-0056 | 4911 | 221119 | 900700108 | 05/11/2009 &nbsp;ACT | 04/06/2010 &nbsp;ACT | 2010-04-13 | 2013-05-30 | D |  | 43 MW STOKER FIRED BIOMASS; 82 MW TANGENTIALLY FIRED NATURAL GAS/ULS DISTILLATE UTILITY BOILER (7% ANNUAL CAPACITY FACTOR) |  | 82 MW Utility Boiler | 11.31 | Natural Gas | 995 | MMBTU/H | 7% annual capacity factor for distillate and natural gas firing. | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | SCR (Regenerative) | 0.06 | LB/MMBTU |  | BACT-PSD |  | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Utility Boiler 1 | 11.31 | Natural Gas | 656 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction (SCR) | 0.2 | LB/MMBTU | 30-DAY ROLLING AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 17.25 | T/YR | ANNUAL MAXIMUM | 0.2 | LB/MMBTU | 30-DAY ROLLING AVERAGE | 0 | 0 | N |  | BACT Limit = 0.006 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Utility Boiler 2 | 11.31 | Natural Gas | 656 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction (SCR) | 0.2 | LB/MMBTU | 30-DAY ROLLING AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 17.25 | T/YR | ANNUAL MAXIMUM | 0.2 | LB/MMBTU | 30-DAY ROLLING AVERAGE | 0 | 0 | N |  | BACT Limit = 0.006 LB/MMBTU (12-Month Rolling Average)
*LA-0315 | G2G PLANT | BIG LAKE FUELS LLC | CALCASIEU | LA | 70605 | USA |  |  |  | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV |  | PSD-LA-781 | 2869 | 325110 | Not Found | 09/04/2013 &nbsp;ACT | 05/23/2014 &nbsp;ACT | 2017-03-13 | 2017-03-16 | A |  | The G2G Plant will be a natural gas to gasoline production facility which will use natural gas to produce methanol that will be subsequently converted into gasoline. |  | Utility Boiler 3 | 11.31 | Natural Gas | 656 | MMBTU/HR |  | Nitrogen Oxides (NOx) | Unspecified | (InOrganic Compounds,Oxides of Nitrogen (NOx),Particulate Matter (PM)) | 10102 | A | Selective Catalytic Reduction (SCR) | 0.2 | LB/MMBTU | 30-DAY ROLLING AVERAGE | BACT-PSD | NSPS , OPERATING PERMIT | U | 0 | U | 17.25 | T/YR | ANNUAL MAXIMUM | 0.2 | LB/MMBTU | 30-DAY ROLLING AVERAGE | 0 | 0 | N |  | BACT Limit = 0.006 LB/MMBTU (12-Month Rolling Average)
[40 empty] | min | 0.0032 | LB/MMBTU
[40 empty] | max | 0.2 | LB/MMBTU
[40 empty] | mean | 0.037496 | LB/MMBTU