## Small Combined Cycle Gas Turbin
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110060000000 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | THREE (3) AUXILARY BOILERS | 16.21 | NATURAL GAS | 218.6 | MMBTU/H, EACH | NATURAL GAS USAGE IN EACH BOILER NOT TO EXCEED 1501.91 MMCF/YR | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN | 0.0019 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110060000000 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | THREE (3) AUXILARY BOILERS | 16.21 | NATURAL GAS | 218.6 | MMBTU/H, EACH | NATURAL GAS USAGE IN EACH BOILER NOT TO EXCEED 1501.91 MMCF/YR | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN | 0.0019 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110060000000 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | TWO (2) NATURAL GAS FIRED COMBUSTION TURBINES | 16.21 | NATURAL GAS | 283 | MMBTU/H, EACH | NATURAL GAS FIRED, OPEN-SIMPLE CYCLE COMBUSTION TURBINES WITH HEAT RECOVERY | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN | 0.0019 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110060000000 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | TWO (2) NATURAL GAS FIRED COMBUSTION TURBINES | 16.21 | NATURAL GAS | 283 | MMBTU/H, EACH | NATURAL GAS FIRED, OPEN-SIMPLE CYCLE COMBUSTION TURBINES WITH HEAT RECOVERY | Particulate matter, filterable (FPM) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN | 0.0019 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AL-0282 | LENZING FIBERS, INC. | LENZING FIBERS, INC. | MOBILE | AL | 36505 | USA | MR. KEVIN, PLANT MANAGER ALLEN | 251-679-2814 | K.ALLEN@LENZING.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-0047-X014 | 2823 | 325221 | 110044000000 | 11/19/2013 &nbsp;ACT | 01/22/2014 &nbsp;ACT | 2015-03-17 | 2016-05-09 | B |  | Production of lyocell fiber by solvent spinning process. | NAICS Code: 325220 | Gas Turbine with HRSG | 16.21 | Natural Gas | 25 | MW |  | Particulate matter, filterable (FPM) | EPA/OAR Mthd 5 | (Particulate Matter (PM)) | PM | P | Good combustion practices. | 0.0075 | LB/MMBTU |  | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110060000000 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | THREE (3) AUXILARY BOILERS | 16.21 | NATURAL GAS | 218.6 | MMBTU/H, EACH | NATURAL GAS USAGE IN EACH BOILER NOT TO EXCEED 1501.91 MMCF/YR | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN | 0.0075 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110060000000 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | THREE (3) AUXILARY BOILERS | 16.21 | NATURAL GAS | 218.6 | MMBTU/H, EACH | NATURAL GAS USAGE IN EACH BOILER NOT TO EXCEED 1501.91 MMCF/YR | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN | 0.0075 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110060000000 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | TWO (2) NATURAL GAS FIRED COMBUSTION TURBINES | 16.21 | NATURAL GAS | 283 | MMBTU/H, EACH | NATURAL GAS FIRED, OPEN-SIMPLE CYCLE COMBUSTION TURBINES WITH HEAT RECOVERY | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN | 0.0076 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110060000000 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | TWO (2) NATURAL GAS FIRED COMBUSTION TURBINES | 16.21 | NATURAL GAS | 283 | MMBTU/H, EACH | NATURAL GAS FIRED, OPEN-SIMPLE CYCLE COMBUSTION TURBINES WITH HEAT RECOVERY | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN | 0.0076 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110060000000 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | TWO (2) NATURAL GAS FIRED COMBUSTION TURBINES | 16.21 | NATURAL GAS | 283 | MMBTU/H, EACH | NATURAL GAS FIRED, OPEN-SIMPLE CYCLE COMBUSTION TURBINES WITH HEAT RECOVERY | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN | 0.0076 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110060000000 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | TWO (2) NATURAL GAS FIRED COMBUSTION TURBINES | 16.21 | NATURAL GAS | 283 | MMBTU/H, EACH | NATURAL GAS FIRED, OPEN-SIMPLE CYCLE COMBUSTION TURBINES WITH HEAT RECOVERY | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN | 0.0076 | LB/MMBTU | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
AL-0321 | KIMBERLY-CLARK MOBILE | KIMBERLY-CLARK CORPORATION - MOBILE OPERATIONS | MOBILE | AL | 36610 | USA | LEEANNE STICKLAND | 251 330 3464 | LEEANNE.STRICKLAND@KCC.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-2012 | 2621 | 322121 | 110058000000 | 08/21/2017 &nbsp;ACT | 10/11/2017 &nbsp;ACT | 2018-01-12 | 2018-05-11 | B |  |  |  | 802 Combustion Turbine | 16.21 | Natural Gas | 22.4 | MW | 22.4MW Solar Titan 250E Combustion Turbine with 130 MMBtu/hr Supplemental Burner. | Particulate matter, filterable &lt; 10 Âµ (FPM10) | EPA/OAR Mthd 201A | (Particulate Matter (PM)) | PM | N |  | 0.0089 | LB/MMBTU | 3 HR | BACT-PSD |  | U | 0 | U | 1.94 | LB/HR | 3 HR | 0 |  |  | 0 | 0 | N |  | When Combustion Turbine & Supplemental Burner are both in operation the following apply: <0.00885 lb/MMBtu <3.09 lb/hr
AL-0321 | KIMBERLY-CLARK MOBILE | KIMBERLY-CLARK CORPORATION - MOBILE OPERATIONS | MOBILE | AL | 36610 | USA | LEEANNE STICKLAND | 251 330 3464 | LEEANNE.STRICKLAND@KCC.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-2012 | 2621 | 322121 | 110058000000 | 08/21/2017 &nbsp;ACT | 10/11/2017 &nbsp;ACT | 2018-01-12 | 2018-05-11 | B |  |  |  | 801 Combustion Turbine | 16.21 | Natural Gas | 22.4 | MW | 22.4MW Solar Titan 250E Combustion Turbine with 130 MMBtu/hr Supplemental Burner | Particulate matter, filterable &lt; 10 Âµ (FPM10) | EPA/OAR Mthd 201A | (Particulate Matter (PM)) | PM | N |  | 0.0089 | LB/MMBTU | 3HR | BACT-PSD |  | U | 0 | U | 1.94 | LB/HR | 3 HR | 0 |  |  | 0 | 0 | N |  | When Combustion Turbine & Supplemental Burner are both in operation the following apply: <0.00885 lb/MMBtu <3.09 lb/hr
AL-0321 | KIMBERLY-CLARK MOBILE | KIMBERLY-CLARK CORPORATION - MOBILE OPERATIONS | MOBILE | AL | 36610 | USA | LEEANNE STICKLAND | 251 330 3464 | LEEANNE.STRICKLAND@KCC.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-2012 | 2621 | 322121 | 110058000000 | 08/21/2017 &nbsp;ACT | 10/11/2017 &nbsp;ACT | 2018-01-12 | 2018-05-11 | B |  |  |  | 802 Combustion Turbine | 16.21 | Natural Gas | 22.4 | MW | 22.4MW Solar Titan 250E Combustion Turbine with 130 MMBtu/hr Supplemental Burner. | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Other - 201a | (Particulate Matter (PM)) | PM | N |  | 0.0089 | LB/MMBTU | 3 HR | BACT-PSD |  | U | 0 | U | 1.94 | LB/HR | 3 HR | 0 |  |  | 0 | 0 | N |  | When Combustion Turbine & Supplemental Burner are both in operation the following apply: <0.00885 lb/MMBtu <3.09 lb/hr
AL-0321 | KIMBERLY-CLARK MOBILE | KIMBERLY-CLARK CORPORATION - MOBILE OPERATIONS | MOBILE | AL | 36610 | USA | LEEANNE STICKLAND | 251 330 3464 | LEEANNE.STRICKLAND@KCC.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-2012 | 2621 | 322121 | 110058000000 | 08/21/2017 &nbsp;ACT | 10/11/2017 &nbsp;ACT | 2018-01-12 | 2018-05-11 | B |  |  |  | 801 Combustion Turbine | 16.21 | Natural Gas | 22.4 | MW | 22.4MW Solar Titan 250E Combustion Turbine with 130 MMBtu/hr Supplemental Burner | Particulate matter, filterable &lt; 2.5 Âµ (FPM2.5) | Other - 201A | (Particulate Matter (PM)) | PM | N |  | 0.0089 | LB/MMBTU | 3 HR | BACT-PSD |  | U | 0 | U | 1.94 | LB/HR | 3 HR | 0 |  |  | 0 | 0 | N |  | When Combustion Turbine & Supplemental Burner are both in operation the following apply: <0.00885 lb/MMBtu <3.09 lb/hr
MI-0436 | CENTRAL POWER PLANT | THE REGENTS OF THE UNIVERSITY OF MICHIGAN | WASHTENAW | MI | 48109-1010 | USA | BRANDI CAMPBELL | 734-647-9017 | CAMPBELB@UMICH.EDU | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Ambrosia Brown, at 517-284-6788 or at browna39@michigan.gov, for technical questions regarding the permit. Thank you. | 2019-01-18 | 8221 | 611310 | Not Found | 04/17/2018 &nbsp;ACT | 08/23/2018 &nbsp;ACT | 2018-10-15 | 2019-02-20 | B |  | The facility supplies heating, cooling and electricity to campus buildings. | The &lsquo;&lsquo;Facilitywide Pollutants&lsquo;&lsquo; listed below are the emissions increases for the project and not for the entire university. | EU-CPP-CHPHRSG (combined heat and power unit) | 16.21 | Natural gas | 190.1 | MMBTU/H | The emission unit is a combined heat and power unit with heat recovery steam generator (HRSG). The primary fuel for the turbine is natural gas but it will be capable of firing ultra-low sulfur diesel (ULSD) as a backup fuel. The CTG has a rating of 190.1 MMBTU/H (HHV) on natural gas and 173.4 MMBTU/H (HHV) on ULSD. The HRSG is equipped with a natural gas-fired duct burner rated at 112 MMBTU/H (HHV). The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx combustion technology and SCR. | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of natural gas as the primary fuel and good combustion practices. | 0.019 | LB/MMBTU | WHEN FIRING NAT.GAS AT FULL LOAD | BACT-PSD |  | N | 0 | N | 3.5 | LB/H | WHEN FIRING ULSD AT FULL LOAD | 0 |  |  | 0 | 0 | N |  | No particulate emission control equipment previously listed for this type of equipment in RBLC for similar process.
MI-0436 | CENTRAL POWER PLANT | THE REGENTS OF THE UNIVERSITY OF MICHIGAN | WASHTENAW | MI | 48109-1010 | USA | BRANDI CAMPBELL | 734-647-9017 | CAMPBELB@UMICH.EDU | 5 | MI001 | MICHIGAN DEPT OF ENVIRONMENTAL QUALITY | MS. CINDY SMITH | (517)284-6802 | SMITHC17@MICHIGAN.GOV | Please contact the permit engineer, Ms. Ambrosia Brown, at 517-284-6788 or at browna39@michigan.gov, for technical questions regarding the permit. Thank you. | 2019-01-18 | 8221 | 611310 | Not Found | 04/17/2018 &nbsp;ACT | 08/23/2018 &nbsp;ACT | 2018-10-15 | 2019-02-20 | B |  | The facility supplies heating, cooling and electricity to campus buildings. | The &lsquo;&lsquo;Facilitywide Pollutants&lsquo;&lsquo; listed below are the emissions increases for the project and not for the entire university. | EU-CPP-CHPHRSG (combined heat and power unit) | 16.21 | Natural gas | 190.1 | MMBTU/H | The emission unit is a combined heat and power unit with heat recovery steam generator (HRSG). The primary fuel for the turbine is natural gas but it will be capable of firing ultra-low sulfur diesel (ULSD) as a backup fuel. The CTG has a rating of 190.1 MMBTU/H (HHV) on natural gas and 173.4 MMBTU/H (HHV) on ULSD. The HRSG is equipped with a natural gas-fired duct burner rated at 112 MMBTU/H (HHV). The HRSG is not capable of operating independently from the CTG. The CTG/HRSG is equipped with dry low NOx combustion technology and SCR. | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | P | Use of natural gas as the primary fuel and good combustion processes. | 0.019 | LB/MMBTU | WHEN FIRING NAT. GAS AT FULL LOAD | BACT-PSD |  | N | 0 | N | 3.5 | LB/H | WHEN FIRING ULSD AT FULL LOAD | 0 |  |  | 0 | 0 | N |  | No particulate emission control equipment previously listed for this type of equipment in RBLC for similar process.
MA-0041 | MEDICAL AREA TOTAL ENERGY PLANT | MATEP LIMITED PARTNERSHIP | SUFFOLK | MA | 2215 | USA | PETER GLUCKLER | (617) 598-2711 | PETER.GLUCKLER@VEOLIA.COM | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Edward Braczyk MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3289 Edward.Braczyk@state.ma.us | NE-14-013 | 4911 | 221112 | 110001000000 | 07/01/2015 &nbsp;ACT | 07/01/2016 &nbsp;ACT | 2017-01-04 | 2017-04-28 | B | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | MATEP proposes to construct and operate a new 14.4 megawatt (MW) combined heat and power (CHP) combustion turbine/heat recovery steam generator at the existing combined heat and power plant. | separate PSD permit under delegated program, and CPA approval (including state minor NSR for other pollutants) other facility-wide emission increase (not listed in next section): GHG(CO2e): 108,500TPY, Sulfuric Acid Mist: 2.55TPY, Lead: 0.1 TPY | Combustion Turbine with Duct Burner | 16.21 | Natural Gas | 203.4 | MMBTU/H | a nominal 14.4 Megawatt (MW) Solar Titan 130 Combustion Turbine Generator (164.6MMBtu/hr for NG firing, 158.8MMBtu/hr for ULSD firing) with Heat Recovery Steam Generator including a Duct Burner (38.8MMBtu/hr NG firing only). Max. ULSD usage: 878,400 gallons per 12-month rolling period | Particulate matter, total &lt; 10 Âµ (TPM10) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.02 | LB/MMBTU | 1 HR BLOCK AVG/EXCLUDING SS, NG FIRING | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 0.034 | LB/MMBTU | 1 HR BLOCK AVG/EXCLUDING SS, ULSD FIRING | 0 |  |  | 0 | 0 | N |  | PM10(firing NG): â‰¤3.29 lb/hr(no duct firing), â‰¤4.07 lb/hr(with duct firing); during start-ups (â‰¤3 hrs): â‰¤12.2 lb per event, during shutdowns (â‰¤1 hr): â‰¤4.1 lb per event; PM10(turbine firing ULSD): â‰¤0.034 lb/MMBtu(no duct firing), â‰¤0.031 lb/MMBtu(with duct firing), â‰¤5.40 lb/hr(no duct firing), â‰¤6.15 lb/hr(with duct firing); during start-ups (â‰¤3 hrs): â‰¤18.5 lb per event, during shutdowns (â‰¤1 hr): â‰¤6.2 lb per event.
MA-0041 | MEDICAL AREA TOTAL ENERGY PLANT | MATEP LIMITED PARTNERSHIP | SUFFOLK | MA | 2215 | USA | PETER GLUCKLER | (617) 598-2711 | PETER.GLUCKLER@VEOLIA.COM | 1 | MA001 | MASSACHUSETTS DEPT OF ENVIRONMENTAL PROTECTION | MR. MARC WOLMAN | (617)292-5515 | marc.wolman@state.ma.us. | Edward Braczyk MassDEP Northeast Regional Office 205B Lowell Street Wilmington, MA 01887 (978) 694-3289 Edward.Braczyk@state.ma.us | NE-14-013 | 4911 | 221112 | 110001000000 | 07/01/2015 &nbsp;ACT | 07/01/2016 &nbsp;ACT | 2017-01-04 | 2017-04-28 | B | http://www.mass.gov/eea/agencies/massdep/air/approvals/air-permits-and-approvals-issued-to-facilities.html | MATEP proposes to construct and operate a new 14.4 megawatt (MW) combined heat and power (CHP) combustion turbine/heat recovery steam generator at the existing combined heat and power plant. | separate PSD permit under delegated program, and CPA approval (including state minor NSR for other pollutants) other facility-wide emission increase (not listed in next section): GHG(CO2e): 108,500TPY, Sulfuric Acid Mist: 2.55TPY, Lead: 0.1 TPY | Combustion Turbine with Duct Burner | 16.21 | Natural Gas | 203.4 | MMBTU/H | a nominal 14.4 Megawatt (MW) Solar Titan 130 Combustion Turbine Generator (164.6MMBtu/hr for NG firing, 158.8MMBtu/hr for ULSD firing) with Heat Recovery Steam Generator including a Duct Burner (38.8MMBtu/hr NG firing only). Max. ULSD usage: 878,400 gallons per 12-month rolling period | Particulate matter, total &lt; 2.5 Âµ (TPM2.5) | Unspecified | (Particulate Matter (PM)) | PM | N |  | 0.02 | LB/MMBTU | 1 HR BLOCK AVG/EXCLUDING SS, NG FIRING | BACT-PSD | SIP , OPERATING PERMIT | U | 0 | U | 0.034 | LB/MMBTU | 1 HR BLOCK AVG/EXCLUDING SS, ULSD FIRING | 0 |  |  | 0 | 0 | N |  | PM2.5(firing NG): â‰¤3.29 lb/hr(no duct firing), â‰¤4.07 lb/hr(with duct firing); during start-ups (â‰¤3 hrs): â‰¤12.2 lb per event, during shutdowns (â‰¤1 hr): â‰¤4.1 lb per event; PM2.5(turbine firing ULSD): â‰¤0.034 lb/MMBtu(no duct firing), â‰¤0.031 lb/MMBtu(with duct firing), â‰¤5.40 lb/hr(no duct firing), â‰¤6.15 lb/hr(with duct firing); during start-ups (â‰¤3 hrs): â‰¤18.5 lb per event, during shutdowns (â‰¤1 hr): â‰¤6.2 lb per event.