## Small Combined Cycle Gas Turbin
RBLCID | FACILITY_NAME | CORPORATE_OR_COMPANY_NAME | FACILITY_COUNTY | FACILITY_STATE | FACILITY_ZIP_CODE | FACILITY_COUNTRY | FACILTY_CONTACT_NAME | FACILITY_PHONE | FACILITY_CONTACT_EMAIL | EPA_REGION | AGENCY_CODE | AGENCY_NAME | AGENCY_CONTACT | AGENCY_PHONE | AGENCY_EMAIL | OTHER_AGENCY_CONTACT_INFO | PERMIT_NUM | SIC_CODE | NAICS_CODE | FACILITY_REGISTRY_SYSTEM_NUMBER | COMPLETE_APPLICATION_DATE | PERMIT_ISSUANCE_DATE | DATE_DETERMINATION_ENTERED_INTO_RBLC | DATE_DETERMINATION_LAST_UPDATED | PERMIT_TYPE | PERMIT_URL | FACILITY_DESCRIPTION | PERMIT_NOTES | PROCESS_NAME | PROCCESS_TYPE | PRIMARY_FUEL | THROUGHPUT | THROUGHPUT_UNIT | PROCESS_NOTES | POLLUTANT | TESTMETHOD | POLLUTANT_GROUP(S) | CAS_NUMBER | CONTROL_METHOD_CODE | CONTROL_METHOD_DESCRIPTION | EMISSION_LIMIT_1 | EMISSION_LIMIT_1_UNIT | EMISSION_LIMIT_1_AVG_TIME_CONDITION | CASE-BY-CASE_BASIS | OTHER_ APPLICABLE_REQUIREMENTS | OTHER_FACTORS | PERCENT_EFFICIENCY | COMPLIANCE_VERIFIED | EMISSION_LIMIT_2 | EMISSION_LIMIT_2_UNIT | EMISSION_LIMIT_2_AVGERAGE_TIME_CONDITION | STANDARAD_EMISSION_LIMIT | STANDARD_EMISSION_LIMIT_UNIT | STANDARD_LIMIT_AVERAGE_TIME_CONDITION | COST_EFFECTIVENESS | INCREMENTAL_COST_EFFECTIVENESS | Cost_Verified | DOLLAR_YEAR_USED_IN_COST_ESTIMATES | POLLUTANT_COMPLIANCE_NOTES
AL-0282 | LENZING FIBERS, INC. | LENZING FIBERS, INC. | MOBILE | AL | 36505 | USA | MR. KEVIN, PLANT MANAGER ALLEN | 251-679-2814 | K.ALLEN@LENZING.COM | 4 | AL001 | ALABAMA DEPT OF ENVIRONMENTAL MGMT | MR. DALE HURST | (334) 271-7882 | ADH@ADEM.STATE.AL.US |  | 503-0047-X014 | 2823 | 325221 | 110044000000 | 11/19/2013 &nbsp;ACT | 01/22/2014 &nbsp;ACT | 2015-03-17 | 2016-05-09 | B |  | Production of lyocell fiber by solvent spinning process. | NAICS Code: 325220 | Gas Turbine with HRSG | 16.21 | Natural Gas | 25 | MW |  | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 18 | (Volatile Organic Compounds (VOC)) | VOC | A | CO oxidation catalyst and good combustion practices. | 1.6 | PPM | PPM VD @15% O2 WITH DUCT BURNERS | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0704 | UTILITY PLANT | M & G RESINS USA LLC | NUECES | TX |  | USA | MAURO FENOGLIO | (281) 874-8074 |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MICHAEL PARTEE | (512) 239-3312 | michael.partee@tceq.texas.gov | Mr. Sean O'Brien 512-239-1137 sean.obrien@tceq.texas.gov | 108819 PSDTX1354 | 4911 | 221112 | unknown | 02/22/2013 &nbsp;ACT | 12/02/2014 &nbsp;ACT | 2015-03-20 | 2016-05-09 | A |  | In support of the new PET (polyethylene terephthalate) unit and new PTA (terephthalic acid) plant proposed by M&amp;G Resins USA LLC, the company also proposes a Utility Plant that will consist of either one of two options. All steam generated from the Utility Plant will be used as process steam. There is no steam driven electrical generator. |  | cogeneration turbine | 16.21 | natural gas | 49 | MW | General Electric LM6000 natural gas-fired combustion turbine equipped with lean pre-mix low-NOx combustors. One heat recovery steam generator (HRSG) with 263 million British thermal units per hour (MMBtu/hr) natural gas-fired duct burner system containing a selective catalytic reduction system (SCR) | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | A | oxidation catalyst | 4 | PPMVD | @15% O2, 24-HR ROLLING AVERAGE | BACT-PSD |  | N | 0 | U | 0 |  |  | 0 |  |  | 0 | 0 | N
LA-0295 | WESTLAKE FACILITY | EQUISTAR CHEMICALS, LP | CALCASIEU | LA | 70669 | USA | JOSEPH BUSH | (337) 882-1615 | JOE.BUSH@LYONDELLBASELL.COM | 6 | LA001 | LOUISIANA DEPARTMENT OF ENV QUALITY | MR. BRYAN D. JOHNSTON | (225)219-3450 | BRYAN.JOHNSTON@LA.GOV | Permit writer: Anthony Randall, (225) 219-3417 or anthony.randall@la.gov | PSD-LA-806 | 2821 | 325211 | 110001000000 | 09/02/2015 &nbsp;ACT | 07/12/2016 &nbsp;ACT | 2016-08-10 | 2016-09-19 | D |  | Polypropylene manufacturing facility | Complete application date = date of administrative completeness Permit is for a retroactive PSD review. | Solar Titan 130 Gas Turbine with Unfired HRSG (3-08, EQT 323) | 16.21 | Natural Gas | 159.46 | MM BTU/HR | Turbine is subject to 40 CFR 60 Subpart KKKK. Output power at generator: 14.117 MW | Volatile Organic Compounds (VOC) | EPA/OAR Mthd 25A | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices, including good equipment design, use of gaseous fuels for good mixing, and proper combustion techniques consistent with the manufacturer's recommendations to maximize fuel efficiency and minimize emissions (see notes below) | 1.64 | LB/H | HOURLY MAXIMUM | BACT-PSD | OPERATING PERMIT | U | 0 | U | 0 |  |  | 2.5 | PPMVD @ 15% O2 | ANNUAL AVERAGE | 0 | 0 | N |  | Good combustion practices shall include monitoring of the flue gas oxygen content, combustion air flow, fuel consumption, and flue gas temperature. These parameters shall be maintained within the manufacturerâ€™s recommended operating guidelines or within a range that is otherwise indicative of proper operation of the emissions unit. PSD permit requires an annual stack test for VOC. If VOC < 75% of the permit limit, the frequency of the testing may be reduced to once every 2 years.â€¯ If result of any subsequent test exceeds 75% of the permit limit, resume annual testing.
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110060000000 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | THREE (3) AUXILARY BOILERS | 16.21 | NATURAL GAS | 218.6 | MMBTU/H, EACH | NATURAL GAS USAGE IN EACH BOILER NOT TO EXCEED 1501.91 MMCF/YR | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN | 5.5 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110060000000 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | THREE (3) AUXILARY BOILERS | 16.21 | NATURAL GAS | 218.6 | MMBTU/H, EACH | NATURAL GAS USAGE IN EACH BOILER NOT TO EXCEED 1501.91 MMCF/YR | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN | 5.5 | LB/MMCF | 3-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0173 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110060000000 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-07-17 | 2016-05-04 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | TWO (2) NATURAL GAS FIRED COMBUSTION TURBINES | 16.21 | NATURAL GAS | 283 | MMBTU/H, EACH | NATURAL GAS FIRED, OPEN-SIMPLE CYCLE COMBUSTION TURBINES WITH HEAT RECOVERY | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN | 2.5 | PPMVD AT 15% OXYGEN | 1-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
IN-0180 | MIDWEST FERTILIZER CORPORATION | MIDWEST FERTILIZER CORPORATION | POSEY | IN | 47620 | USA | MICHAEL CHORLTON | 3176258315 |  | 5 | IN001 | INDIANA DEPT OF ENV MGMT, OFC OF AIR | MR. MATT STUCKEY | (317) 233-0203 | mstuckey@idem.in.gov | PERMIT WRITER: DAVID MATOUSEK (317) 232-8253 DMATOUSE@IDEM.IN.GOV SECTION CHIEF: NATHAN BELL (317) 233-5670 NBELL@IDEM.IN.GOV | 129-33576-00059 | 2873 | 325311 | 110060000000 | 08/26/2013 &nbsp;ACT | 06/04/2014 &nbsp;ACT | 2014-08-12 | 2016-05-05 | A | HTTP://PERMITS.AIR.IDEM.IN.GOV/33576F.PDF | A STATIONARY NITROGEN FERTILIZER MANUFACTURING FACILITY |  | TWO (2) NATURAL GAS FIRED COMBUSTION TURBINES | 16.21 | NATURAL GAS | 283 | MMBTU/H, EACH | NATURAL GAS FIRED, OPEN-SIMPLE CYCLE COMBUSTION TURBINES WITH HEAT RECOVERY | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | GOOD COMBUSTION PRACTICES AND PROPER DESIGN | 2.5 | PPMVD AT 15% OXYGEN | 1-HR AVERAGE | BACT-PSD |  | N | 0 |  | 0 |  |  | 0 |  |  | 0 | 0 | N
TX-0551 | PANDA SHERMAN POWER STATION | PANDA SHERMAN POWER LLC | GRAYSON | TX |  | USA |  |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MICHAEL PARTEE | (512) 239-3312 | michael.partee@tceq.texas.gov | Ms. Tara Capobianco, P.E. 512-239-1117 tcapobia@tceq.state.tx.us | PSDTX1198 | 4911 | 221112 | UNKNOWN | 12/22/2008 &nbsp;ACT | 02/03/2010 &nbsp;ACT | 2010-04-05 | 2010-05-17 | A |  | A combined-cycle power plant producing a nominal 600 MW with two Siemens SGT6-5000F (501F) or two GE 7FA gas turbines. | State permit 87225 | Natural Gas-fired Turbines | 16.21 | Natural Gas | 600 | MW | 2 Siemens SGT6-5000F or 2 GE Frame 7FA. Both capable of combined or simple cycle operation. 468 MMBtu/hr duct burners. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 1 | PPMVD | @ 15% O2, 3-HR AVG, SIMPLE CYCLE MODE | BACT-PSD |  | U | 0 | U | 4 | PPMVD | @ 15% O2, 3-HR AVG, COMBINED CYCLE MODE | 0 |  |  | 0 | 0 | N
TX-0552 | WOLF HOLLOW POWER PLANT NO. 2 | STARK POWER GENERATION II HOLDINGS, LLC | HOOD | TX |  | USA |  |  |  | 6 | TX001 | TEXAS COMMISSION ON ENVIRONMENTAL QUALITY (TCEQ) | MICHAEL PARTEE | (512) 239-3312 | michael.partee@tceq.texas.gov | Ms. Ruth Alvirez 512-239-5220 ralvirez@tceq.state.tx.us | PSDTX1110 | 4911 | 221112 | UNKNOWN | 12/07/2007 &nbsp;ACT | 03/03/2010 &nbsp;ACT | 2010-04-05 | 2010-05-18 | B |  | A combined-cycle power plant generating a nominal 800 MW with either 2 MHI501G turbines or 2 GE 7FA turbines. | State permit 83638 | Natural gas-fired turbines | 16.21 | natural gas | 600 | MW | Project will be either 2 MHI501G gas turbines plus 230 MMBtu/hr duct burner firing for each turbine or 2 GE 7FA gas turbines plus 570 MMBtu/hr duct burner firing for each turbine. | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | P | Good combustion practices | 4 | PPMVD | @ 15% O2, 3-HR AVG, MHI501G | BACT-PSD |  | U | 0 | U | 3 | PPMVD | @ 15% O2, 3-HR AVG, GE 7FA | 0 |  |  | 0 | 0 | N
WY-0067 | ECHO SPRINGS GAS PLANT | WILLIAMS FIELD SERVICES COMPANY | CARBON | WY | 82336 | USA | CORTNIE MORRELL | 3078722880 | CORTNIE.MORRELL@WILLIAMS.COM | 8 | WY001 | WYOMING AIR QUAL DIVISION, AIR QUALITY | MR. ANDREW KEYFAUVER | (307)777-7340 | andrew.keyfauver@wyo.gov | MS. JAMIE SHARP WY DEQ AIR QUALITY DIVISION 122 WEST 25TH STREET CHEYENNE, WY 82002 307-777-7817 | MD-7837 | 1321 | 211112 | 110010000000 | 05/29/2008 &nbsp;ACT | 04/01/2009 &nbsp;ACT | 2009-04-02 | 2009-04-16 | A |  |  |  | TURBINE S37 | 16.21 | NATURAL GAS | 16162 | HP | 12,555 HP SOLAR MARS100-15000S OR 16,162 HP SOLAR TITAN 130-20502S TURBINE | Volatile Organic Compounds (VOC) | Unspecified | (Volatile Organic Compounds (VOC)) | VOC | N | GOOD COMBUSTION PRACTICES | 25 | PPV |  | BACT-PSD | NSPS , NESHAP |  | 0 |  | 3.7 | T/YR |  | 0 |  |  | 0 | 0 | N |  | BASELINE