## Oct 2025 ETT-WORKING
October 2025 ETT List
Note: Column titled "Est. New ETT Score" is the estimated new score based on the violations that have Returned to Compliance (RTCd) during the Quarter. Please note that this score will likely change on the next quarter's list due to further violations being generated. Comments submitted by Drinking Water Program staff on December 1, 2025.
Staff | RMW | Est. New ETT Score | System Information | 10 Point |  | 5 Point | [7 empty] | 1 Point | [11 empty] | General Comments | How to Return to Compliance | Known Hardware Problems
|  |  |  | SW | Nitrate | RTCR | SW | GWR | Nitrate | Arsenic | DBP | LCR | Rads | RTCR | SW | GWR | Arsenic | DBP | LCR | IOC | VOC | SOC | Rads | CCR | PN
BARNES | No RMW | 12 | AC ALASKA COMMERCIAL STORE / AK2270427 (475 / NTNC) | [5 empty] | 1 | [7 empty] | 3 | 1 |  |  |  | 2 |  |  |  | Overdue for nitrate (last sample 2023) arsenic (last Q sample 2024). System has not submitted an SOC waiver or SOC samples. System has not submitted DBP2 since 2023. | Collect Nitrate, Arsenic, VOC, SOC (or submit waiver), and DBP2 sample. | None known
NAKANISHI | YKHC | 41 | ALAKANUK WATER SYSTEM / AK2270362 (570 / C) | [7 empty] | 1 | [6 empty] | 29 |  |  |  | 2 |  |  |  | SOC sampling due in 2025, monthly TOC has not been submitted since 8/2021. Quarterly DBP's not taken in 2025. | Sample for SOC's or submit SOC waiver application. Take monthly TOC/Alkalinity samples from intake and treatment plant. Take quarterly DBP samples. | None known
SHARP | TCC | 17 | ALLAKAKET PUBLIC WATER SYSTEM / AK2300816 (135 / C) |  |  |  |  | 1 | [10 empty] | 2 |  |  | 6 |  | 1 |  | System did not complete 2023 CCR certification or 2023/2024 lead consumer notice certification. Has overdue survey deficiencies from their 2023 survey to address. System has not completed 2023-2025 SOC waiver, nor sampled for SOC. | Complete past due CCR and lead consumer notification steps and complete the 2023-2025 SOC waiver application. Must also correct all outstanding survey deficiencies. | None known
HOYT | No RMW | 17 | ALPINE INN / AK2244808 (30 / NC) |  |  | 2 | [7 empty] | 2 | [11 empty] | System has not completed seasonal start-up procedures or certification for 2024 and 2025 season. Open total coliform monitoring violations. | Submit seasonal start-up procedures and certification for 2026 season and collect total coliform sample. | None known
LATIMER | No RMW | 11 | AMORE MOCHA / AK2249069 (56 / NC) | [5 empty] | 1 |  |  |  |  | 5 | [11 empty] | System noted that a nitrate sample was collected Nov 17, 2025, when the positive TCR sample was collected. | System must collect/submit Nitrate sample in 2025. | None known
LATIMER | DEC | 13 | ANGOON PUBLIC WATER / AK2130017 (450 / C) | [14 empty] | 6 | 1 |  |  | 2 |  |  | 1 | System is still on BWN. PWS needs to consistently complete/submit MOR and on time. Results have not yet been received for samples collected in October. SOC waiver renewal received and under review. Progress overall has been good & monthly sampling was completed for Aug./Sept./Oct. 2025. | Sample TCR Monthly, & TTHM/HAA5 quarterly. | One storage tank remains out of commission. Pressure filters may need media added or replaced.
LATIMER | No RMW | 11 | BAY VIEW TRAILER COURT / AK2241101 (51 / C) | [5 empty] | 1 |  |  | 1 | [6 empty] | 1 | [6 empty] | System has not replied to recent requests for completion of LSLI & for updates on collecting overdue annual nitrate sample (which during October was noted as already collected in a phone conversation). | Complete LSLI, & collect nitrate sample by 12/31/2025. | None known
AGUE | BBAHC | 13 | CHIGNIK BAY WATER SYSTEM / AK2260228 (199 / C) | 1 | [14 empty] | 2 | [6 empty] | System has not submitted a complete monthly operator report since incurring a treatment technique violation for low chlorine residuals in June 2025, and last collected annual lead and copper samples in 2022. | Submit a complete monthly operator report showing adequate disinfection, and collect 5 lead and copper samples. | None known
SHARP | NSHC | 115 | DIOMEDE JOINT UTILITIES / AK2340141 (83 / C) |  | 2 |  |  |  |  | 10 |  |  |  |  | 39 |  |  |  | 2 | [6 empty] | Diomede continues to exceed the RAA MCL for Arsenic and Nitrate. System has continued to accrue monthly operator report violations since August 2023 for failure to submit complete operator reports primarily due to lack of a consistent full time operator. | System needs to begin using the new WTP in 2026. New plant should address Nitrate and Arsenic MCL exceedances. System needs to begin sending in complete monthly operator reports and complete overdue lead consumer notice process. | A new WTP was constructed to meet SWTR, Nitrate and Arsenic MCLs, and corrosion control. A temporary WTP operated during 2025 pumping season, but did not treat for arsenic or nitrate and is not operating within designated design parameters to meet SWTR. Permanent WTP granted operational approval in August 2025, but no source water was available to use new WTP to fill WST for winter. Current water in WST was treated with the temp plant. New WTP expected to start operating summer 2026.
AGUE | YKHC | 16 | EMMONAK WATER SYSTEM / AK2270299 (820 / C) | [8 empty] | 1 | [5 empty] | 3 | 2 |  | 1 | 2 |  |  |  | System did not complete Lead Service Line Inventory, 3 OEL Reports, or submit an SOC monitoring waiver renewal application. Overdue for VOC and lead and copper sampling. | Complete Lead Service Line Inventory and OEL Reports. Submit SOC waiver or sample, and collect VOC and lead and copper samples. | None known
MORRISON | No RMW | 29 | FOREST PARK TC / AK2210794 (175 / C) |  |  |  |  | 2 |  |  |  | 1 | [6 empty] | 2 |  | 4 | 2 |  |  | 1 | PwS has violations for not correcting significant deficiencies from the 2016/ 2019 surveys. Did not submit Lead Service Line Inventory. Did not sample for lead and copper in 2024. Has not sampled for VOC since 2Q 2024 and is on quarterly sampling schedule. | System must submit engineering plans to correct deficiencies. Sample for lead and copper, VOC and SOC. Submit LSLI. | System has ongoing issues with maintaining adequate distribution system pressure.
POEPPEL | YKHC | 62 | GRAYLING WATER SYSTEM / AK2280066 (195 / C) | 3 |  | 1 | [8 empty] | 23 |  |  | 2 | [7 empty] | System is behind on LT2 sampling. On long-term BWN until the PWS submits monthly operator reports and consistently samples. Storage tank is aged and too small to meet community needs. | Address the remaining sanitary defects. Submit monthly operator reports that meet operating requirements. Take LT2 samples according to LT2 sample plan. Take DBP samples in the correct months. | New water storage tank design has started. An ANTHC project to connect 10 homes to service has started. South loop water main distribution replacement plan set is anticipated to be completed by the end of 2025.
SHARP | TCC | 21 | HUGHES PUBLIC WATER SUPPLY / AK2300272 (107 / C) | [11 empty] | 14 |  |  | 1 | 4 | [6 empty] | PWS overdue for lead consumer notice certification since 2022. Did not complete 2024 DBP sampling. Despite submitting partial monthly operator reports (MOR) system has not submitted a complete MOR since October 2024. | System must submit complete monthly operator report, complete outstanding lead consumer notice process, and collect DBP sample during December 2025. | None known
HOYT | DEC | 26 | KAKE MUNICIPAL WATER / AK2130083 (415 / C) | [7 empty] | 5 | [14 empty] | Exceeding DBP MCL. System is trying to preform operational changes to lower values. Operator is working with RMW to find a solution for exceedances. | Collect set of samples that allows the LRAA to be calculated below the MCL. | Treatment plant upgrades may be needed.
CAHILL | No RMW | 29 | KING FOR A DAY / AK2299036 (53 / NC) |  |  | 3 |  |  | 1 |  |  |  |  | 7 | [11 empty] | PWS did not complete SSUP in 2023, 2024 or 2025 seasons. Last TC and Nitrate sample results are from 10/01/2023. Certified letter sent when system moved to monthly TC due to number of violations, but letter was not picked up. | PWS can return to compliance by taking annual Nitrate and monthly Total Coliform, and will need to complete and return 2026 seasonal startup procedures. Sanitary Survey due in 2026. | None known
HOYT | DEC | 99 | KLAWOCK / AK2120169 (904 / C) | [7 empty] | 19 | [14 empty] | Operator adjusted chlorine levels down in month of October, which can be observed in the monthly operator reports (Chlorine Average September 0.83 mg/L, October 0.65 mg/L). | Continue to collect DBP samples that allow for the LRAA to fall below the MCL. | System is looking for funding to replace anthracite in all four filters at the WTP.
SHARP | No RMW | 99 | KOTZEBUE MUN. WATER SYSTEM / AK2340060 (3234 / C) | [7 empty] | 19 | [14 empty] | System has exceeded the TTHM MCL since 2019 and the HAA5 LRAA since 3rd quarter 2023. | System needs to optimize their treatment system to increase DBP precursor removal and reduce DBP levels. | Monitoring of new WTP will continue throughout the interim operation period (extended to Jan. 19, 2026). DBP precursor removal data is to be analyzed by the design engineering firm to determine what treatment are needed to improve DBP results. Long term fixes are being designed for implementation this winter and include improving intake, and installing greensand filtration pre-treatment. A NF membrane pilot test was to determine DBP precursor removal efficiency was completed; results of pilot study not yet provided to DEC.
AGUE | YKHC | 31 | KWETHLUK NEW PIPED WATER SYSTEM / AK2272017 (760 / C) | [7 empty] | 6 | [14 empty] | System last collected DBP and DBP Precursor samples in May 2025. The HAA5 LRAA at the East Return Loop has exceeded the MCL since July 2024, and the TOC/Alkalinity removal ratio has remained below 1.0 since February 2024. | Collect DBP samples quarterly and DBP precursor samples monthly. | None known
BARNES | BBAHC | 11 | MANOKOTAK WATER SYSTEM / AK2260090 (293 / C) | [15 empty] | 1 |  | 1 | 6 |  |  |  | Overdue for Lead/Copper samples (last 2024). PWS has not collected VOC since 2013. System has not submitted SOC waiver or sampled quarterly for SOC. | System needs to collect VOC and SOC samples and collect a Lead/Copper sample set. | None known
AGUE | YKHC | 11 | MOUNTAIN VILLAGE WATER SYSTEM / AK2270150 (850 / C) |  |  |  |  | 1 | [9 empty] | 2 | 1 | 1 | [5 empty] | System is overdue for DBPs, lead and copper, and inorganics. Several significant deficiencies identified in the 2022 sanitary survey remain open. Operator is aware lead and copper samples are overdue but is having trouble finding people who are willing to allow sampling from their homes. | Collect DBP and lead and copper samples. Address open significant deficiencies. | System is on long-term BWN; lower loop of distribution system does not maintain pressure above 20 PSI. Open significant deficiencies from 2022 survey include: improperly abandoned well within 200' of an active well, issues with the caps or seals on 2 active wells, no backflow prevention on the water haul point, and a hose that is not NSF-certified at the water haul point.
HOYT | DEC | 42 | NANWALEK / AK2240464 (281 / C) | [10 empty] | 13 | 17 |  |  | 10 | [6 empty] | 1 | System has been on a BWN since February 2025. A new operator contacted EPS on 11/21/2025 and a list of outstanding sampling and tasks have been provided to the system. | Complete all routine sampling and submit completed monthly operator reports on time. Meet operator certification requirements. | None known
CAHILL | No RMW | 23 | PALMER LIFEWAYS DAYCARE / AK2226055 (56 / NTNC) | [6 empty] | 4 | [6 empty] | 1 | [8 empty] | System continues to have high Arsenic, Conditional Approval to Construct granted 02/18/2025 for installation of POU treatment. Two requests sent for public notice certification, missing 2nd and 3rd quarter. | System can return to compliance by testing below the Arsenic MCL after receiving approval to operate Arsenic treatment system. Also submitting public notice certification, missing 2nd and 3rd quarter 2025. | PWS plans to install POU treatment. Engineering construction approval has been granted.
NAKANISHI | No RMW | 12 | PETERS CREEK TERRACE / AK2211473 (70 / C) | [8 empty] | 1 | [6 empty] | 3 | [6 empty] | Lead service line inventory not completed in 2024, PbCu samples last taken in 2017, system is overdue for 2020 and 2023 sampling requirements. | System should complete Lead Service line inventory and sample for lead and copper. | None known
BARNES | YKHC | 14 | PLATINUM CITY WATER SYSTEM / AK2271059 (51 / C) |  |  |  | 1 | [13 empty] | 4 |  |  |  |  | System does not meet applicable water treatment and filtration requirements. System has not collected valid VOC sample since 2012. | System needs to collect VOC sample in 2025. | System does not meet applicable water treatment and filtration requirements.
KEIM | TCC | 16 | RUBY WATER SYSTEM / AK2360866 (215 / C) | [14 empty] | 14 | 1 | [6 empty] | System hasn't submitted a distribution chlorine sample since December 2023. PWS didn't follow proper sampling protocol and therefore 2024 lead/copper samples could not be used for compliance. | System must begin to collect a distribution chlorine sample at the same time and place as monthly TCR sample. System must collect lead/copper samples in 2025. | None known
LATIMER | No RMW | 13 | S & S CENTER / AK2244719 (54 / NTNC) | [8 empty] | 1 | [6 empty] | 1 |  |  | 2 |  |  |  | Owner/operator has not replied to most recent emails and voice msgs re lead site notices and SOC waiver renewal application. | Complete LSLI & quarterly SOC sampling or waiver renewal application. | None known
POEPPEL | DEC | 14 | SAINT GEORGE WATER SYSTEM / AK2260074 (65 / C) |  |  |  |  | 1 | [10 empty] | 4 | [6 empty] | Overdue for Lead/Copper samples last sampled in 2013. System has open significant deficiencies from 2021. | Sample for lead and copper. Address the outstanding corrective actions from the 2021 sanitary survey. | Old water storage tank is unstable/failing.
DAVIS | YKHC | 15 | SCAMMON BAY WATER SYSTEM / AK2270184 (637 / C) | [11 empty] | 10 | [10 empty] | System currently not monitoring or reporting daily turbidity. | Meet turbidity monitoring and reporting requirements. | System is awaiting parts and assistance to repair the turbidimeter and adjust calibration.
KEIM | Maniilaq | 21 | SELAWIK SAFEWATER FACILITY / AK2340379 (846 / C) | 1 | [6 empty] | 1 |  |  |  | 1 |  |  | 4 | 1 | [6 empty] | PWS received treatment technique violation in June for not maintaining entry point chlorine readings at or greater than 0.2 mg/L. Did not submit filtration performance information with June operator report. PWS exceeded LRAA MCL for 2nd Qtr. 2025 and has not sampled since July 2024, LRAA based on those results. Has also not completed DBP OEL report. PWS didn't sample for lead and copper in 2024. | PWS must keep their chlorine above 0.2 mg/L consistently and submit a complete monthly operator report. PWS must sample for lead and copper in 2025, DBPs in January 2026, and complete outstanding OEL report. | Latest sanitary survey indicates instrumentation that controls chemical dosing are not working and chemical pumps are in need of upgrading. MIOX disinfectant generator is not working and the dedicated CT contactor is not being used as intended; it appears calcium hypochlorite is only added at the WST heat-add loop which increases chlorine use and DBP formation potential. The WTP would benefit from an engineers evaluation of the treatment process to determine its needs and to find funding to make repairs and upgrades.
BJORKMAN | No RMW | 42 | SET FREE ALASKA SNODGRASS / AK2220483 (47 / NTNC) | [6 empty] | 8 | [15 empty] | Working with engineering. Plans for treatment were submitted 5/22/24, but system has not yet responded to request for information. | Install a form of treatment to lower levels below the MCL | None known
CAHILL | No RMW | 18 | SHEENA MAY ESTATES / AK2224337 (74 / C) | [6 empty] | 3 | [9 empty] | 1 | [5 empty] | PWS blends two sources to help mitigate high Arsenic. Arsenic sample collected in 1st quarter 2024 taken from incorrect sample point. RAA for 2024 = .011 Mg/L | PWS can return to compliance by testing below the Arsenic MCL. | None known
NAKANISHI | No RMW | 17 | SNOWCREST VIEW SOUTH / AK2210891 (25 / C) | [8 empty] | 1 |  | 1 |  |  |  |  | 6 |  |  | 2 |  | 2 |  | CCR overdue from 2024, SOC waiver needed for 2023-2025. Lead service line inventory not completed in 2024. Lead consumer notification overdue from 2023 and 2024. Total coliform samples last taken in May of 2025. | Complete CCR, SOC waiver application, 2 Lead Consumer Notifications, and Lead Service line inventory. Sample for total coliform. | None known
NAKANISHI | YKHC | 19 | ST. MARYS WATER SYSTEM / AK2270176 (548 / C) | [11 empty] | 15 |  |  |  | 3 | [6 empty] | Insufficient turbidity readings taken since March 2024. Last lead and copper samples taken 12/2023. | Take 20 Lead and copper samples every six months. Take turbidity readings every 4 hours while making water. | SCADA equipment is non-functional. WTP upgrade project and replacement of SCADA equipment is in PER stage.
HARRIS | No RMW | 12 | STERLING MOOSE RIVER MANOR / AK2249099 (33 / C) |  |  |  |  | 1 |  |  |  | 1 | [6 empty] | 1 | [6 empty] | Overdue on Lead Service Line Inventory, and correcting significant deficiency identified in a sanitary survey. | Complete and submit the LSLI to DEC for approval. Address open CASS schedule items identified in the 2023 sanitary survey. | None known
SHARP | No RMW | 16 | VALLEY WATER COMPANY / AK2310926 (1575 / C) | [8 empty] | 2 | [6 empty] | 1 | [6 empty] | Violation for lack of corrosion control was issued in 2006 and PWS still does not have corrosion control. PWS hasn't completed and submitted initial LSLI, due 10/16/2024. | System must install corrosion control to address high copper levels and submit LSLI. | The PWS is working through funding process to implement some of the corrective actions in the Master Plan, including ones related to copper exceedance. No information yet on project award or design start date.
SHARP | NSHC | 23 | WALES WATER SYSTEM / AK2340191 (173 / C) | [9 empty] | 6 | [5 empty] | 1 | [6 empty] | PWS exceeds Uranium RAA MCL. System changed sources to a SW source in fall 2024, but had to resort to old source after new source quantity issues. Did not collect required lead/copper samples in 2024 . | New SW source and WTP should reduce Uranium levels once fully brought online; however, repairs must be made to the new SW source intake in order for it to produce enough water to meet system demand. Wales must collect overdue lead/copper samples. | New surface water source with lower uranium and a cartridge filtration WTP were constructed and placed into operation (August 2024). In October 2024, the new source was not producing enough water to sustain the community so they have reverted to using the old groundwater wells and have been bypassing the new WTP since that time. Unsuccessful attempts to improve the new source were made in 2025. Additional attempts to fix the source will be made in summer 2026.
WHITEAKER | No RMW | 13 | WHITE BIRCH APARTMENTS / AK2313233 (72 / C) | [8 empty] | 1 | [6 empty] | 3 | [6 empty] | System only collected 4 out of 5 lead/copper samples in 2024 and has not completed their initial lead service line inventory. | System must submit a complete set of lead and copper samples and complete their lead service line inventory. | None known
KEIM | No RMW | 12 | WILDWOOD HOMES LLC / AK2310853 (114 / C) |  |  |  |  | 1 |  |  |  | 1 | [6 empty] | 1 | [6 empty] | PWS hasn't completed corrective actions from 2023 sanitary survey: modifications were made to the water system without prior approval from DEC and there is a separation distance issue between the well and wastewater lines. PWS hasn't completed and submitted initial LSLI. | PWS must continue to work with DWP engineering to complete sanitary survey corrective actions by submitting a complete waiver and other necessary information related to the modifications. PWS must complete and submit initial LSLI. | Comments were provided on a project to replace all water mains in the distribution, remove all private sewer lines, and remove all but one of the community sewer lines within the source well’s protective radius. A separation distance waiver was submitted and reviewed as part of the project (sanitary survey deficiency), but the project has been incomplete since June 2023. They will also need approval from the Wastewater Program for the project; no wastewater approval request has been received.

## Definitions+Contact List
DW Program Staff Contact Information
Mat-Su = Office located in Wasilla, AK. Covers the Mat-Su area. Staff: Jamie Bjorkman (Program Coordinator) 262‐3423, Jessica Cahill (EPS) 376-1824, Charity Bare (Engineering Supervisor) 262-3400
Northern = Office located in Fairbanks, AK. Covers the Northern Alaska PWSs. Staff: Teslyn Hakala (Program Coordinator) 451-3038, Michael Sharp (EPS) 451-2178, Jenny Roberts (EPS) 451‐2137, Gretchen Keim (EPS) 451-2231, Johnny Mendez (Engineering Supervisor) 451-5193.
Southcentral / ANC= Office located in Anchorage, AK. Covers Anchorage bowl, Prudhoe Bay, Bethel/YK Delta, Dillingham area, Aleutian Chain, Pribilof and Kodiak Island area PWSs. Staff: Leslie Morrison (Program Coordinator) 269-7619, Elizabeth Nakanishi (EPS) 269‐7517, Kristine Poeppel (EPS) 269‐7521, Monica Ague (EPS) 269-7653, John Davis (EPS) 262-8201, Karis Barnes (EPS) 262-8204, Chris Pletnikoff (Engineering Supervisor) 269‐6064.
Kenai / Southeast = Office located in Soldotna, AK. Covers the Kenai Peninsula and Southeast area. Staff: Jamie Bjorkman (Program Coordinator) 262‐3423, James Latimer (EPS) 262-3410, Christina Harris (EPS) 262-3420, Emily Hoyt (EPS) 465-5108, Charity Bare (Engineering Supervisor) 262-3400
GENERAL ETT QUESTIONS: Jeanine Vance (EPM) 269-2007, Karen Garland (EPS) 269-7576, Eric Burg (EPS) 262-3401
Link to DW Program Directory (contact information) | http://dec.alaska.gov/eh/dw/contact/
Resource Links
Alaska Community Database Online
The Community Database Online is a portal for information resources about Alaskan Communities and Places of Interest in an interactive format.
Link to Database Online Webpage | https://dcra-cdo-dcced.opendata.arcgis.com/
Alaska Community Photo Library
The Community Photo Library offers a glimpse into Alaska's communities and lifestyle by providing images of places, people, cultural events, public facilities, landscapes, and other dimensions of community life.
Link to Photo Library Webpage | https://www.commerce.alaska.gov/dcra/admin/Photo
Remote Maintenance Worker (RMW) Service Area Abbreviations
BBAHC= Bristol Bay area Health Corporation | Maniilaq= Maniilaq Health Corporation | TCC= Tanana Chiefs Conference
DEC= AK Department of Environmental Conservation | NSHC= Norton Sound Health Corporation | YKHC= Yukon Kuskokwim Health Corporation
No‐RMW= Not served by an RMW Program
Link to RMW Directory | https://dec.alaska.gov/media/p4dntxhf/rmw-directory.pdf
Definitions
AL= Action Level | IFE= Individual Filter Effluent | RMW= Remote Maintenance Worker
ANTHC= Alaska Native Tribal Health Consortium | IOC= Inorganic Chemicals | RTC= Return to compliance (fall off ETT list)
BACTI or t‐Coli = Total Coliform Sample | LCR= Lead/Copper Rule | RTCR= Revised Total Coliform Rule
BWN= Boil Water Notice | LRAA= Locational Running Annual Average (Stage 2) | SOC= Synthetic Organic Chemicals
CCR= Consumer Confidence Report | LT1= Long Term 1 Enhanced Surface Water Treatment Rule | Surface Water (SW)= Surface Water violations Surface Water Treatment Rules (SWTR, LT1, and LT2)
CFE= Combined Filter Effluent | LT2= Long Term 2 Enhanced Surface Water Treatment Rule
DPB= Disinfection by Products | M/R= Monitoring and Reporting (type of violation) | SSUP = Seasonal Startup Procedures
DSRD= Distribution Chlorine Residual | MCL= Maximum Contaminant Level (type of violation) | TC= Total Coliform (also called Bacti)
EHO= Environmental Health Officer | MOR= Monthly operator report | TOC= Total Organic Carbon
EP= Entry Point | NOV= Notice of Violation | TCR= Total Coliform Rule
EPA= Environmental Protection Agency | OCC= Optimal corrosion control (Lead/Copper Rule) | TT= Treatment Technique (violation)
EPRD= Entry Point Residual Distribution | PE= Public Education (requirement under Lead/Copper Rule) | TTHM= Total Trihalomethanes (Stage 1 Rule)
ETT= Enforcement Targeting Tool | PER= Preliminary Engineering Report | VOC= Volatile Organic Chemicals
FANLs= Facility Analyte Level (refers to SW/DBP monitoring requirements) | PN= Public Notice | VSW= Village Safe Water
GAC= Granular Activated Carbon | PWS= Public Water System | WTP= Water Treatment Plant
GWUDI= Groundwater under the direct influence of surface water | RAA= Running Annual Average
HAA5= Haloacetic Acids (Stage 1 Rule) | Rads= Radionuclides Rule