## Community Readiness
DEC Western Alaska Community Recovery & Readiness
Community | Drinking Water | Sewer/Wastewater | Fuel/Contamination | Solid Waste/Landfill | Honey Bucket | Lead Program/Next Step | Notes - Water/Drinking Water | Notes - SPAR | Notes - Landfills
Bethel | ✅ Operating | ✅ Functioning | ✅ None Identified | ✅ Stable | N/A | Regional hub
Chefornak | ✅ BWN lifted 10/22; system functional | ✅ Functioning - Additional repairs still needed | ⚠️ Limited access | ⚠️ Wet conditions | ✅ Functional | RMW oversight, DW | Update 10/30: DEC engineers inspected the water treatment plant on October 26 and found no storm-related damage. A total coliform sample collected October 14 was negative, and a VOC sample collected October 26 showed non-detect results for all VOCs. The Drinking Water Program Manager spoke with Chefornak City Administrator Leticia to share the results of VOC, lead, and total coliform testing. The water has been confirmed safe for all potable uses. Leticia will notify residents via text and has the program manager’s direct line for any questions. YKHC RMW Sanderson traveled to assess the sewer line in Chefornak. He found about 500 feet of sewer main that is off its supports and turned 90 degrees from where it should be. YKHC RMWs are formulating a plan to address this. This will be a major effort and will require equipment to lift the pipe. Update 10/31: The wastewater force main serving the LKSD school and community washeteria was displaced from its supports and shifted from its normal discharge point, but it appears to still function. YKHC RMWs are planning repairs, which will require heavy equipment, with more details expected in the next day or so. | Update 10/31: SPAR and SW staff along with representative from Forestry ops made contact with owners of the community store and tank farm operator. Reported no interruptions to fuel support or leaks from the tank farm were reported. | Update 10/31: The landfill is accessible.
Eek | ✅ System functional | ✅ Functional | ✅ None Identified | ✅ Accessible | ✅ Active | EH DW support
Goodnews Bay | ✅ Operating | ✅ Working | ✅ None Identified | ✅ Stable | ✅ Functional | EH DW support
Golovin | ✅ In compliance | ✅ Functional | ✅ None Identified | ✅ Stable | ✅ Functional | EH monitoring
Hooper Bay | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | EH monitoring
Kipnuk | ⚠️ Boilers and heat loops online; circulation stabilization in progress | ✅ Functioning - Additional repairs still needed | ⚠️ Fuel sheens widespread | ⚠️ Debris throughout site | ⚠️ Needs assessment | SPAR & VSW | Electricians are onsite working to connect temporary generators and plan permanent electrical grid repairs. 15 community members are staying in the school; a few residents flew to Anchorage for supplies. Power wires are down throughout the community, many homes washed off the foundation (stilts), many boardwalks are damaged, sewage and water lines have flood debris lying on them. RMWs indicates community wastewater system is functional but does need follow-on repairs that exceeds the RMW capacity. We are reaching out to ANTHC to coordinate response. Update 10/30: Remote Maintenance Workers (RMWs) drained the water plant on October 16 to prevent freezing until power can be restored. Records show the community and school operate on separate systems, with the school maintaining its own source and treatment plant. ANTHC and YKHC staff were on site October 28 to assess whether the school system could provide potable water for reconstruction efforts. No post-storm total coliform or VOC samples have been collected from either system. The contractors have the backup generator operating on a 55-gallon drum while they work on getting it piped to the bulk fuel tank. The operator got the boilers and glycol loops running and circulating. RMW White worked with the operator over the phone to ensure that the necessary components were turned on in the correct sequence. We brought the circulation pumps on and then the boilers. We then brought on each of the heat loops to the raw water line, water storage tank, sewer force main, and school water line. The plan is to let them all run and stabilize overnight, then start thawing the respective lines before bringing anything else back online. We will be sending Willie in on the 30th to assist the operator. | Two DEC responders assessed Kipnuk on Wednesday, October 22nd with the USCG. Responders report a lot of miscellaneous tanks and drums that floated during the storm and are now orphaned as debris. Fuel or sheen is observed in almost every puddle under ice. Under the federal disaster declaration USCG will hire Alaska Chadux Network for response to oil spill concerns. Update 10/31: On October 29, Alaska Chadux retrieved and secured additional small storage oil and oil product containers based on previous assessments. The Chadux team built another containment site to secure collected miscellaneous oily and oil product containers for temporary storage over the winter. | Based on communication with community it is likely that access to the site is limited and that the landfill was likely damaged in the storm. At its closest point, this site is 45 feet south of a large tundra pond and 75 feet NW of the sewage lagoon. Since cover material is not applied regularly to waste and they utilize minimal compaction there is a high risk of rising flood waters carrying waste from the landfill into the pond and/or lagoon. Update: 10/24/25: DOT Imagery shows that at least 75% of the landfill is inundated with water. Waste in the tundra pond is not visible (high water) and may have floated out of the fenced area but no visible debris to the south of the site. Fences may have withstood the storm impacts, no visible breaches. Waste seen north of the landfill may have been staged prior to the storm. Extensive damage to structures and debris throughout the site. Damages to several board walks, including road to landfill.
Kongiganak | ⚠️ Raw line detached; repairs ongoing | ⚠️ Functional backup | ⚠️ Potential contamination | ⚠️ Limited landfill capacity | ✅ Operational | RMW & SPAR | Update 10/30: RMWs are on site repairing the damaged and partially frozen raw water line. The community has enough water in storage to last through February. RMWs are developing a plan to begin pumping from an alternate raw water source in January. A VOC sample collected October 23 showed non-detect results, and DEC will work with the community to obtain a current coliform sample. Update 10/31: The RMW team moved and fused back together 1800+ feet of pipe. The remaining gap between the two ends of pipe is 850 feet. The main pump being down for service and the back up pump breaking delayed the pump effort or it would have been completed before the storm. | Update 10/30: DEC staff, including two SPAR responders, visited Kongiganak on October 28. Due to travel constraints, the team was on the ground for about two hours. Three unidentified drums or tanks were located, but no visible oil or hazardous material releases were observed. The team also noted that piping from a residential sewage tank had detached from the house. A spill site was inspected along the cross-town fuel transfer line that supplies the teacher housing tank. The line was closed at the time of the incident, and approximately 800 gallons of fuel oil were drained from the section. Repairs were completed the same day. Field readings showed low vapor levels (60 ppb) with frozen ground limiting fuel migration. Minor soil removal and in-place burning were conducted to aid cleanup. Additional remediation is recommended when conditions allow. | Section of boardwalk/bridge to landfill is missing 8 ft of boards. Other minor damages reported along road to landfill and images show single boards missing throughout boardwalk to landfill. No images or assessment of landfill or salvage area.
Kotzebue | ✅ In compliance | ⚠️ Lagoon erosion; pipe displacement | ⚠️ Minor household spills | ✅ Landfill good | N/A | SPAR, City crews | The main findings in Kotzebue are erosion concerns along the bridge on Ted Steven’s Road, the sewage lagoon 3, and along Front Road. Ted Stevens road is 1 of 2 evacuation points out of town and is still closed and was actively under construction. Sewage concerns include interruptions to lift stations 4, 9, and 12. 4 has been returned to service but 9 and 12 are on bypass. There are several sewer lines to residences that have experienced erosion and flood waters have caused pipes to rise out of earthen trenches and be displaced. These have since frozen and burst. | Lift Station 9 junction box was fully submerged in the flood and was damaged. Lift station 12 was also fully submerged and electrical components damaged. New pumps and controls have been ordered and are enroute. Sewage backups in 3 homes are likely due to flushing rags down the system. Kotzebue spent 6 hours on 10/26 clearing a basketball size clump of rags from system. DEC RMW offered assistance with RMWs and they indicated they would call if they needed additional assistance.
Kwigillingok | ✅ In compliance | ⚠️ Lagoon road access washout; haul trailer repairs pending | ⚠️ Priority A fuel response; contractor mobilizing to secure displaced and at-risk tanks, assess damaged fuel dispenser; results pending. | ⚠️ Main landfill inaccessible; unpermitted site washed out | ✅ Functional | VSW, EH, SPAR field teams; contractors deploying 10/29 | RMWs began work on reattaching and restoring the raw water supply line for the drinking water system today. Significant debris and boats were entangled with the line and were moved. In some places the line was as much as 300 feet out of place. RMWs remain on site as of 10/24 and are working on restoring the heat trace to the raw water intake line. The raw water line is connected, but now has frozen segments preventing full use of the intake line. Once the heat trace is functional and sufficient glycol is available, the intent is to thaw the line and resume pumping water to resume drinking water production. 10/23 estimates for remaing stored potable water is at 40,000 gallons. Update 10/30: RMWs have been repairing the damaged raw water line that carries source water to the treatment plant. The finished water tank currently holds about 40,000 gallons of safe, treated water that was not affected by flooding. A VOC sample collected October 23 showed non-detect results, and DEC will assist with new coliform sampling once the system is fully operational. A YKHC and a Norton Sound Health Corp RMW will travel to Kwigilingok and make repairs to the school's sewer line to the lagoon, and work on other sewer issues with home dog houses. Update 10/31: The honey bucket disposal lagoon appears to be functioning normally. There is a washout near a culvert along the access road to the lagoon and DOT is in the process of repairing the washout with gravel (with other repairs). The haul trailers are in the process of being repaired but are awaiting new pumps to complete the repairs. | DEC identified roughly 12 displaced 500-gallon or larger oil storage tanks in the community and numerous 500- to 10,000-gallon oil storage tanks with compromised foundations that are at risk of spilling. SPAR has issued a TRFP for a contractor to recover and secure displaced oil and hazardous substance containers within the community itself, including tanks and drums, stabilize or empty tanks at risk of tipping or leaking, and create a safe and secure location for storage of oil and household hazardous waste over the winter for future transportation and disposal. The contract should be awarded on October 28th with desired mobilization on October 29th. The fuel dispenser for the bulk storage tank farm was damaged in the storm and is non-operable forcing the community to manually transfer fuel. The SPAR TRFP directs the contractor to assess damage to the Kwig, Inc. tank farm fuel dispenser and be prepared to conduct repairs upon DEC's direction under an approved request from the SEOC. Update 10/30: Working with contractor and air carrier in Bethel to get contractor on-site on/before 11/1. Detailed SCOPE OF WORK meeting with contractor scheduled for 10/31. | This site is at high risk of erosion. Since waste has not been covered there is a strong chance that flood waters have picked up and carried waste downstream into the community and the ocean.
Marshall | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional
Napakiak | ✅ In compliance | ⚠️ Lagoon integrity under review | ⚠️ Used oil spill at two homes | ⚠️ Landfill saturated | ✅ Operating | RMW, EH, SPAR | Drinking water system was flooded, but well has been chlorinated and tested satisfactory. Water production has resumed normally. The Flush, Tank, Haul (FTH) system suffered widespread damage at most homes. “Doghouses” which provide insulation were displaced, but all but one were salvagable. A wide variety of clamps and fitting are needed for repairs since the system spans decades and the designs have changed over time. The honebucket lagoon appears intact, but will require pumpout in spring, but a dewatering pump is needed at that time. Update 10/30: DEC engineers inspected the system on October 23–24 and confirmed that the well was overtopped by floodwaters. The well was shock chlorinated, and all three coliform samples collected on October 14 were negative. A VOC sample collected October 24 was non-detect for all VOCs, and the system continues to produce water normally. | Biggest SPAR concern was reported vapor intrusion and fuel spill inside the post office but the building was locked so DEC wasn’t able to assess. SPAR will follow up with the post master. A dozen or so HHOT that have kinked fuel lines or were knocked off their stands. With new snow and ice the team wasn’t able to reassess the sheening observed on October 20th. | SW staff visited community on 10/23/25. Site is accessible, no road damage. Landfill did flood during the storm and ponded water still remaining in site. Landfill operator reported potential leachate seep to DEC (not SW) and it was inspected. Flood waters carried waste north of the site. Homes took on flood water and there is likely large amounts of structural damage.
Napaskiak | ✅ BWN lifted 10/22; system functional | ⚠️ Localized issues | ⚠️ Minor diesel spill near city office; small household spills | ⚠️ Wet landfill; access limited - regular garbage operations to resume soon | ✅ Collection resuming | SPAR follow-up; EH monitoring | Update 10/30: DEC engineers inspected the water treatment plant on October 22 and confirmed it was unaffected by the storm. The system continues to operate normally. A total coliform sample collected October 16 was negative, and a VOC sample collected during the inspection showed non-detect results. |  | Waste collection has been paused due to the wet conditions in the landfill. SW Staff on site on 10/23/25 and noted that MSW is piling up at the entrance to the site. Waste should move in once ground is harder. Minimal structural damage and the community has been able to pick up the small amount of storm debris which will go into the LF when collection resumes.
Nightmute | ✅ In compliance; BWN for general traditional water sources is still in effect; School is still awaiting VOC results. | ⚠️ Minor leak near teacher housing; functional school system | ⚠️ Fuel contamination in multiple homes | ⚠️ Waste flooded into town; cleanup underway | ✅ Lagoon functional; pit trench not needed | DW Eng., SPAR, VSW field follow-up+I16 | The Nightmute Water Treatment Plant building appears to have shifted and has impacted the well casing. The well casing is intact but is leaning over a bit. They are able to make water, but there was concern about fuel contamination. While in Nightmute, staff discovered a source of drinking water that is being used by approximately half of the village population. It appears to be a culvert in a stream where people are collecting untreated surface water. The Drinking Water program issued a general BWN for traditional sources to Nightmute on 10/24/25. This is just a precaution to alert people to the possible dangers of drinking untreated surface water, it is not regulatory. The Drinking Water program tested both the community and school water systems for E. coli; results showed no coliforms, and the water is safe to drink. However, the nearby stream used as a traditional water source contained coliforms and should be boiled for at least two minutes before consumption. DW engineers examined the school’s water treatment system but could not collect a VOC sample due to objections from the principal. ***YKSD Water Operator will take VOC sample Update 10/30: Both the community and school water systems tested absent of coliforms, indicating safe drinking water. A VOC sample collected from the community well on October 26 showed non-detect results for all VOCs. The school operator will collect additional VOC samples for lab analysis. A boil water notice remains in effect for traditional surface water sources, which should be boiled for at least two minutes before drinking. YKHC RMWs White and Kamuck arrived in Nightmute on October 29, 1925, and were able to address the main leak at the teacher housing. Reinsulated the sewer junction box that the storm destroyed. One remaining leak to address, but it is a small leak in an individual teacher housing unit. | SPAR was in Nightmute on October 21st and reported 16 damaged houses and at least half of those structures needed their heating oil tanks restored. At the direction of the SEOC, SPAR has been trying to coordinate assistance from DOT to get the heating oil tanks replumbed. DOT is aware of the need and the ask but it is unclear if they’ve added it to their task scope. On October 25th DMVA reported 15-18 homes that are impacted by fuel fumes and contamination and that cannot be reoccupied. SPAR assessed houses on October 26th for concerns of indoor fuel odors. Impacted homes are still wet and there are significant indoor air quality concerns beyond any potential fuel impacts. SPAR packaged and is shipped boot cleaning station kits and additional personal protective equipment to Nightmute on October 27th as space allows on flights to address needs identified while in the community yesterday (26th). SPAR is aware of reports of widespread fuel odor along the riverbank near the old tank farm prior to the recent snowfall when rocks are dislodged and odor in a swale that runs through a residential street. Additional oil spill response and soil clean up is necessary in the community, especially preparing for spring break-up. | The landfill and lagoon were compromised, and debris impacts are widespread; the National Guard is assisting with removal, and the City has authorization to place debris in a monofill at the new Class III site. The water system is operational; a precautionary BWN remains active due to ongoing use of untreated surface water by some residents, and a filtration unit was installed on 10/25 to support safe meal preparation. Road/boardwalk repairs are ongoing, debris remains along transportation routes, and a phased return is underway as infrastructure stabilizes. Update 10/30: The temporary debris disposal site approved for disaster cleanup is currently difficult to access. The tundra mat road leading to the site can only be reached by four-wheeler, making it impossible to haul large debris supersacks at this time. The community’s regular landfill, located across the river, is also inaccessible. Details on the cause of the inaccessibility are still being confirmed. As a result, the community currently does not have a reliable way to manage day-to-day household waste. Update 10/31: SW staff visited Nightmute yesterday and spoke with DOT and DOT contractors to improve access to the permitted monofil to assist with debris removal.
Nome | ✅ In compliance | ✅ Functioning
Nunam Iqua | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | EH | Update 10/31: The RMW in Nunam Iqua reported that the operator plans to reinstall the summer intake pump on Monday. The four feet of water currently available is sufficient until pumping resumes. The summer pump had been removed for winter preparations, but the ice isn’t thick enough yet to install the winter setup. VOC test results showed non-detect results.
Nunapitchuk | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | EH/SPAR coordination
Oscarville | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | SPAR closeout 10/24 | Update 10/30: The Oscarville systems are non-public because they serve fewer than 25 people, and the Washeteria is not currently in use. DEC engineers inspected the school’s water system on October 24 and collected samples for coliform and VOC testing. Both coliform samples were negative; VOC results showed non-detect results. The school currently has 19 students, including three evacuees from Kwigillingok. |  | Solid Waste staff visited Oscarville on 10/24/25. A fair amount of trash around community, some trash was reportedly washed out of landfill by flooding.
Quinhagak | ✅ In compliance | ⚠️ Lagoon erosion risk | ⚠️ Fuel line damage; minor | ✅ Landfill ok | N/A | DOT/DEC/VSW coordination | The wastewater system appears to be functioning. There is concern erosion from the storm is approaching the sewage lagoon. An ARUC engineer has assessed the lagoon and erosion. It appears there is no immediate threat to the lagoon from the ARUC report. A plan is emerging through coordination with DOT, ARUC, DEC and the community to use locally sourced material to add reinforcements to the beach to protect the lagoon from further erosion during the 2025/26 winter storm season. Update 10/30: RMWs have been on site conducting repairs to the system’s controls and intake line. Three wells remain operational. The operators have been working to raise the raw water line and reattach it to all sleepers. Five total coliform samples collected October 22 were negative. A VOC sample collected October 24 showed non-detect results. |  | Landfill access has not been impacted. The storm caused erosion of landfill entrance, but not listed as a primary concern. This site is only 600 ft W of the ocean and is threatened by erosion. The community could find a new location for a monofill that could be converted into a Class III site.
St. Michaels | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | SPAR closeout 10/24 | General updates for Stebbins and St. Micheal include general wind damages to homes, sheds, smoke houses including roof, wall, windows, and some sheds and smoke houses demolished. Main community concerns consist of listing power lines in both communities.
Stebbins | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | SPAR closeout 10/24 | See St. Michael's for notes
Teller | ✅ In compliance | ✅ Functioning
Toksook Bay | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functioning | EH DW closeout |  |  | Access to the landfill has not been impacted. DOT has noted moderate potholing along the landfill road.
Tuntutuliak | ⚠️ Surface source; turbidity high; BWN in effect | ✅ Working | ⚠️ Minor sheen near storage | ⚠️ Access issues | ✅ Collection ongoing | EH & SPAR | Update 10/30: RMWs have confirmed no damage to the washeteria. The well was overtopped during flooding, but a total coliform sample collected October 20 was negative. The community remains under a long-term boil water notice unrelated to the storm. A VOC sample collected October 23 showed non-detect results.
Tununak | ✅ BWN lifted 10/22; system functional | ⚠️ Wastewater partial | ⚠️ Limited supplies | ⚠️ Capacity limited | ✅ Active | EH DW field crew | DW conducting hydrocarbon testing for ground water system. |  | The Tununak River Bridge (#1385) has lost roughly half of the roadway width for roughly 100 ft extending toward town along the ocean side. DOT has not listed this as a primary concern, but it should be watched since the landfill is only accessible via this bridge.
Most recent updates in RED
This document is a working draft prepared by the Alaska Department of Environmental Conservation (DEC) for situational awareness and coordination purposes. The information contained herein represents the best available data at the time of compilation and is subject to change as field conditions, assessments, and community reports are updated. This spreadsheet should not be interpreted as a final verification of community readiness or infrastructure condition. Data may be incomplete, unverified, or based on preliminary assessments. DEC and partner agencies continue to refine and validate information through ongoing field operations and coordination with local, Tribal, and federal partners. For official updates or confirmed public health and environmental safety information, please refer to communications released directly by DEC or the State Emergency Operations Center (SEOC).