## Total Capital Investment
Shaded cells indicate user inputs.
Total Capital Investment - DSI (Dry Sorbent Injection) | [7 empty] | Date: | 2022-12-28 | Total Capital Investment - DSI (Dry Sorbent Injection) | [7 empty] | Date: | XX/XX/2023
Project: |  | UAF - BACT Analysis | [5 empty] | Prepared By: | M. Jahn | Project: |  | UAF - BACT Analysis | [5 empty] | Edited By: | D. Jones
Vendor: |  | BACT Process Systems, Inc. | [5 empty] | Updated By: | C. Kimball | Vendor: |  | BACT Process Systems, Inc. | [5 empty] | QA By: | M. Coss
[8 empty] | Rev: | B | [8 empty] | Rev:
Capital Costs | [9 empty] | Capital Costs
DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  |  | DIRECT COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST
(1) | Purchased equipment and material costs | [8 empty] | (1) | Purchased equipment and material costs
| (a) | Basic equipment | [8 empty] | (a) | Basic equipment
|  | DSI System | 1 | EA | 5875000 | [6 empty] | DSI System | 1 | EA | 4700000
|  | ID Fan | 1 | EA | 431588.04 | [6 empty] | ID Fan | 1 | EA | 431588.04
|  | Total DSI System | [5 empty] | TOTAL = | 6306588.04 |  |  | Total DSI System |  | A | Equipment Cost (EPA CCM) |  |  | TOTAL = | 5131588.04
| (b) | Instrumentation | [8 empty] | (b) | Instrumentation
|  | Total Instrumentation | 1 | EA | 142000 | [6 empty] | Total Instrumentation | 1 | EA | 10% | CCM Table 1.8
[8 empty] | TOTAL = | 142000 | [8 empty] | TOTAL = | 513158.804
| (c) | Freight | [8 empty] | (c) | Freight
|  | ID Fan Freight | 1 | EA | 85120 | [6 empty] | ID Fan Freight | 1 | EA | 5% | CCM Table 1.8
[8 empty] | TOTAL = | 85120 | [8 empty] | TOTAL = | 256579.402
| (d) | Extended Outage Costs | [8 empty] | (d) | Extended Outage Costs
|  | Additional days beyond a typical 3 week outage | 35 | Days | 48028 | [6 empty] | Additional days beyond a typical 3 week outage | 0 | Days | 0
[8 empty] | TOTAL = | 1680980 | [8 empty] | TOTAL = | 0
| (e) | Vendor representatives Costs | [8 empty] | (e) | Vendor representatives Costs
|  | Onsite Vendor Representatives Costs (enter no. of days and daily rate) | 5 | Days | 2000 | [6 empty] | Onsite Vendor Representatives Costs (enter no. of days and daily rate) |  | Days
[8 empty] | TOTAL = | 10000 | [8 empty] | TOTAL = | 0
Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor scope. |  |  |  |  | PEMC = | 8224688.04 | Purchased Equipment and Material Cost (PEMC) |  |  | All above costs included in vendor scope. |  |  |  |  | PEMC = | 5901326.246
(2) | Direct Installation Costs | [8 empty] | (2) | Direct Installation Costs
| (a) | Concrete | 1 | LOT | 98000 |  |  |  | 98000 |  | (a) | Foundations & Support | 1 | LOT | 12% | CCM Table 1.8 |  |  | 708159.1495
| (b) | Site Vibro Compaction (DSI Unloading Building/Storage Silo) | 1 | LOT | 31000 |  |  |  | 31000 |  | (b) | Handling & Erection | 1 | LOT | 40% | CCM Table 1.8 |  |  | 2360530.4984
| (c) | Structural steel | 1 | LOT | 84000 |  |  |  | 84000 |  | (c) | Electrical | 1 | LOT | 1% | CCM Table 1.8 |  |  | 59013.2625
| (d) | Electrical | 1 | LOT | 771000 |  |  |  | 771000 |  | (d) | Piping | 1 | LOT | 30% | CCM Table 1.8 |  |  | 1770397.8738
| (e) | Abovegrade piping | 1 | LOT | 367000 |  |  |  | 367000 |  | (e) | Insulation | 1 |  | 1% | CCM Table 1.8 |  |  | 59013.2625
Direct Installation Costs (DIC) - Guess at new building, foundation, piping, electrical, etc. | [7 empty] | DIC = | 1351000 |  | (f) | Painting | 1 | LOT | 1% | CCM Table 1.8 |  |  | 59013.2625
[10 empty] | Direct Installation Costs (DIC) - Guess at new building, foundation, piping, electrical, etc. |  |  |  |  | 85% |  |  | DIC = | 5016127.3091
Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 9575688.04
[10 empty] | Total Direct Costs (TDC) | [7 empty] | TDC = (PEMC) + (DIC) = | 10917453.5551
INDIRECT COSTS
(3) | Engineering, Procurement & Construction Support Services |  | 10% | % TDC |  |  | 957568.804 |  |  | INDIRECT COSTS
(4) | Performance tests |  | 1 | EA | 75000 |  | 75000 |  |  | (3) | Engineering |  | 10% | CCM Table 1.8 |  |  |  |  | 1091745.3555
Total Indirect Costs (TIC) | [7 empty] | TIC = | 1032568.804 |  | Construction and Field Exp. |  | 10% | CCM Table 1.8 |  |  |  |  | 1091745.3555
[11 empty] | Contractor Fees |  | 10% | CCM Table 1.8 |  |  |  |  | 1091745.3555
[11 empty] | Start-Up |  | 1% | CCM Table 1.8 |  |  |  |  | 109174.5356
MANAGEMENT AND CONTINGENCY COSTS | [9 empty] | (4) | Performance tests |  | 1% | CCM Table 1.8 |  |  |  |  | 109174.5356
(5) | Contingency |  | 10% | % TDC |  |  | 957568.804 |  |  | Total Indirect Costs (TIC) |  |  | 32% |  |  |  |  | TIC = | 3493585.1376
Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 957568.804
MANAGEMENT AND CONTINGENCY COSTS
TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 11565825.648 | (5) | Contingency |  | 10% | % TDC |  |  |  |  | 1441103.8693
[10 empty] | Total Management and Contingency Costs (TM&CC) | [7 empty] | TM & CC = | 0
[10 empty] | TOTAL CAPITAL INVESTMENT (TCI) | [7 empty] | TCI = (TDC)+(TIC)+(TM&CC) = | 14411038.6927
|  | Line Number/Description | Title |  | UAF Comments |  |  |  | Department Comments
|  | Line Number 1a | Total DSI System |  | DSI price provided by OEM Vendor. Cost includes equipment supply and installation costs. Installation costs of vendor supplied equipment was assumed to be 25% of equipment cost. |  |  |  | The Department removed the 25% increase in cost for equipment installation which is accounted for elsewhere.
|  | Line Number 1a | ID Fan |  | Pricing provided by Clarage for new ID Fan for CDS system. Fan pricing was scaled from 1250 HP to 950 HP. Fan shipping is provided in line number 1c. |  |  |  | Left unchanged from UAF's price quote and calculations
|  | Line Number 1b | Total Instrumentation |  | Total costs for new communication links and I/O integration into existing DCS room. |  |  |  | Used EPA's Pollution Cost Control Manual Table 1.8 assumption of 10% of the cost of the equipment price.
|  | Line Number 1c | ID Fan Shipping Costs |  | Costs to ship ID fan to site. CDS pricing was used and scaled from 1250 HP to 950 HP. |  |  |  | Used EPA's Pollution Cost Control Manual Table 1.8 assumption of 5% of the cost of the equipment price.
|  | Line Number 1d | Extended Outage Costs |  | UAF typically schedules for a 3 week outage on Boiler #5. A DSI outage will take 8 weeks and the University will incur 5 additional weeks of outage costs that inlcude purchasing electric power and running additional boilers for steam generation. Costs per day were provided by UAF personnel. The daily outage cost calculations are presented in the last section of Appendix H beginning on page H-74. |  |  |  | The Department removed these costs for the cost calculation in order to make a conservative estimate.
|  | Line Number 1e | Vendor Representative Costs |  | Costs incurred for OEM to send a Field Technician to the field to confirm installation and provide technical guidance if needed. Cost per day includes hourly burdened rate for employee daily allowances and travel expenses. |  |  |  | The Department removed these costs and included a cost for startup below under (3).
|  | Line Number 2a thru 2e | Direct Install Costs |  | Costs broken down into individual disciplines for balance of plant equipment, materials and labor for the DSI System. Cost estimate basis for each discipline are provided as attachments. |  |  |  | Used the direct installation cost percentages from EPA's Pollution Cost Control Manual Table 1.8.
|  | Line Number 3 | Engineering Services |  | Costs for Preliminary Engineering costs to assist the University in soliciting bidders with specifications, preliminary drawings and procurement support for the AQCS system. Additional services include home office support for shop drawing review and occasional site support during construction for potential issues. Engineering is a percentage of the Total Direct Costs of the Project. |  |  |  | Used the direct installation cost percentages from EPA's Pollution Cost Control Manual Table 1.8.
|  | Line Number 4 | Performance Test |  | Costs for a 3rd party performance testing company to validate emissions and performance guarantees by DSI vendor during operation
|  | Line Number 5 | Construction Contingency |  | Construction Contingency is an allottment for additonal or unexpected costs during the project. RS Means defines contingency allowances and ranges between 3-20% depending on what design stage the project is in. A 10% contingency is a project that is in Design Development, wheras a Conceptual Design phase allows for a 20% contingency. A 10% contingency for this cost estimate is considered low as the project is still in a Development phase. |  |  |  | Used the 10% contingency factor from EPA's Pollution Cost Control Manual Table 1.8, Footnote c.
Note on G11: Author: ($3.4M for Reactor, Humidification + $1.3M for Duct changes) * 1.25 for scaling. Ref. UAF BACT Appendix E, pgs 23 & 24.
Note on R11: Author: ($3.4M for Reactor, Humidification + $1.3M for Duct changes) removed 1.25 installation factor. Ref. UAF BACT Appendix E, pgs 23 & 24.
Note on G12: Author: cost = ($425k for the fan + $142k for motor) * (950/1250) The scaling factors are to drop from 1250 hp to 950 hp. BACT Apppendix H pg 10.
Note on R12: Author: cost = $425k for the fan + 142k for the motor and scaled down from 1250 hp to 950 hp
Note on G15: Author: BACT Appendix H, pg 18
Note on G18: Author: Author: BACT Appendix H, pg 22 talks about shipping costs for the ID fan, 56k per step deck for each truck and they will need two trucks. Scaled down for smaller fan.
Note on G21: Author: Appendix H, pg 75-88. Confused on the total electric costs.Also the cost for transport of 413k doesn't match the net savings on pdf pg 85.
Note on G29: Author: BACT Appendix H pg 29
Note on G30: Author: BACT Appendix H, pg 31.
Note on G31: Author: BACT Appendix H pg 29.
Note on G32: Author: BACT Appendix H pgs 39 and 40.
Note on G33: Author: BACT Appendix H pg 43

## Cost Effectiveness
Shaded cells indicate user inputs
Total Annualized Costs - DSI (Dry Sorbent Injection) | [7 empty] | Date: | 2022-12-28 |  | Total Annualized Costs - DSI (Dry Sorbent Injection) | [7 empty] | Date: | 2022-12-28
Project: |  | UAF - BACT Analysis | [5 empty] | Prepared By: | M. Jahn |  | Project: |  | UAF - BACT Analysis | [5 empty] | Prepared By: | M. Jahn
Vendor: |  | BACT Process Systems, Inc. | [5 empty] | Updated By: | C. Kimball |  | Vendor: |  | BACT Process Systems, Inc. | [5 empty] | Updated By: | C. Kimball
[8 empty] | Rev: | B | [9 empty] | Rev: | B
Annualized Costs | [10 empty] | Annualized Costs
DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL |  | DIRECT ANNUAL COSTS |  |  | QTY | UNIT | UNIT COST | TOTAL MATERIALS COST | TOTAL LABOR COST |  | TOTAL
(1) | Operating Labor |  | 8864 | MH | 49.09 | Excluded | 435133.76 |  | 435133.76 |  | (1) | Operating Labor |  | 547.5 | MH | 49.09 |  |  |  | 26876.775
(2) | Supervisory Labor |  |  | MH |  | Excluded | Excluded |  | Excluded |  | (2) | Supervisory Labor |  | 15% | % of Operating Labor |  |  |  |  | 4031.5163
(3) | Maintenance Labor |  | 520 | MH | 49.09 | Excluded | 25526.8 |  | 25526.8 |  | (3) | Maintenance Labor |  | 547.5 | MH | 49.09 |  |  |  | 26876.775
(4) | Maintenance Materials |  | 1 | LOT | 25526.8 | 25526.8 | Excluded |  | 25526.8 |  | (4) | Maintenance Materials |  |  | LOT | 0 |  |  |  | 0
(5) | Utilities | [9 empty] | (5) | Utilities
| (a) | Hydrated Lime: | 394.2 | TON | 1377 | 542813.4 | Excluded |  | 542813.4 |  |  | (a) | Hydrated Lime: | 394.2 | TON | 1377 | 542813.4 | Excluded |  | 542813.4
| (b) | Electricity: | 2683275.6 | kWh | 0.205 | 550071.498 | Excluded |  | 550071.498 |  |  | (b) | Electricity: | 2683275.6 | kWh | 0.205 | 550071.498 | Excluded |  | 550071.498
| (c) | Water: | 8935.2 | (k)Gallons | 11.3 | 100967.76 | Excluded |  | 100967.76 |  |  | (c) | Water: | 8935.2 | (k)Gallons | 11.3 | 100967.76 | Excluded |  | 100967.76
Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 1680040.018 |  | Total Direct Annual Costs (TDAC) | [7 empty] | TDAC = | 1251637.7243
INDIRECT ANNUAL COSTS | [10 empty] | INDIRECT ANNUAL COSTS
(6) | Overhead |  | 1% | % |  |  | 115658.2565 |  | 115658.2565 |  | (6) | Overhead |  | 60% | of total labor and material costs CCM Table 1.9 |  |  |  |  | 34671.0398
(7a) | Administrative Charges, Insurance |  | 3% | % total capital |  |  | 346974.7694 |  | 346974.7694 |  | (7) | Property Tax |  | 1% | of Total Capital Investment - CCM Table 1.9 |  |  |  |  | 144110.3869
(7b) | Capital Recovery Factor [see inputs below] |  | 0.084671 | [7 empty] | (7a) | Administrative Charges, Insurance |  | 3% | of Total Capital Investment - CCM Table 1.9 |  |  |  |  | 432331.1608
(8) | Capital Recovery | [6 empty] | CRF * TCI = | 979292.7503 |  | (7b) | Capital Recovery Factor [see inputs below] |  | 0.093051
[11 empty] | (8) | Capital Recovery | [6 empty] | CRF * TCI = | 1340955.4412
Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 1441925.7762 |  | Total Indirect Annual Costs (TIAC) | [7 empty] | TIAC = | 1952068.0287
TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 3121965.7942 |  | TOTAL ANNUALIZED COSTS (TAC) | [7 empty] | TAC = (TDAC) + (TIAC) = | 3203705.7529
[11 empty] | Cost Per Ton ($/ton) | [5 empty] | TAC/Tons of SO2 Removed |  |  | 35348.9112
Data Inputs for Capital Recovery Factor:
|  | Data Inputs for Capital Recovery Factor: |  |  |  |  | Uncontrolled emissions (tpy) = |  | 129.4728 |  | Annual Interest Rate (EPA OAQPS Control Cost Manual) |  |  | 8.5 | % |  |  | Uncontrolled emissions (tpy) = |  | 129.4728
|  | Annual Interest Rate (EPA OAQPS Control Cost Manual) | 7.5 | % |  |  | controlled emissions (tpy) = |  | 38.8418 |  | Project Life (EPA OAQPS Control Cost Manual) |  |  | 30 | years |  |  | controlled emissions (tpy) = |  | 38.8418
|  | Project Life (EPA OAQPS Control Cost Manual) | 30 | years |  |  | Reduction (tpy) = |  | 90.631 | [8 empty] | Reduction (tpy) = |  | 90.631
Line Number/Description |  |  | Title |  | UAF Comments |  |  |  |  | Department Comments
Line Number 1 through 3 |  |  | Operating/Maintenance Labor |  | Provided by UAF. Rate is burdoned rate for level of personnel operating and performing maintenance on this type of equipment. Additional FT operations person is assumed per shift. Four total shifts per week. Quarter FT maintenance persons is assumed for the new DSI system. |  |  |  |  | Assumed 0.5 hours per shift for operating and maintenance labor, and 15% of operator labor for supervisor labor per Table 1.9 of EPA CCM
Line Number 4 |  |  | Maintenance Material |  | Allotment for maintenance materials. Item is equal to the maintenance labor allotment in line 3. |  |  |  |  | Did not include an allotment for maintenance materials
Line Number 5a |  |  | Hydrated Lime |  | Hydrated Lime consumption rates provided by DSI vendor. Hydrated Lime costs provided by L'hoist. |  |  |  |  | Left unchanged from UAF's calculations
Line Number 5b |  |  | Electricity |  | Pricing provided by UAF for published utility rates on campus. Electical consumption rate provided by DSI vendor. Additional consumption by larger ID Fan was also included. |  |  |  |  | Left unchanged from UAF's calculations
Line Number 5c |  |  | Water |  | Pricing provided by UAF for published utility rates on campus. Water consumption rate provided by DSI vendor. |  |  |  |  | Left unchanged from UAF's calculations
Line Number 6 |  |  | Overhead |  | Calculated as percent of Total Capital Investment |  |  |  |  | Calculated as 60% of total labor and material costs per Table 1.9 of EPA's CCM
Line Number 7a |  |  | Admin Charges, etc |  | Calculated as percent of Total Capital Investment |  |  |  |  | Calculated as 3% of total total capital investment (admin charges + insurance) and 1% (property tax) per Table 1.9 of EPA's CCM
Line Number 7b |  |  | Capital Recovery Factor |  | EPA calculated factor using Interest Rate and Project Life Span |  |  |  |  | Updated to current bank prime interest rate of 8.5%
Line Number 8 |  |  | Capital Recovery |  | Capital Recovery Factor times Total Capital Investment.
Annual Interest Rate (EPA OAQPS Control Cost Manual) |  |  | Annual Interest Rate |  | Latest federal prime rate. https://www.federalreserve.gov/releases/h15/
Project Life (EPA OAQPS Control Cost Manual) |  |  | Project Life |  | Project Life expectancy in years. |  |  |  |  | Left life expectancy unchaged at 30 years
Note on G8: Author: hourly salary from BACT Appendix H pg 71
Note on G10: Author: hourly salary from BACT Appendix H pg 71
Note on G13: Author: BACT Appendix H pg 57
Note on G14: Author: Electricity cost from BACT Appendix H pg 55. Note that the cost to UAF is likely lower. https://www.gvea.com/services/rates/
Note on G15: Author: water cost from BACT Appendix H pg 55 shows $12.17/1k gallons.