## Community Readiness
DEC Western Alaska Community Recovery & Readiness
Community | Drinking Water | Sewer/Wastewater | Fuel Systems/Spill Assessments | Solid Waste/Landfill | Honey Bucket | Lead Program/Next Step | Notes - Water/Drinking Water | Notes - SPAR | Notes - Landfills
Bethel | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | N/A | Regional hub
Chefornak | ✅ In compliance | ✅ Functioning - Local crews repairing sewer doghouses | ⚠️ Confirmed spills(s) - developing plan for spring response actions, as needed | ✅ Accessible | ✅ Functional | RMW oversight, DW | DEC engineers inspected the water treatment plant on October 26 and found no storm-related damage. A total coliform sample collected October 14 was negative, and a VOC sample collected October 26 showed non-detect results for all VOCs. The Drinking Water Program Manager spoke with Chefornak City Administrator Leticia to share the results of VOC, lead, and total coliform testing. The water has been confirmed safe for all potable uses. The wastewater force main serving the LKSD school and community washeteria was displaced from its supports but is functional. Piping and anchors are being sourced. Repairs expected this winter. Update 11/19: The sewer discharge line requires repair. DOT’s contractor is preparing to begin work, with VSW providing consulting support. | Barring new spill reports, no action planned before spring. On-site notes from 10/31: No reported interruptions or spills from tank farm. No reported home heating oil tank spills. One confirmed spill at man camp, estimated 20-50 gallons diesel. | Update 10/31: The landfill is accessible.
Eek | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | EH DW support |  | On-site notes from 10/28: No displaced heating oil tanks or used oil spills.
Goodnews Bay | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | EH DW support
Golovin | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | EH monitoring |  | On-site notes from 10/27: No SPAR concerns identified.
Hooper Bay | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | EH monitoring
Kipnuk | ⚠️ Boilers and heat loops online; circulation stabilization in progress - ANTHC is designing a Reverse Osmosis (RO) treatment skid to treat brackish source water. The system currently has fully treated water in the storage tank, but will be unable to make additional water until the RO unit is in place. | ✅ Functioning | ⚠️ Confirmed spills(s) - developing plan for spring response actions, as needed | ⚠️ Debris throughout site | ⚠️ Needs assessment | SPAR & VSW | Update 11/5: ANTHC assessed Kipnuk’s drinking water system and confirmed that the raw water reservoir was impacted by the storm surge, resulting in brackish (saline) conditions. The community’s existing water treatment system cannot effectively treat saltwater. To restore potable water, ANTHC is designing a skid-based reverse osmosis (RO) unit that will integrate with the current treatment system to remove salinity. Water samples were collected from the reservoir to guide the design and sizing of the new RO system. Samples were submitted to SGS on November 3 for analysis of inorganics, alkalinity, pH, total dissolved solids, anions, nitrate, VOCs, and total trihalomethanes. Expedited testing was not requested, as the results will not affect the design or fabrication timeline of the RO system. SGS’s standard 10-day turnaround provides the needed data without additional cost. The engineer advised that Kipnuk will not be able to produce treated water until the RO unit is installed. Fabrication of the RO unit is expected to take approximately six weeks. Update 11/10: The Kipnuk community system has approximately 50,000 gallons of treated drinking water in their storage tanks. This water is being reserved to use as RO unit backwash water. The LKSD school has approximately 150,000 gallons of treated water in storage and is providing water to the community. Update 11/19: Brice Construction is bringing in a temporary shower unit at the washeteria. ANTHC is designing and procuring an RO unit; estimated 12 weeks out. | Fall and early winter work has focused on assessment and recovery of tanks and other oil and hazardous substance containers. Anticipate need to assess soil contamination in Kipnuk in the spring. On-site notes from SPAR assessments between 10/22 and 11/6: Responders report a lot of miscellaneous tanks and drums that floated during the storm and are now orphaned as debris. Fuel or sheen is observed in almost every puddle under ice. According to the Tribal representative roughly 120 heating oil tanks were moved by floodwaters. Many homes cannot be lifted or repaired until surrounding debris—including tanks, drums, and damaged boardwalk material—is cleared. USCG contractor, Chadux, addressed damaged fuel tanks and secured small storage oil and oil product containers and was demobilized around 11/1. On 11/6 SPAR assisted in the relocation of a 1,500-gallon double-walled heating oil tank that was sitting on the community water line. DEC also met with DOT and Brice Construction to review potential modifications to ongoing work. Items under consideration include removal of heating oil tanks from debris fields, consolidation and secure storage of recovered fluids, battery and refrigerant recovery, wheeler and equipment oil draining, monofill needs, and guidance for safe debris segregation and burning under solid-waste rules. | Update 11/5: The Solid Waste Program also worked with Air Division on the requirements for contractor use of air curtain incinerators, which is allowed under exemption NSPS EEEE. We have provided information on this exemption and requirements to the contractor. Update 11/18: Limited access to the landfill by sled with Hondas (very small loads). They're burning waste in the 2 Tok burn units in the landfill where waste needs to be cut down to fit in. Long and slow process. Trash remains spread all around the landfill. They have small, borrowed heavy equipment as all of the heavy equipment bound for them was diverted to Kwig because of ice. They are helicoptering equipment over when they can, but equipment is low on the priority list. Contractor is trying to get them an air-curtain incinerator. Unsure if it is in Kwig or needs to be purchased.
Kongiganak | ⚠️Functioning treatment and washeteria/watering point. DOT to replace raw water line this winter. | ✅ Functioning | ⚠️ Potential contamination - developing plan for spring response actions, as needed | ✅ Landfill access restored and landfill has capacity for disaster debris. Permanent access solution will be needed in the spring. | ✅ Functional | RMW & SPAR | Update 11/10: • Update: YKHC submitted a request on November 5 for raw water line repair supplies. DOT is assisting with procurement and transport. • Sufficient stored water until January 2026. DOT procuring 10,000 feet of HDPE pipe to replace damage raw water pipe. • System will draw water from alternative source in January to make more drinking water Update 11/11: Continuing work on permanent power to the airport clinic, washeteria and armory. Update 11/20: DOT contractor awaiting materials deliver to replace raw water line. VSW is gathering previous design and construction drawings to assist. | Barring new spill reports, no action planned before spring. On-site notes from 10/28: Three unidentified drums or tanks were located, but no visible oil or hazardous material releases were observed. A spill site was inspected along the cross-town fuel transfer line that supplies the teacher housing tank. The line was closed at the time of the incident, and approximately 100 gallons of fuel oil spilled with 800 gallons recovered from the fuel line. Repairs were completed the same day. Field readings showed low vapor levels (60 ppb) with frozen ground limiting fuel migration. Minor soil removal and in-place burning were conducted to aid cleanup. Additional remediation is recommended when conditions allow. | Section of boardwalk/bridge to landfill is missing 8 ft of boards. Other minor damages reported along road to landfill and images show single boards missing throughout boardwalk to landfill. No images or assessment of landfill or salvage area. Update 11/11: DOT & Contractors are building boardwalk to the landfill. Update 11/19: DOT has constructed a temporary bridge to the landfill, but a permanent solution is needed in the spring. They have access to the landfill and it has capacity for disaster debris.
Kotzebue | ✅ In compliance | ⚠️ Lagoon erosion; pipe displacement | ⚠️ Confirmed spills(s) - developing plan for spring response actions, as needed | ✅ Accessible | N/A | SPAR, City crews | The main findings in Kotzebue are erosion concerns along the bridge on Ted Steven’s Road, the sewage lagoon 3, and along Front Road. Ted Stevens road is 1 of 2 evacuation points out of town and is still closed and was actively under construction. Sewage concerns include interruptions to lift stations 4, 9, and 12. 4 has been returned to service but 9 and 12 are on bypass. There are several sewer lines to residences that have experienced erosion and flood waters have caused pipes to rise out of earthen trenches and be displaced. These have since frozen and burst. 11/20 Update: DOT addressing repairs to sewer lagoon cell 3. Lift stations #4 and #9 have been repaired and returned to service. Final electrical work on lift station #12 expected to be complete by Monday, 11/24/25, at which point it will also be returned to service. | Barring new spill reports, no action planned before spring. Single spill report associated with storm received. No other damage identified during 10/23 on-site assessment.
Kwigillingok | ✅ In compliance; ANTHC leading water treatment plant repairs | ✅ Functioning - Local crews repairing sewer doghouses | ⚠️ Potential contamination - developing plan for spring response actions, as needed | ⚠️ Main landfill inaccessible; unpermitted site washed out | ✅ Functional | VSW, EH, SPAR field teams; contractors deploying 10/29 | RMWs have been repairing and reattaching the raw water supply line, which was displaced by up to 300 feet and tangled with debris and boats. The line is reconnected but has frozen sections preventing full use; once heat trace repairs are complete and glycol is available, thawing will begin to restore drinking water production. The finished water tank currently holds about 40,000 gallons of safe, treated water, and recent VOC results were non-detect. DEC will assist with coliform sampling once the system is operational. YKHC and Norton Sound RMWs will also address sewer line repairs at the school and residential dog houses. The honeybucket lagoon remains functional, and DOT is repairing a nearby washout; haul trailers are awaiting new pumps for final repairs. Update 11/11: DOT is completing access to sewage lagoon and cemetery and were working with ANTHC to troubleshoot power and water issues. | Barring new spill reports, no action planned before spring. Assessment of soil contamination in community may be necessary. Additional recovery of displaced tanks and containers may be necessary as soilwaste and debris removal is expanded. DEC and its contractor, US Ecology, recovered fuel and secured displaced tanks and oil and hazardous substance containers across the community. Approximately 2,000 gallons of fuel was collected. Collected waste is secured in community for overwinter storage. DEC contractor demoblized 11/11. | The Solid Waste Program also worked with Air Division on the requirements for contractor use of air curtain incinerators, which is allowed under exemption NSPS EEEE. We have provided information on this exemption and requirements to the contractor. Update 11/18: Landfill access remains very limited due to mushy soil. Boardwalks to landfill are in poor condition with coffins staged on them for reburial at an unknown time. Per on-site contractor debris burning is going well with an air-curtain incinerator. Operating 24/7 with high volume reduction. Burning some community trash. Ash is being supersacked for eventual landfill disposal.
Marshall | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional
Napakiak | ✅ In compliance | ✅ Functioning - Local crews repairing sewer doghouses | ⚠️ Confirmed spills(s) - developing plan for spring response actions, as needed | ✅ Accessible | ✅ Functional | RMW, EH, SPAR | The community’s drinking water well was overtopped during flooding but has since been shock chlorinated and tested safe. All coliform and VOC results were non-detect, and the system is now operating normally. The Flush, Tank, Haul (FTH) system sustained widespread damage, with many insulated “doghouses” displaced—though all but one were salvageable. Repairs are ongoing and require various fittings due to age differences across the system. The honeybucket lagoon remains intact but will need to be pumped out in the spring once a dewatering pump is available. Update 11/3: Electrical service is still needed to restore power to the doghouses. | Barring new spill reports, no action planned before spring. A dozen or so HHOT that have kinked fuel lines or were knocked off their stands. Additional assessments of soil contamination may be necessary in the spring. Response supplies were provided to Napakiak for a potential used oil spill reported on 10/17. DEC conducted a vapor intrusion assessment of the Post Office on November 8 in response to community concerns. Floodwaters reached nine inches inside the building, but no visible fuel leaks, odors, or mold were found. Both Toyo stove fuel lines and nearby tanks showed no signs of leakage. Air monitoring showed low VOC levels overall, with the highest indoor reading around 190 ppb—considered low and not indicative of a hazardous fuel release. A comparison check at the adjacent store showed higher VOC levels (600 ppb), likely from general indoor sources, helping confirm that elevated readings in the Post Office are not fuel-related. DEC-SPAR made the following suggestions for the Post Office building: · Remove wet/frozen lower wall and floor insulation and replace when the wood is dry. · Repair both Toyo oil stoves. · Request an electrician to test and observe the electrical outlet boxes to determine if safe to energize. · Obtain a granular activated carbon indoor air filter to mitigate vapors that may emanate when the building is heated. This may be combined with a HEPA filter to provide additional protection of mold spores. | SW staff visited community on 10/23/25. Site is accessible, no road damage. Landfill did flood during the storm and ponded water still remaining in site. Landfill operator reported potential leachate seep to DEC (not SW) and it was inspected. Flood waters carried waste north of the site. Homes took on flood water and there is likely large amounts of structural damage. Update 11/3: SWP staff visited Napakiak on November 2. The road to the landfill is in good shape. National Guard personnel were actively mucking out houses and delivering wet insulation and other debris to the landfill. The landfill appears to be in good shape., and response personnel were bringing wet insulation to the landfill for disposal from their work mucking out houses.
Napaskiak | ✅ In compliance - System functional but the washeteria which contains the treatment system has pre-storm structural damage and pre-storm leaks from the floors. | ✅ Functioning - Local crews repairing sewer doghouses | ⚠️ Confirmed spills(s) - developing plan for spring response actions, as needed | ✅ Accessible | ✅ Functional | SPAR follow-up; EH monitoring | Update 10/30: DEC engineers inspected the water treatment plant on October 22 and confirmed it was unaffected by the storm. The system continues to operate normally. A total coliform sample collected October 16 was negative, and a VOC sample collected during the inspection showed non-detect results. | Barring new spill reports, no action planned before spring. On-site notes from 10/23: Many residents had already repaired their HHOT. SPAR provided sorbent pads. There was a report of a large spill near the City Office with a strong smell of diesel; fresh snow made it challenging to assess the extent of any spill. There was one home that had a fuel line break inside the home. | Waste collection has been paused due to the wet conditions in the landfill. SW Staff on site on 10/23/25 and noted that MSW is piling up at the entrance to the site. Waste should move in once ground is harder. Minimal structural damage and the community has been able to pick up the small amount of storm debris which will go into the LF when collection resumes. Update 11/5: SWP staff visited Napaskiak on November 4. We visited the landfill and observed no storm damage to the access road or the landfill fence. The landfill does not have damage from the storm. Staff took both drone and ground photos. There were approximately 50 supersacks of demolition debris staged outside of the landfill. The SWP believes there is adequate space in the landfill to accommodate this debris. We will work with Napaskiak on this issue.
Nightmute | ✅ In compliance | ✅ Functioning - Local crews repairing sewer doghouses | ⚠️ Confirmed spills(s) - developing plan for spring response actions, as needed | ✅ One-time monofill is accessible - monofill site is the preferred location for future landfill. | ✅ Functional | DW Eng., SPAR, VSW field follow-up | The Nightmute Water Treatment Plant building shifted during flooding, causing the well casing to lean slightly, though it remains intact and is producing water normally. Drinking water testing for both the community and school systems showed no coliforms, and a VOC sample from the community well on October 26 was non-detect for all VOCs, confirming the water is safe to drink. The school operator will collect additional VOC samples for analysis. Staff also identified a traditional drinking water source—a stream culvert used by roughly half the village population. This untreated surface water contained coliforms and should be boiled for at least two minutes before consumption. A precautionary Boil Water Notice for traditional sources was issued on October 24, 2025. YKHC RMWs White and Kamuck arrived on October 29, 1925, and repaired the main leak at teacher housing and reinsulated a storm-damaged sewer junction box. One minor leak in an individual teacher housing unit remains to be addressed. Update 11/10: Leak in teacher housing unit has been repaired. FOR AWARENESS: A Boil Water Notice for a traditional water source is issued as a precaution to help protect public health. Because these sources are not regulated public water systems, the notices are not formal regulatory actions, they are more in the spirit of a public service reminder. Traditional surface water sources naturally contain microbial contaminants, so they should always be boiled before drinking. For that reason, BWNs for traditional sources are not usually “lifted” the way they are for regulated systems, since untreated surface water is never fully safe without boiling or treatment. Update 11/18: Drinking Water Program contacted the lab about VOC testing results for Nightmute school. Results for sample collected on 10/30/25 were non-detect. | Barring new spill reports, no action planned before spring. SPAR visited Nightmute on October 21 and documented 16 damaged homes, with at least half needing heating oil tank restoration. Coordination with DOT is underway to re-plumb the tanks, though it is unclear if this has been added to their task scope. SPAR assessed homes for vapor intrusion issues on October 26 noting wet conditions and indoor air quality concerns. Boot cleaning station kits and additional PPE were shipped on October 27 to support safe operations. Reports of fuel odor along the riverbank near the old tank farm and a swale in a residential area indicate further oil spill response and soil cleanup will be needed, especially ahead of spring break-up. | Update 11/11: Access to the new landfill is complete for storm debris disposal. Update 11/18: Landfill being used for both debris and community waste. No burning for volume reduction as no burn units on-site. The community was pursuing a new landfill site before Halong, and this was their preferred site. The goal will be to convert the 1-time landfill into a full Class III landfill in 2026. Unknown funding to complete this activity.
Nome | ✅ In compliance | ✅ Functioning | ✅ None Identified |  |  |  |  | On-site notes from 10/25: No SPAR concerns identified.
Nunam Iqua | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | EH | Update 10/31: The RMW in Nunam Iqua reported that the operator plans to reinstall the summer intake pump on Monday. The four feet of water currently available is sufficient until pumping resumes. The summer pump had been removed for winter preparations, but the ice isn’t thick enough yet to install the winter setup. VOC test results showed non-detect results. | On-site notes from 10/30: The team inspected the community tank farm, bulk fuel receiving header, and electrical transformer storage area, and observed no damage or oil/hazardous material releases. | Update 11/1: SWM staff visited Nunum Iqua and met with Tribal Office staff, including the major. One home was reportedly flooded, plus there was some wind damage to a couple of homes, particularly to porches. Staff visited the landfill and were able to get drone and ground photos. The landfill does not appear to have taken any damage and is accessible.
Nunapitchuk | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | EH/SPAR coordination |  | SPAR spoke with community officials who reported no damage to the bulk tank farm, critical infrastructure such as the clinic, washateria, school, power plant, used oil storage or home heating oil tanks.
Oscarville | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | SPAR closeout 10/24 | Update 10/30: The Oscarville systems are non-public because they serve fewer than 25 people, and the Washeteria is not currently in use. DEC engineers inspected the school’s water system on October 24 and collected samples for coliform and VOC testing. Both coliform samples were negative; VOC results showed non-detect results. The school currently has 19 students, including three evacuees from Kwigillingok. | On-site notes from 10/24: No storm damage identified at the community bulk tank farm. Two potential spills were reported by the community, but SPAR was unable to find contamination at those locations. | Solid Waste staff visited Oscarville on 10/24/25. A fair amount of trash around community, some trash was reportedly washed out of landfill by flooding.
Quinhagak | ✅ In compliance - ARUC and City procuring materials to repair raw water intake electrical controls. | ✅ Functioning - DOT placing super sacks to protect lagoon this winter | ⚠️ Fuel line damage; no spill(s) | ✅ Accessible | N/A | DOT/DEC/VSW coordination | The wastewater system appears to be functioning. There is concern erosion from the storm is approaching the sewage lagoon. An ARUC engineer has assessed the lagoon and erosion. It appears there is no immediate threat to the lagoon from the ARUC report. A plan is emerging through coordination with DOT, ARUC, DEC and the community to use locally sourced material to add reinforcements to the beach to protect the lagoon from further erosion during the 2025/26 winter storm season. Update 10/30: RMWs have been on site conducting repairs to the system’s controls and intake line. Three wells remain operational. The operators have been working to raise the raw water line and reattach it to all sleepers. Five total coliform samples collected October 22 were negative. A VOC sample collected October 24 showed non-detect results. Update 11/3: The community sustained significant electrical and water system damage. Of the three well pumps, one was displaced and two require electrical repairs; ANTHC is coordinating repairs but may need additional assistance. There are ongoing concerns that if the remaining operational pump fails before the others are restored, water service will be disrupted. High water levels around the intake also pose a risk, and the community recommends raising the intake by five feet to prevent future flood damage. The wastewater lagoon has exposed permafrost and will require gravel and reseeding before spring thaw to prevent erosion. The water system foundation continues to settle, raising concerns about long-term stability. Update 11/19: DOT placing super sacks to protect lagoon this winter | On-site notes from 10/21: No spills identified. No home heating oil tanks dispalced. Fuel lines and the vent pipe on the National Guard heating oil tank were damaged and require repair. | Landfill access has not been impacted. The storm caused erosion of landfill entrance, but not listed as a primary concern. This site is only 600 ft W of the ocean and is threatened by erosion. The community could find a new location for a monofill that could be converted into a Class III site.
St. Michaels | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | SPAR closeout 10/24 | General updates for Stebbins and St. Micheal include general wind damages to homes, sheds, smoke houses including roof, wall, windows, and some sheds and smoke houses demolished. Main community concerns consist of listing power lines in both communities. | On-site notes from 10/24: No SPAR concerns identified.
Stebbins | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | SPAR closeout 10/24 | See St. Michael's for notes | On-site notes from 10/24: No SPAR concerns identified.
Teller | ✅ In compliance | ✅ Functioning | [5 empty] | On-site notes from 10/25: No SPAR concerns identified.
Toksook Bay | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | EH DW closeout |  | On-site notes from 10/30: No SPAR concerns identified. DEC Spill response conex resupplied 11/7/2025 with 7 bales of Sorbent pads 17" X 19" 100, 18 bales of Sorbent boom, 5" X 10' 4, 2 Sorbent rolls 36" X 150' (38x144) and 200 oil waste bags. Items received by Toksook Bay city manager and stored into the DEC response Conex. | Update 11/1: SWM staff visited Toksook Bay and visited the landfill. The landfill is accessible and did not appear to have taken any damage from the storm. SWM staff got drone footage and ground photos of the landfill. Staff also met with both the Tribal office staff and City office staff. There is reportedly not a significant amount of debris in the village; however, City office staff reported that there were storm damaged porches and some materials blown off of fish drying rack structures. SWM staff also got drone footage of both the old and new tank farms. No major damage was seen.
Tuntutuliak | ✅ In compliance - The school system requested VOC testing; samples were sent out on 11/5 by LKSD. | ✅ Functioning | ⚠️ Confirmed spills(s) - developing plan for spring response actions, as needed | ✅ Accessible | ✅ Functional | EH & SPAR | Update 10/30: RMWs have confirmed no damage to the washeteria. The well was overtopped during flooding, but a total coliform sample collected October 20 was negative. The community remains under a long-term boil water notice unrelated to the storm. A VOC sample collected October 23 showed non-detect results. Update 11/10: DEC staff and YKHC RMWs have resolved the issue and BWN was lifted. | Barring new spill reports, no action planned before spring. An estimated 2,000 gallon spill on 10/11 was reported from the service station. Sorbents were deployed but all indications are the storm waters took most of the oil. The community is describing only residual oil remaining from the release. The USCG and their contractor visited Tuntutuliak on 10/16 and found no recoverable product and no recoverable product expected moving forward. SPAR staff were in Tuntutuliak on 10/23 and didn’t highlight any SPAR specific concerns. | Update 11/3: SWP staff visited Tuntutuliak on November 1. No impact to landfill from storm; however, there were 30 homes reportedly flooded. Crews were mucking out flooded homes at time of visit, including removing insulation, and drying out floors in preparation for new insulation. One home is marked for demolition. Took aerial and thermal drone footage of the landfill, tank farm, damaged homes, and school tank farm, as well as ground photography of the landfill and damaged homes.
Tununak | ✅ In compliance | ✅ Functioning | ✅ None Identified | ✅ Accessible | ✅ Functional | EH DW field crew | DW conducting hydrocarbon testing for ground water system. | On-site notes from 11/5: No SPAR concerns identified. SPAR visited homes impacted by storms and noted no concerns related to Home Heating Oil Tanks or the bulk fuel tank farms. | The Tununak River Bridge (#1385) has lost roughly half of the roadway width for roughly 100 ft extending toward town along the ocean side. DOT has not listed this as a primary concern, but it should be watched since the landfill is only accessible via this bridge. Update 11/10: Bridge has been repaired.
Most recent updates in RED
| This document is a working draft prepared by the Alaska Department of Environmental Conservation (DEC) for situational awareness and coordination purposes. The information contained herein represents the best available data at the time of compilation and is subject to change as field conditions, assessments, and community reports are updated. This spreadsheet should not be interpreted as a final verification of community readiness or infrastructure condition. Data may be incomplete, unverified, or based on preliminary assessments. DEC and partner agencies continue to refine and validate information through ongoing field operations and coordination with local, Tribal, and federal partners. For official updates or confirmed public health and environmental safety information, please refer to communications released directly by DEC or the State Emergency Operations Center (SEOC). | [5 empty] | FOR AWARENESS: A Boil Water Notice for a traditional water source is issued as a precaution to help protect public health. Because these sources are not regulated public water systems, the notices are not formal regulatory actions, they are more in the spirit of a public service reminder. Traditional surface water sources naturally contain microbial contaminants, so they should always be boiled before drinking. For that reason, BWNs for traditional sources are not usually “lifted” the way they are for regulated systems, since untreated surface water is never fully safe without boiling or treatment.